## Cover Sheet Tables 1-15
| Yes | No | <-- for dropdowns
Energy Safety Data Guidelines Appendix D, Section 1.2
Wildifire Mitigation Data Tables Template: Tables 1 - 15
Update the below table to establish which reporting period this submission this represents.
Utility Name |  | Southern California Edison
First year of 3-year WMP cycle |  | 2023
Reporting Period year |  | 2022
Reporting Period quarter |  | Q4
Date Modified |  | 2023-02-01

## PMT_FLUPS (hidden)
Table | Metric Desc | Lead | Backup/Support | What's New/Changing | Cannot Provide/Reason | Needed FLUP | Follow Up Comments
1 | Quarterly Initiative Update (QIU) | Nancy Richardson | Suzie Olmos | - Column D (Project Start Date) - Column E (Project End Date) - Column H (Initiative Objective) - Column O (WMP Initiative Code) - Column Q (Risk Target Reduction) - Column R (Mid-Year Target Y/N) - Column AJ (Reference Compliance Branch Reqs) - Column AK (Audit) - Column AL (Audit File Documentation Requested) - Column AM (Folder Link) - Column AN (Person in Charge Name) - Column AO (Person in Charge Email) | - Column AJ (Reference Compliance Branch Reqs) - NEED MORE INFORMATION - Column AK (Audit) - NEED MORE INFORMATION - Column AL (Audit File Documentation Requested) - NEED MORE INFORMATION - Column AM (Folder Link) - NEED MORE INFORMATION - Column AN (Person in Charge Name) - CAN PROVIDE BUT NEED TO KNOW WHO TO LIST - Column AO (Person in Charge Email) -- CAN PROVIDE BUT NEED TO KNOW WHO TO LIST | - Action Item: Nancy reach out to Ryan to provide clarification on new columns | - 12/27 Sent email to Nancy requesting follow up to Reg (JF)
2 | Performance Metrics | See Table 2 for Leads | See Table 2 for Backups | - For all Risk Events --> New: Columns J-L (Line Type, Inspection Type, Inspection Method) - 2. Time between vegetation inspection finding and resulting trimming activity - 3. Time between level 1 asset inspection finding and resulting maintenance activity - 4. Time between level 2 asset inspection finding and resulting maintenance activity - 5. Time between level 3 asset inspection finding and resulting maintenance activity - 6. Vegetation management work orders - 7. Asset management work orders - 8. Response Time - 14. Grid condition findings from inspection (New requirement is providing number of assets inspected) - 15. Grid condition fixes in response to inspection findings - 16. Vegetation clearance findings from inspection (New requirement is number of trees inspected and resulting number of trees out of compliance) | - 2. Time between vegetation inspection finding and resulting trimming activity - PER BILL K. DATA CANNOT BE PROVIDED, MELANIE SUGGESTED REACHING OUT TO NAPA/VALERIA TO SEE IF THEY CAN SUPPORT - 6. Vegetation management work orders - Need to confirm with Bill K if information can be provided (can be notifications, looking for open notifications and those that are past due) - 8. Response Time - Need to confirm with Jonathan and Matt that data can be provided - 17. Community outreach metrics - This is not a new requirement, but we have not historically been able to provide this information | - Action Item: Jen to confirm backups for Table 2 data providers (specifically Elizabeth, Brian Standish, Derek Tafoya) - Action Item: Jen to confirm Risk team can provide newly requested columns - Action Item: Felicia to facilitate meeting with Veg folks (Napa and Valeria) to confirm if new Veg metrics can be provided, include Kevin Arlic in conversation - Action Item: Jen to confirm Jonathan and Matt can provide data (Time between detecting a locked open circuit breaker and dispatching personnel to investigate the cause) - Action Item: Jen to confirm with Tom Brady if we evacaute customers in event of a wildfire Bill K doesn't have Veg WO's for Non-QC or timing between. -May have to reach out to RPPM/Joe scamanochi - Song Yun (lyn duong) -depends on district/territory -Median time probably exists, but 95% not likely for any | - Action Item: Felicia to facilitate meeting with Veg folks (Napa and Valeria) to confirm if new Veg metrics can be provided, include Kevin Arlic in conversation- 12/21 FM Mtg held with Napa and Josh Fine to review new metrics. F/U meeting scheduled for 1/3. Per Josh info can be provided and he could assist new Veg data SME. Also informed additional discussion needed for projections - 12/27 Confirmed backup for Derek Tafoya is Jonathan Brownstein (JF) - 12/27 Sent email to Elizabeth and Brian, awaiting confirmation on who backup are (JF), confirmed Robin Willis is the backup for Elizabeth and Cory Perez is the backup for Brian - 12/27 Sent email to Amber and Creneza, awaiting confirmation can support new data fields (JF), meeting scheduled for 12/28 to discuss --> met with Amber and Creneza, cannot provide LiDAR or drone because system is not set up to capture LiDAR or drone inspections (need to confirm with Aerial team), can provide aerial inspection findings but only for detailed and we wouldn't cover them in patrol, for median and 95th percentile will leverage methodology Sunny drafted on whiteboard, values will be cumulative updated annually and not by quarter, for section 3-5 inspection findings will align with inspections in sections 14 and 15 - 12/27 Sent email to Matt and Jonathan, awating confirmation can support new data fields (JF) - 12/27 Confirmed with Tom Brady that SCE does not instruct customers to evacuate, cannot provide data for 17. Community outreach metrics (JF) - 12/29 Met with Elizabeth and also communicated to Brian that for table 2 (based on final requirements) the line type, inspection type and method do not apply to their sections. Also, we noted that the data goes back to 2020 (and not 2015) (JF)
3 | Additional Metrics | Jonathan Morales | Jen Fernandez |  |  | - Action Item: Kyle to see clarification from OEIS on whether to leverage existing effectiveness metrics or convert to new performance metrics, may need to schedule meeting to identify data providers if needed | - 12/29 Sent email to Kyle seeking clarification (JF)
4 | Weather Patterns | David Holder | Jessica Clawson |  |  | - Action Item: Felicia to confirm Jessica is the backup | Confirmed Jessica is the backup 12/20 FM
5 | Risk Event Drivers | See Table 5 for Leads | See Table 5 for Backups | - Drivers - Subdrivers |  | - Action Item: Jen to send note to data providers advising of the new drivers and subdrivers | - 12/29 Sent email to Elizabeth and Brian advising of new drivers (JF) - 12/29 Met with Elizabeth, mapped out the new drivers, I asked Brian to reach out to her for the new list. We also noted the data is from 2022-on (JF)
6 | Ignitions | Derek Tafoya | Need Backup | - Drivers - Subdrivers |  | - Action Item: Jen to send note to data providers advising of the new drivers and subdrivers - Action Item: Jen to confirm backup for Derek | - 12/27 Confirmed Derek's backup is Jonathan Brownstein (JF) - 12/29 Sent email to Derek advising of new drivers (JF)
7 | State of Service Territory and Equipment | David Holder | Jessica Clawson | - 4. Residential customers - 5. Commercial customers - 6. AFN customers |  | - Action Item: Felicia to confirm Jessica is the backup - Action Item: Confirm with David that he can break out the meter types by res, comm and AFN in a spatial format to break out in WUI, non-WUI, HTFD tier, urban/rural/highly rural | - Confirmed Jessica is the backup 12/20 FM - Per Jessica, additional assistance needed from Cust Srv to break out meter type by res, comm, and AFN. 12/2 FM Meeting set up for 1/3
8 | Planned Utility Equipment Net Additions or Removals | TBD | TBD |  |  | - Action Item: Sunny to reach out to Dave Fanous (Distr.) and Jack Haggenmiller (Trans) to see if we can provide: Planned T&D additions or removals, overhead, underground, substation broken out by WUI, non-WUI, HTFD tier, urban/rural/highly rural - Action Item: Jen to reach out to Ryan to ask other IOUs what criteria they are using to derive their data | - 12/27: Sent email to Sunny regarding AI (JF) - 12/27: Sent email to Ryan regarding IOU criteria (JF)
9 | Location of Utilitiy Infrastructure Upgrades | TBD | TBD |  |  | - Action Item: Sunny to reach out to Dave Fanous (Distr.) and Jack Haggenmiller (Trans) to see if we can provide: Planned T&D upgrades, overhead, underground, substation broken out by WUI, non-WUI, HTFD tier, urban/rural/highly rural - Action Item: Jen to reach out to Ryan to ask other IOUs what criteria they are using to derive their data | - 12/27: Sent email to Sunny regarding AI (JF) - 12/27: Sent email to Ryan regarding IOU criteria (JF)
10 | Recent Use of PSPS / Other PSPS Metrics | See Table 10 for Leads | See Table 10 for Leads | 1. Recent use of PSPS and fast-trip (1.a, 1.b, 1.d and 1.e) 2. Customer hours of PSPS and other outages (2.c) 5. Other PSPS metrics (5.d - 5.h) | SAIDI / SAIFI - Due to technical issues, may not be able to resolve in time to provide data for filing | - Action Item: Sunny to follow up with Rashad to see when data will be ready - Action Item: Jen to follow up with Scott on 5.d-5.h | - 12/29: Sent email to Al and Scott confirming they can provide data for 5.d-5.h (JF)
11 | Mitigation Initiative Financials | Yoshi Nori | Vivek Gadh |  |  | - Action Item: Jen to confirm Yoshi to support | - 12/27: Sent email to Yoshi and Vivek (JF), confirmed they will take the lead on this table
12 | Mid Year and End Year Targets | Nancy Richardson | Suzie Olmos | New table |  | - Action Item: Jen to confirm which activities have mid year targets and if we can start reporting after WMP is filed since targets are not yet approved | - 12/29 Sent email to Kyle seeking clarification (JF)
13 | Open Work Orders / Notifications | Amber Beaulieu | Creneza Bui | New table |  | - Action Item: Confirm with Amber she can support | 12/21 FM : John Grass scheduled mtg on 12/21 to discuss ACI open notification items. Mary Soledad created ACI notification criteria. Per discussion with Sunny we may want to align criteria and set boundaries to criteria (i.e., all open items as of quater end and due in 2023). Sunny suggested we continue to keep Amber as POC
14 | HFTD Area Risk | Berta Sandberg | Lisa Mau | New table |  | - Action Item: Confirm with Berta and Lisa can support | - 12/27: Sent email to Berta and Lisa (JF), Berta confirmed she will take the lead on this table
15 | Top Risk Scores | Berta Sandberg | Lisa Mau | New table |  | - Action Item: Confirm with Berta and Lisa can support | - 12/27: Sent email to Berta and Lisa (JF), Berta confirmed she will take the lead on this table
Table | Projections Y/N
1 | No
2 | Yes
3 | Yes
4 | No
5 | Yes
6 | Yes
7 | Yes
8 | Yes
9 | Yes
10 | Yes
11 | Yes
12 | Yes
13 | No
14 | No
15 | No

## SummaryUpdate (hidden)
Table | As of Date | Progress Updates | PMT Notes/Concerns
1 | 2023-01-06 | Nancy Richardson has begun populating tables with guidance from Reg team | PMT Check-in call for set for Mon 1/9
2 | 2023-01-06 | Data SME and Metric AORs assigned. Amber Beaulieu has begun inputting inspection/finding/fixes metrics. | Veg team has already reached out indicating difficulty producing retroactive and Non-HFTD metrics. PMT check-in call set for Mon 1/9
3 | 2023-01-06 | Reg team still finalizing metric list for inclusion in table 3 | PMT to follow up with Regulatory
4 | 2023-01-06 | Geospatial Analysis team working on populating RFW/HWW metrics today | PMT to follow up with GA team next week to confirm completion
5 | 2023-01-06 | Outage/Wire Down SMEs just completed GIS QDR inputs and working on Non-Spatial next | PMT to follow up with Risk team next week to confirm completion
6 | 2023-01-06 | Ignition SME just completed GIS QDR inputs and working on Non-Spatial next | PMT to follow up with Risk team next week to confirm completion
7 | 2023-01-06 | Geospatial Analysis team compiling Q1-Q3 metrics, awaiting Q4 Asset GDB from IT to calc Q4 inputs. | PMT to follow up with GA team next week to confirm completion
8 & 9 | 2023-01-06 | PMT met with Major Project Org managers today to identify applicable programs and identify SME AORs | PMT to resume data collection efforts Weds 1/10
10 | 2023-01-06 | Data SMEs identified. | PMT call to review PSPS metrics in depth Tues 1/10
11 | 2023-01-06 | Yoshinori Goya confirmed AOR and informed PMT a draft version of the table should be completed by Fri 1/13 COB. | PMT to follow up next week
12 | 2023-01-06 | Table assigned to Nancy R to populate after table 1 completion | PMT Check-in call for set for Mon 1/9
13 | 2023-01-06 | Table AOR and assumption/filter criteria confirmed. Amber Beaulieu/Cindy Jacobs to populate | Over 900k rows expected unless criteria is further refined. PMT working with John Graass in Reg to refine requirements.
14 & 15 | 2023-01-06 | Berta S confirmed as POC. Planning to have tables populated by Fri 1/13 deadline | PMT to follow up next week
Table | As of Date | Progress Updates | PMT Notes/Concerns
1 | 2023-01-18 | Nancy working on populating 2022 and 2023 versions of the QIU
2 | 2023-01-06 | Asset Inspections-inputs being revised today based on updated Notification criteria methodology. Veg- Cycle Time and Open WOs completed. Counts of Trees Inspected/Out of Compliance - partially completed. Awaiting Past Due Wos (methodology finalized today). Ignitions/Outages/WD-Just awaiting Outages with Protection Devices enables projections. Igntion Related Damages/Acres/Injuries/Fatalities - Completed Circuit Mile conversion of Asset Inspections - Awaiting Amber's completion.
3 | 2023-01-06 | Awaiting Reg team to finalize metrics to be included, as well as methodology and SME (if needed).
4 | 2023-01-06 | David Holder (Geospatial Analysis team) has metrics completed just needs to add to table
5 | 2023-01-06 | Completed - awaiting projections by Data Science team (Paolo Joson/Jonathan Wuo)
6 | 2023-01-06 | Completed - awaiting projections by Data Science team (Paolo Joson/Jonathan Wuo)
7 | 2023-01-06 | David Holder (Geospatial Analysis team) has metrics completed just needs to add to table
8 & 9 | 2023-01-06 | Awaiting data from Angel Brito, Johnathan Hughes
10 | 2023-01-06 | Awaiting all data (sync up call for this afternoon)
11 | 2023-01-06 | Yoshinori Goya almost completed
12 | 2023-01-06 | Nancy/Jennifer finalizing quarter end targets to complete after Table 1 QIU is finalized
13 | 2023-01-06 | Amber B has this file completed, but will populate outside QDR due to file size.
14 & 15 | 2023-01-06 | Berta S completed offline and will begin populating today.
Table | As of Date | Progress Updates | PMT Notes/Concerns
1 | 2023-01-19 | Nancy working on populating 2022 and 2023 versions of the QIU
2 | 2023-01-06 | Asset Inspections-inputs being revised today based on updated Notification criteria methodology. Veg- Cycle Time and Open WOs completed. Counts of Trees Inspected/Out of Compliance - partially completed. Awaiting Past Due Wos (methodology finalized today). Ignitions/Outages/WD-Just awaiting Outages with Protection Devices enables projections. Igntion Related Damages/Acres/Injuries/Fatalities - Completed Circuit Mile conversion of Asset Inspections - Awaiting Amber's completion.
3 | 2023-01-19 | Performance Metrics finalized by Reg. Data source and SME's identified. Jonathan M to work with Data Science/Veg/CS on projections
4 | 2023-01-06 | David Holder (Geospatial Analysis team) has completed inputs thru Q4 2022. Jonathan M to verify
5 | 2023-01-06 | Completed - awaiting projections by Data Science team (Paolo Joson/Jonathan Wuo)
6 | 2023-01-06 | Completed - awaiting projections by Data Science team (Paolo Joson/Jonathan Wuo)
7 | 2023-01-19 | David Holder (Geospatial Analysis team) has metrics completed just needs to add to table
8 & 9 | 2023-01-19 | Angel B out until Monday, attempts made to obtain data from Johnathon Hughes
10 | 2023-01-19 | Al Watson's team/Scott Scudder beginning to populate data.
11 | 2023-01-06 | Yoshinori Goya almost completed
12 | 2023-01-06 | Nancy/Jennifer finalizing quarter end targets to complete after Table 1 QIU is finalized
13 | 2023-01-06 | Amber B has this file completed, but will populate outside QDR due to file size.
14 & 15 | 2023-01-06 | Berta S completed offline and will begin inputting data today
Table | As of Date | Progress Updates
1 | 2023-01-25 | Completed and awaiting Reg team review/edits to be finalized
2 | 2023-01-25 | Completed - only Veg/Asset Open and Past Due WO projections still needed. Amber/Cindy performing last review and confirmation on all metrics.
3 | 2023-01-25 | Only projections needed. Data Science team expects to have this done by Fri 1/26.
4 | 2023-01-25 | Completed
5 | 2023-01-25 | Only projections needed. Data Science team expects to have this done by Fri 1/26.
6 | 2023-01-25 | Completed (including projections)
7 | 2023-01-25 | Completed
8 & 9 | 2023-01-25 | Geospatial Analysis team working on this now. ETA tomorrow COB for completion
10 | 2023-01-25 | Only projections needed.
11 | 2023-01-25 | Completed and awaiting Reg team review/edits to be finalized
12 | 2023-01-25 | Completed and awaiting Reg team review/edits to be finalized
13 | 2023-01-25 | Completed
14 & 15 | 2023-01-25 | Completed - awaiting final review and sign off for Gary Chen and Reg team
Table | As of Date | Progress Updates
1 | 2023-01-30 | Awaiting PMT/Reg pens down
2 | 2023-01-30 | Completed - Projections included
3 | 2023-01-30 | Completed - Projections included
4 | 2023-01-30 | Completed
5 | 2023-01-30 | Completed
6 | 2023-01-30 | Completed
7 | 2023-01-30 | Completed
8 & 9 | 2023-01-30 | Geospatial Analysis team working on this now. ETA is EOD for completion
10 | 2023-01-30 | Completed - Projections included
11 | 2023-01-30 | Awaiting Reg team pens down
12 | 2023-01-30 | Awaiting PMT/Reg pens down
13 | 2023-01-30 | Completed
14 & 15 | 2023-01-30 | Awaiting Reg team pens down

## Table 1
UtilityID | SubmissionDate | InitiativeClassification | ProjectStartDate | ProjectEndDate | UtilityInitiativeName | InitiativeDescription | InitiativeObjective | WMPInitiativeCategory | WMPInitiativeCategory# | WMPInitiativeActivity | ActivityNameifOther | WMPInitiativeActivity# | UtilityInitiativeTrackingID | WMPInitiativeCode | WMPPageNumber | RiskTargetReduction | MidYearTarget (Yes/No) | QuantTargetUnits | AnnualQuantTarget | ProjectedQuantProgressQ1 | ProjectedQuantProgressQ1-2 | ProjectedQuantProgressQ1-3 | ProjectedQuantProgressQ1-4 | QuantActualProgressQ1 | QuantActualProgressQ1-2 | QuantActualProgressQ1-3 | QuantActualProgressQ1-4 | AnnualQualTarget | QualActualProgressQ1 | QualActualProgressQ1-2 | QualActualProgressQ1-3 | QualActualProgressQ1-4 | Status | CorrectiveActionsIfDelayed | REFERENCE: Compliance Branch Requirements --> | Audit | Audit File Documentation Requested | FolderLink | PersonInChargeName | PersonInChargeEmail
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Wildfire Safety Community Meetings | Community meetings, primarily in SCE's HFRA, to share information about SCE’s WMP efforts | Share grid hardening, PSPS, and emergency preparedness updates, and highlight SCE's various programs, services, and resources. Also, receive direct feedback from meeting participants | Community Outreach and Engagement | 8.5 | Public Outreach and Education Awareness Program |  | 8.5.2 | DEP-1 | Community Outreach and Engagement_Public Outreach and Education Awareness Program_DEP-1_2023 | TBD | N/A | Yes | # of meetings | SCE will host at least four wildfire community safety meetings by region in targeted HFRA communities based on the impact of 2022 PSPS events and ongoing wildfire mitigation activities | 0 | 4 | 4 | 4 |  |  |  |  | Quantitative Initiative |  |  |  |  | Planned
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | SCE Emergency Response Training | Technical training programs that prepare employees to perform their jobs safely, comply with regulatory requirements and laws, maintain system reliability, and leverage new technology | Provide effective emergency response and restore service during and after a major event. | Emergency Preparedness | 8.4 | Emergency Preparedness Plan |  | 8.4.2 | DEP-2 | Emergency Preparedness_Emergency Preparedness Plan_DEP-2_2023 | TBD | N/A | No | Qualitative Initiative | Qualitative Initiative | [8 empty] | PSPS response teams are fully qualified/re-qualified by 7/1 annually to maintain readiness |  |  |  |  | In Progress
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Customer Research and Education | SCE develops surveys to capture customer feedback on SCE’s wildfire mitigation initiatives with a special emphasis on PSPS activities | Improve its understanding of how to reduce impacts of wildfires, PSPS, and wildfire mitigation work for its customers | Community Outreach and Engagement | 8.5 | Public Outreach and Education Awareness Program |  | 8.5.2 | DEP-4 | Community Outreach and Engagement_Public Outreach and Education Awareness Program_DEP-4_2023 | TBD | N/A | Yes | # of surveys | SCE plans to conduct at least five PSPS‐related customer studies in 2023 | 1 | 1 | 3 | 4 |  |  |  |  | Quantitative Initiative |  |  |  |  | In Progress
SCE | 2023-02-01 | Project | 2023-01-01 | 2023-12-31 | Aerial Suppression | SCE funds up to four aerial firefighting helicopters, support personnel and equipment to bolster firefighting capabilities | Fire suppression within SCE’s service area | Emergency Preparedness | 8.4 | External Collaboration and Coordination |  | 8.4.3 | DEP-5 | Emergency Preparedness_External Collaboration and Coordination_DEP-5_2023 | TBD | Wildfire vulnerability | No | Qualitative Initiative | Qualitative Initiative | [8 empty] | Provide fire agencies with funding to support quick reaction force (QRF) program for 2023 |  |  |  |  | In Progress
SCE | 2023-02-01 | Project | 2023-01-01 | 2023-12-31 | Wildfire Safety Data Mart and Data Management (WiSDM / Ezy) | Centralized wildfire data repository (WiSDM) and SCE's asset inventory (Ezy) | Streamline collection of and reporting out of SCE's wildfire mitigation efforts | Grid Design, Operations, and Maintenance | 8.1 | Asset Management and Inspection Enterprise System(s) |  | 8.1.5 | DG-1 | Grid Design, Operations, and Maintenance_Asset Management and Inspection Enterprise System(s)_DG-1_2023 | TBD | N/A | Yes | Qualitative Initiative | Qualitative Initiative | [8 empty] | WiSDM: Enable semi-automated data aggregation and validations of Wildfire Data for SCE's Quarterly Data Request (QDR) submission and external portal for external data sharing by Q4 2023 Ezy: Enable Lidar data management by end of year |  |  |  |  | In Progress
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Distribution High Fire Risk‐Informed (HFRI) Inspections and Remediations (Ground and Aerial) | Distribution equipment and structures inspections beyond the GO 95 and GO 165 requirements | Detect equipment anomalies and mitigate ignition risks that cannot be detected during compliance ‐ driven programs alone | Grid Design, Operations, and Maintenance | 8.1 | Asset inspections |  | 8.1.3.1 | IN-1.1 | Grid Design, Operations, and Maintenance_Asset inspections_IN-1.1_2023 | TBD | Equipment ignition likelihood, Contact from vegetation ignition likelihood, Contact by object ignition | Yes | # of structures in HFRA | Inspect 187,000 structures in HFRA | 32000 | 101320 | 172640 | 187000 |  |  |  |  | Quantitative Initiative |  |  |  |  | In Progress
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Transmission High Fire Risk‐Informed (HFRI) Inspections and Remediations (Ground and Aerial) | Transmission equipment and structures inspections beyond the GO 95 and GO 165 requirements | Detect equipment anomalies and mitigate ignition risks that cannot be detected during compliance ‐ driven programs alone | Grid Design, Operations, and Maintenance | 8.1 | Asset inspections |  | 8.1.3.1 | IN-1.2 | Grid Design, Operations, and Maintenance_Asset inspections_IN-1.2_2023 | TBD | Equipment ignition likelihood, Contact from vegetation ignition likelihood, Contact by object ignition | Yes | # of structures in HFRA | Inspect 28,000 structures in HFRA | 3400 | 14400 | 25800 | 28000 |  |  |  |  | Quantitative Initiative |  |  |  |  | In Progress
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Infrared Inspection of Energized Overhead Distribution Facilities and Equipment | Infrared (IR) inspections on its distribution circuits that can detect conditions often not visible to the human eye | Detect deteriorated connection points on electrical equipment such as conductors, insulators, splices or connectors that over time can lead to failures if left unmitigated and pose ignition risks | Grid Design, Operations, and Maintenance | 8.1 | Asset inspections |  | 8.1.3.1 | IN-3 | Grid Design, Operations, and Maintenance_Asset inspections_IN-3_2023 | TBD | Equipment ignition likelihood | Yes | # of distribution circuit miles in HFRA | Inspect 5,100 distribution overhead circuit miles in HFRA | 0 | 2295 | 5100 | 5100 |  |  |  |  | Quantitative Initiative |  |  |  |  | Planned
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Infrared Inspection, Corona Scanning, and High-Definition Imagery of Energized Overhead Transmission facilitates and Equipment | Infrared (IR) inspections on its transmission circuits that can detect conditions often not visible to the human eye | Detect deteriorated connection points on electrical equipment such as conductors, insulators, splices or connectors that over time can lead to failures if left unmitigated and pose ignition risks | Grid Design, Operations, and Maintenance | 8.1 | Asset inspections |  | 8.1.3.1 | IN-4 | Grid Design, Operations, and Maintenance_Asset inspections_IN-4_2023 | TBD | Equipment ignition likelihood | Yes | # of transmission circuit miles in HFRA | Inspect 1,000 transmission overhead circuit miles in HFRA | 150 | 600 | 900 | 1000 |  |  |  |  | Quantitative Initiative |  |  |  |  | In Progress
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Generation High Fire Risk Informed Inspections in HFRA | Inspections of generation-related assets in HFRA | Identify potential ignition risks on generation-related assets and mitigate the ignition driver risks through system hardening | Grid Design, Operations, and Maintenance | 8.1 | Equipment Inspections, Maintenance, and Repair |  | 8.1.4 | IN-5 | Grid Design, Operations, and Maintenance_Equipment Inspections, Maintenance, and Repair_IN-5_2023 | TBD | Equipment ignition likelihood, Contact from vegetation ignition likelihood, Contact by object ignition | Yes | # of structures in HFRA | Inspect 170 generation related assets in HFRA | 0 | 55 | 170 | 170 |  |  |  |  | Quantitative Initiative |  |  |  |  | Planned
SCE | 2023-02-01 | Project | 2022-01-01 | 2023-12-31 | Inspection and Maintenance Tools | InspectForce is the centralized asset inspection product used for planning and executing inspections | Improves the effectiveness and speed of inspections, data quality and record accuracy, and helps ensure that information is available, accessible, and timely to support wildfire mitigation activities. | Grid Design, Operations, and Maintenance | 8.1 | Asset Management and Inspection Enterprise System(s) |  | 8.1.5 | IN-8 | Grid Design, Operations, and Maintenance_Asset Management and Inspection Enterprise System(s)_IN-8_2023 | TBD | N/A | Yes | Qualitative Initiative | Qualitative Initiative | [8 empty] | Develop the detailed design to migrate the distribution ground inspection application to the single digital platform |  |  |  |  | In Progress
SCE | 2023-02-01 | Project | 2022-01-01 | 2023-12-31 | Transmission Conductor and Splice Assessment | Identification of anomalies / issues in order to replace or remediate conductors and/or splices that have a higher probability of failure | Reduce transmission conductor wire down events | Grid Design, Operations, and Maintenance | 8.1 | Asset inspections |  | 8.1.3.1 | IN-9 | Grid Design, Operations, and Maintenance_Asset inspections_IN-9_2023 | TBD | N/A | Yes | # Spans/splices | Will inspect 50 spans with Line Vue Will inspect 50 splices with X-Ray | Line Vue: 10 Splices w/X-ray: 10 | Line Vue: 30 X-Ray: 30 | Line Vue: 45 X-Ray: 45 | Line Vue: 50 Splices w/X-ray: 50 |  |  |  |  | Quantitative Initiative |  |  |  |  | In Progress
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Customer Care Programs (Critical Care Backup Battery (CCBB) Program) | Supports all customers enrolled in Medical Baseline (MBL) that reside in a HFRA to provide a battery-powered portable backup solution | Allows eligible customers to operate critical medical equipment during power outages due to PSPS events or other emergencies | Emergency Preparedness | 8.4 | Customer Support in Wildfire and PSPS Emergencies |  | 8.4.6 | PSPS-2 | Emergency Preparedness_Customer Support in Wildfire and PSPS Emergencies_PSPS-2_2023 | TBD | PSPS vulnerability | No | % of batteries delivered | Complete 85% of battery deliveries to eligible customers within 30 calendar days* of program enrollment, subject to customer availability, reschedule requests and battery supply constraints * Number of calendar days subject to change based on customer survey feedback to inform appropriate calendar day measurement | Maintain >/= 85% delivery rate of 30 calendar days from customer enrollment to delivery | Maintain >/= 85% delivery rate of 30 calendar days from customer enrollment to delivery | Maintain >/= 85% delivery rate of 30 calendar days from customer enrollment to delivery | Maintain >/= 85% delivery rate of 30 calendar days from customer enrollment to delivery |  |  |  |  | Quantitative Initiative |  |  |  |  | In Progress
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Customer Care Programs (Portable Power Station and Generator Rebates) | Provides up to five $75 rebates to customers for purchasing a portable power station for their home or small business resiliency needs | Provide additional opportunities to increase customer resiliency | Emergency Preparedness | 8.4 | Customer Support in Wildfire and PSPS Emergencies |  | 8.4.6 | PSPS-3 | Emergency Preparedness_Customer Support in Wildfire and PSPS Emergencies_PSPS-3_2023 | TBD | PSPS vulnerability | No | % of rebates processed | Process 85% of all rebate claims within 30 business days** of receipt from website vendor; excluding website related delays and subject to receiving all required customer information *Number of calendar/business days subject to change based on customer survey feedback to inform appropriate calendar/business day measurement | Maintain >/= 85% process rate of 30 business days from rebate submittal to check processed | Maintain >/= 85% process rate of 30 business days from rebate submittal to check processed | Maintain >/= 85% process rate of 30 business days from rebate submittal to check processed | Maintain >/= 85% process rate of 30 business days from rebate submittal to check processed |  |  |  |  | Quantitative Initiative |  |  |  |  | In Progress
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Weather Stations | Validate real‐time conditions in the field during elevated fire conditions and are used to provide critical situational awareness for PSPS decision‐making and help improve weather models. | Help SCE make decisions during potential fire conditions, including PSPS de-energization and re-energizations | Situational Awareness and Forecasting | 8.3 | Environmental Monitoring Systems |  | 8.3.2 | SA-1 | Situational Awareness and Forecasting_Environmental Monitoring Systems_SA-1_2023 | TBD | PSPS vulnerability | No | # of weather stations installed | Install 85 weather stations in SCE's HFRA | 10 | 40 | 75 | 85 |  |  |  |  | Quantitative Initiative |  |  |  |  | In Progress
SCE | 2023-02-01 | Project | 2022-01-01 | 2023-12-31 | High Definition (HD) Cameras | HD camera installations resolves gaps in SCE’s spatial data and provides improved fire confirmation capabilities | Helps IMTs and first responders more quickly assess and respond to reported fires | Situational Awareness and Forecasting | 8.3 | Ignition Detection Systems |  | 8.3.4.2 | SA-10 | Situational Awareness and Forecasting_Ignition Detection Systems_SA-10_2023 | TBD | Wildfire vulnerability, PSPS vulnerability | No | # of HD cameras installed | Install 10 HD Cameras | 2 | 4 | 6 | 10 |  |  |  |  | Quantitative Initiative |  |  |  |  | In Progress
SCE | 2023-02-01 | Pilot | N/A, activity classified as pilot | N/A, activity classified as pilot | Early Fault Detection (EFD) | EFD technology detects high frequency radio emissions that can occur from arcing or partial discharge conditions on the electric system | EFD could potentially be used to monitor the overall health of the electric system which may inform operational decisions during high‐risk conditions. | Situational Awareness and Forecasting | 8.3 | Grid Monitoring Systems |  | 8.3.3 | SA-11 | Situational Awareness and Forecasting_Grid Monitoring Systems_SA-11_2023 | TBD | Equipment ignition likelihood, Contact from vegetation ignition likelihood, Contact by object ignition | No | # of locations | Install Early Fault Detection (EFD) at 50 locations | 0 | 24 | 45 | 50 |  |  |  |  | Quantitative Initiative |  |  |  |  | Planned
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Weather and Fuels Modeling | Weather and fuels modeling including weather forecasts and historic weather data spanning the entire SCE service area | Maintain and enhance operational weather and fuel forecasting capabilities | Situational Awareness and Forecasting | 8.3 | Weather Forecasting |  | 8.3.5 | SA-3 | Situational Awareness and Forecasting_Weather Forecasting_SA-3_2023 | TBD | PSPS vulnerability | No | Qualitative Initiative | Qualitative Initiative | [8 empty] | Equip 500 weather station locations with machine learning capabilities |  |  |  |  | In Progress
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Fire Science Enhancements | Various modeling tools to predict fire ignition and consequence outputs such as fire perimeter size, structures impacted, populations affected, and injury and death | Expand data analysis, emphasize fire potential forecasting, and improve modeling efforts as it relates to fire science | Situational Awareness and Forecasting | 8.3 | Environmental Monitoring Systems |  | 8.3.2 | SA-8 | Situational Awareness and Forecasting_Environmental Monitoring Systems_SA-8_2023 | TBD | PSPS vulnerability | No | Qualitative Initiative | Qualitative Initiative | [8 empty] | Complete analytics report summarizing assessment of historical consequence data for improved fire spread modeling |  |  |  |  | In Progress
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Covered Conductor | Replacing bare wire with conductor / components (fire-resistant poles, composite crossarms, FR3 transformers, wildlife covers, surge arresters, polymer insulators and vibration dampers) to protect against the arcing, faults, or energy release that can come from incidental contact. | Reduce CFO, EFF and Wire-to-Wire Risk | Grid Design, Operations, and Maintenance | 8.1 | Covered Conductor Installation |  | 8.1.2.1.1 | SH-1 | Grid Design, Operations, and Maintenance_Covered Conductor Installation_SH-1_2023 | TBD | Equipment ignition likelihood, Contact from vegetation ignition likelihood, Contact by object ignition, PSPS Likelihood | No | # of circuit miles in HFRA | Install 1,100 circuit miles of covered conductor in SCE’s HFRA | 280 | 611 | 952 | 1100 |  |  |  |  | Quantitative Initiative |  |  |  |  | In Progress
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Tree Attachment Remediation | Program removes electrical equipment from trees and installs them on new fire-resistant poles | Reduce EFF Risk | Grid Design, Operations, and Maintenance | 8.1 | Traditional Overhead Hardening |  | 8.1.2.5 | SH-10 | Grid Design, Operations, and Maintenance_Traditional Overhead Hardening_SH-10_2023 | TBD | Equipment ignition likelihood, Contact from vegetation ignition likelihood, Contact by object ignition | No | # of tree attachment remediations | Remediate 400 tree attachments in SCE’s HFRA | 45 | 215 | 400 | 400 |  |  |  |  | Quantitative Initiative |  |  |  |  | In Progress
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Long Span Initiative | LiDAR on distribution long spans helps to identify locations with potential conductor clash issues and remediates the highest risk locations upon field validation | Reduce Wire to Wire Risk | Grid Design, Operations, and Maintenance | 8.1 | Covered Conductor Installation |  | 8.1.2.1.1 | SH-14 | Grid Design, Operations, and Maintenance_Covered Conductor Installation_SH-14_2023 | TBD | Equipment ignition likelihood, Contact from vegetation ignition likelihood, Contact by object ignition | No | # of remediations | Remediate 400 spans in SCE’s HFRA | 2023 workplan in development; quarterly milestones to be provided in Q1 2023 QDR | 2023 workplan in development; quarterly milestones to be provided in Q1 2023 QDR | 2023 workplan in development; quarterly milestones to be provided in Q1 2023 QDR | 2023 workplan in development; quarterly milestones to be provided in Q1 2023 QDR |  |  |  |  | Quantitative Initiative |  |  |  |  | Planned
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Vertical Switches | Upgrading switches in need of replacement as older switches may generate incandescent particles if not properly adjusted or constructed. | Reduce EFF Risk | Grid Design, Operations, and Maintenance | 8.1 | Other Grid Topology Improvements to Minimize Risk of Ignitions |  | 8.1.2.10 | SH-15 | Grid Design, Operations, and Maintenance_Other Grid Topology Improvements to Minimize Risk of Ignitions _SH-15_2023 | TBD | Equipment ignition likelihood | No | # of switches | Install 9 vertical switches in SCE’s HFRA | 2023 workplan in development; quarterly milestones to be provided in Q1 2023 QDR | 2023 workplan in development; quarterly milestones to be provided in Q1 2023 QDR | 2023 workplan in development; quarterly milestones to be provided in Q1 2023 QDR | 2023 workplan in development; quarterly milestones to be provided in Q1 2023 QDR |  |  |  |  | Quantitative Initiative |  |  |  |  | Planned
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Vibration Damper Retrofit | Retrofit aims to stop wind-driven vibration (known as Aeolian vibration) that may lead to conductor abrasion or fatigue over time. | Reduce Wire to Wire Risk | Grid Design, Operations, and Maintenance | 8.1 | Covered Conductor Installation |  | 8.1.2.1.1 | SH-16 | Grid Design, Operations, and Maintenance_Covered Conductor Installation_SH-16_2023 | TBD | Equipment ignition likelihood, Contact from vegetation ignition likelihood, Contact by object ignition | No | # structures | Retrofit vibration dampers on 300 structures where covered conductor is already installed in SCE’s HFRA | 2023 workplan in development; quarterly milestones to be provided in Q1 2023 QDR | 2023 workplan in development; quarterly milestones to be provided in Q1 2023 QDR | 2023 workplan in development; quarterly milestones to be provided in Q1 2023 QDR | 2023 workplan in development; quarterly milestones to be provided in Q1 2023 QDR |  |  |  |  | Quantitative Initiative |  |  |  |  | Planned
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Rapid Earth Fault Current Limiters (REFCL) (Ground Fault Neutralizer) | Detects ground faults on one phase of a three-phase powerline and rapidly reduces the voltage on the faulted conductor while boosting the voltage on the two remaining phases. Ignitions caused by single phase to ground faults can be mitigated with the use of the Ground Fault Neutralizer which reduces fault energy. | Reduce CFO and EFF Risk | Grid Design, Operations, and Maintenance | 8.1 | Emerging Grid Hardening Technology Installations and Pilots |  | 8.1.2.6 | SH-17 | Grid Design, Operations, and Maintenance_Emerging Grid Hardening Technology Installations and Pilots_SH-17_2023 | TBD | Equipment ignition likelihood, Contact from vegetation ignition likelihood, Contact by object ignition | No | Qualitative Initiative | Qualitative Initiative | [8 empty] | SCE will complete construction of GFN at two substations (Acton and Phelan) |  |  |  |  | In Progress
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Rapid Earth Fault Current Limiters (REFCL) (Grounding Conversion) | The REFCL grounding conversion applications act to reduce energy and ignition risk associated with single phase to ground faults. | Reduce CFO and EFF Risk | Grid Design, Operations, and Maintenance | 8.1 | Emerging Grid Hardening Technology Installations and Pilots |  | 8.1.2.6 | SH-18 | Grid Design, Operations, and Maintenance_Emerging Grid Hardening Technology Installations and Pilots_SH-18_2023 | TBD | Equipment ignition likelihood, Contact from vegetation ignition likelihood, Contact by object ignition | No | Qualitative Initiative | Qualitative Initiative | [8 empty] | SCE will complete grounding conversion at one location, subject to land availability |  |  |  |  | In Progress
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Undergrounding Overhead Conductor | Undergrounding greatly reduces wildfire and PSPS risk by virtually eliminating the possibility for objects to contact energized conductor as well as greatly limiting the ignition-causing potential from equipment failures | Reduce CFO, EFF and Wire-to-Wire Risk | Grid Design, Operations, and Maintenance | 8.1 | Undergrounding of Electric Lines and/or Equipment |  | 8.1.2.2 | SH-2 | Grid Design, Operations, and Maintenance_Undergrounding of Electric Lines and/or Equipment_SH-2_2023 | TBD | Equipment ignition likelihood, Contact from vegetation ignition likelihood, Contact by object ignition, PSPS Likelihood | No | # of circuit miles in HFRA | Convert 11 circuit miles of overhead to underground in SCE's HFRA | 3 | 3 | 8 | 11 |  |  |  |  | Quantitative Initiative |  |  |  |  | In Progress
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Branch Line Protection Strategy | Proactively installing CLFs on branch lines where no fusing previously existed and replacing conventional fuses with CLFs or other CAL FIRE “Exempt” fuse designs | Refine circuit protection strategies to further reduce wildfire risk while balancing system reliability | Grid Design, Operations, and Maintenance | 8.1 | Other Grid Topology Improvements to Mitigate or Reduce PSPS Events |  | 8.1.2.11 | SH-4 | Grid Design, Operations, and Maintenance_Other Grid Topology Improvements to Mitigate or Reduce PSPS Events _SH-4_2023 | TBD | Equipment ignition likelihood, Contact from vegetation ignition likelihood, Contact by object ignition | No | # of locations with installed / replaced fuses | Install or replace fusing at 500 fuse locations that serve HFRA circuitry | 2023 workplan in development; quarterly milestones to be provided in Q1 2023 QDR | 2023 workplan in development; quarterly milestones to be provided in Q1 2023 QDR | 2023 workplan in development; quarterly milestones to be provided in Q1 2023 QDR | 2023 workplan in development; quarterly milestones to be provided in Q1 2023 QDR |  |  |  |  | Quantitative Initiative |  |  |  |  | Planned
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Installation of System Automation Equipment - RAR / RCS | Installing RARs and RCSs to accommodate enhanced settings which can help to sectionalize circuits and control the flow of electricity remotely | Reduce CFO and Wire-to-Wire Risk | Grid Design, Operations, and Maintenance | 8.1 | Other Grid Topology Improvements to Minimize Risk of Ignitions |  | 8.1.2.10 | SH-5 | Grid Design, Operations, and Maintenance_Other Grid Topology Improvements to Minimize Risk of Ignitions _SH-5_2023 | TBD | Equipment ignition likelihood, Contact from vegetation ignition likelihood, Contact by object ignition | No | # of RARs / RCSs installed and operationalized | SCE will install 6 RAR/RCS sectionalizing devices subject to 2022 PSPS analysis and subject to change | 2023 workplan in development; quarterly milestones to be provided in Q1 2023 QDR | 2023 workplan in development; quarterly milestones to be provided in Q1 2023 QDR | 2023 workplan in development; quarterly milestones to be provided in Q1 2023 QDR | 2023 workplan in development; quarterly milestones to be provided in Q1 2023 QDR |  |  |  |  | Quantitative Initiative |  |  |  |  | Planned
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Circuit Breaker Relay Hardware for Fast Curve | Upgrading circuit breakers and installing fast curve settings to increase the speed of the relay detecting a fault and deenergizes a circuit | Reduce CFO and Wire-to-Wire Risk | Grid Design, Operations, and Maintenance | 8.1 | Other Grid Topology Improvements to Mitigate or Reduce PSPS Events |  | 8.1.2.11 | SH-6 | Grid Design, Operations, and Maintenance_Other Grid Topology Improvements to Mitigate or Reduce PSPS Events _SH-6_2023 | TBD | Equipment ignition likelihood, Contact from vegetation ignition likelihood, Contact by object ignition | No | # of installations and placed into service | Replace/upgrade 75 CB relay units with fast curve settings in SCE’s HFRA | 5 | 26 | 57 | 75 |  |  |  |  | Quantitative Initiative |  |  |  |  | In Progress
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Transmission Open Phase Detection | Facilitates detection and de-energization of an open phase (broken transmission conductor) before it can contact a grounded object and create a fault event. | Refine circuit protection strategies to further reduce wildfire risk while balancing system reliability | Situational Awareness and Forecasting | 8.3 | Grid Monitoring Systems |  | 8.3.3 | SH-8 | Situational Awareness and Forecasting_Grid Monitoring Systems_SH-8_2023 | TBD | Equipment ignition likelihood | No | Qualitative Initiative | Qualitative Initiative | [8 empty] | Install TOPD at 5 locations that serve HFRA circuitry with both alarm and trip functionality |  |  |  |  | In Progress
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Hazard Tree Management Program | Identifies trees that pose a risk to electric facilities based on the tree’s observed structural integrity and site conditions. | Reduce Contact From Vegetation Risk | Vegetation Management & Inspections | 8.2 | Vegetation Inspections |  | 8.2.2.1 | VM-1 | Vegetation Management & Inspections_Vegetation Inspections_VM-1_2023 | TBD | Contact from vegetation ignition likelihood | Yes | # grids | Inspect 550 grids and prescribe mitigation for hazardous trees with strike potential within those grids in SCE’s HFRA | 131 | 305 | 447 | 550 |  |  |  |  | Quantitative Initiative |  |  |  |  | In Progress
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | LiDAR Transmission Vegetation Inspections | LiDAR as an inspection and measurement tool acquired via air patrol to identify clearances between high-voltage transmission lines and vegetation. | Make substantial progress on evaluation of incorporation of remote sensing technology into vegetation inspections | Vegetation Management & Inspections | 8.2 | Vegetation Inspections |  | 8.2.2.1 | VM-10 | Vegetation Management & Inspections__VM-10_2023 | TBD | N/A | Yes | # circuit miles | SCE will inspect at least 1,820 HFRA circuit miles *Subject to change based on program adjustments and evolution of remote sensing technologies | 750 | 1390 | 1700 | 1820 |  |  |  |  | Quantitative Initiative |  |  |  |  | In Progress
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Structure Brushing | Removal of vegetation around all poles and structures subject to PRC 4292 | Reduce EFF Risk | Vegetation Management & Inspections | 8.2 | Pole Clearing |  | 8.2.3.1 | VM-2 | Vegetation Management & Inspections_Pole Clearing_VM-2_2023 | TBD | Equipment ignition likelihood, Contact from vegetation ignition likelihood | Yes | # structures brushed | Inspect and clear (where clearance is needed) 63,700 structures*, with the exception of structures for which there are customer access or environmental constraints *These structures are in addition to poles subject to PRC 4292 | 3690 | 29870 | 63700 | 63700 |  |  |  |  | Quantitative Initiative |  |  |  |  | In Progress
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Expanded Clearances for Legacy Facilities | Remove / clear additional vegetation using the standard remediation methods of trims, removals, and/or weed abatement to render the defensible space around a generation facility even more vegetation free | Reduce Contact From Vegetation and EFF Risk | Vegetation Management & Inspections | 8.2 | Clearance |  | 8.2.3.3 | VM-3 | Vegetation Management & Inspections_Clearance_VM-3_2023 | TBD | Equipment ignition likelihood, Contact from vegetation ignition likelihood | Yes | # of sites treated | Perform vegetation treatment and maintenance to 50 sites | 0 | 30 | 45 | 50 |  |  |  |  | Quantitative Initiative |  |  |  |  | Planned
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Dead and Dying Tree Removal | Patrols in HFRA to identify and remove dead, dying, or diseased trees affected by drought conditions and/or insect infestation. | Reduce Contact From Vegetation Risk | Vegetation Management & Inspections | 8.2 | Clearance |  | 8.2.3.3 | VM-4 | Vegetation Management & Inspections_Clearance_VM-4_2023 | TBD | Contact from vegetation ignition likelihood | Yes | # of grids | Inspect 650 grids and prescribe mitigation for dead and dying trees with strike potential within those grids | 148 | 345 | 530 | 650 |  |  |  |  | Quantitative Initiative |  |  |  |  | In Progress
SCE | 2023-02-01 | Project | 2022-01-01 | 2023-12-31 | VM Work Management Tool | Data Warehouse used for Routine Vegetation Management inspections and resulting mitigations | Consolidated work tracking and reporting to optimize operations and improve data accuracy | Vegetation Management & Inspections | 8.2 | Vegetation Management Enterprise System |  | 8.2.4 | VM-6 | Vegetation Management & Inspections_Vegetation Management Enterprise System_VM-6_2023 | TBD | N/A | Yes | Qualitative Initiative | Qualitative Initiative | [8 empty] | Enable supplemental Vegetation Management (emergent work) tree maintenance program capabilities in Arbora by end of year |  |  |  |  | In Progress
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Detailed Inspections for the Prescription, Where Necessary and Feasible, of Expanded Vegetation Clearances from Distribution Lines in HFRA | Distribution expanded line clearances to mitigate the risk of vegetation contact with energized conductors | Reduce Contact From Vegetation Risk | Vegetation Management & Inspections | 8.2 | Clearance |  | 8.2.3.3 | VM-7 | Vegetation Management & Inspections_Clearance_VM-7_2023 | TBD | Contact from vegetation ignition likelihood | Yes | # of grids | SCE plans to inspect 1,900 grids within our distribution system | 524 | 1088 | 1508 | 1900 |  |  |  |  | Quantitative Initiative |  |  |  |  | In Progress
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Detailed Inspections for the Prescription, Where Necessary and Feasible, of Expanded Vegetation Clearances from Transmission Lines in HFRA | Transmission expanded line clearances to mitigate the risk of vegetation contact with energized conductors | Reduce Contact From Vegetation Risk | Vegetation Management & Inspections | 8.2 | Clearance |  | 8.2.3.3 | VM-8 | Vegetation Management & Inspections_Clearance_VM-8_2023 | TBD | Contact from vegetation ignition likelihood | Yes | # of grids | SCE plans to inspect 1,000 grids within our transmission system | 152 | 619 | 884 | 1000 |  |  |  |  | Quantitative Initiative |  |  |  |  | In Progress
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | LiDAR Distribution Vegetation Inspections | LiDAR as an inspection and measurement tool acquired via air patrol to identify clearances between high-voltage distribution lines and vegetation. | Make substantial progress on evaluation of incorporation of remote sensing technology into vegetation inspections | Vegetation Management & Inspections | 8.2 | Vegetation Inspections |  | 8.2.2.1 | VM-9 | Vegetation Management & Inspections_Vegetation Inspections_VM-9_2023 | TBD | N/A | Yes | # circuit miles | SCE will inspect at least 1,020 HFRA circuit miles *Subject to change based on technology, program adjustments, and grid/circuits layout | 0 | 650 | 1020 | 1020 |  |  |  |  | Quantitative Initiative |  |  |  |  | In Progress
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Customer Education and Engagement - Community Meetings | Community meetings, primarily in SCE's HFRA, to share information about SCE’s WMP efforts. | Share grid hardening, PSPS, and emergency preparedness updates, and highlight SCE's various programs, services, and resources. Also, receive direct feedback from meeting participants. | Emergency Planning & Preparedness | 7.3.10 | Public Outreach and Education Awareness Program |  |  | DEP-1.2 | Emergency Planning & Preparedness_Public Outreach and Education Awareness Program_DEP-1.2_2022 | 491 | N/A | No | # of meetings | SCE will host at least nine wildfire community safety meetings in targeted communities based on the impact of 2021 PSPS events and ongoing wildfire mitigation activities. | 0 | 9 | 9 | 9 | 0 YTD; 9 meetings currently scheduled for Q2 | 10 | Met target in Q2 | Met target in Q2 | Quantitative Initiative |  |  |  |  | Completed
SCE | 2023-02-01 | Project | 2022-01-01 | 2022-12-31 | Customer Education and Engagement, Marketing Campaign | The marketing campaign seeks to educate customers about PSPS and emergency preparedness and reduce the impact of a PSPS or a wildfire primarily through three methods: (1) advertising campaign; (2) social media; and (3) direct customer mailings. | Raise awareness about the purpose of PSPS, emergency preparedness, and SCE’s wildfire mitigation plan | Emergency Planning & Preparedness | 7.3.10 | Public Outreach and Education Awareness Program |  |  | DEP-1.3 | Emergency Planning & Preparedness_Public Outreach and Education Awareness Program_DEP-1.3_2022 | 502 | N/A | No | % PSPS awareness | PSPS Awareness goal: 50% | 50% | 50% | 50% | 50% | 55% | 53% | 52% | 57% | Quantitative Initiative |  |  |  |  | Completed
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | SCE Emergency Response Training | Technical training programs that prepare employees to perform their jobs safely, comply with regulatory requirements and laws, maintain system reliability, and leverage new technology | Provide effective emergency response and restore service during and after a major event. | Emergency Planning & Preparedness | 7.3.9 | Public Outreach and Education Awareness Program |  |  | DEP-2 | Emergency Planning & Preparedness_Public Outreach and Education Awareness Program_DEP-2_2022 | 477 | N/A | No | # trained | IMT – Have all PSPS IMT and Task Force members fully trained and qualified or requalified by July 1, 2022 UAS – SCE plans to expand the program by technically qualifying 50 UAS Operators that have passed the FAA 107 exam. | IMT: PSPS IMT Training and Exercise Kick-off UAS: 20 | IMT: PSPS IMT Trained in all Requalification Training Requirements & conduct readiness exercise UAS: 35 | IMT: 0 UAS: 50 | IMT: 0 UAS: 50 | IMT: Training and IMT Exercise kicked-off in Q1. Training to begin in Q2. UAS: 21 | IMT: 346 UAS: 43 | IMT: 346 UAS: 56 | Met target in Q3 | Quantitative Initiative |  |  |  |  | Completed
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Customer Research and Education | SCE develops surveys to capture customer feedback on SCE’s wildfire mitigation initiatives with a special emphasis on PSPS activities | Improve its understanding of how to reduce impacts of wildfires, PSPS, and wildfire mitigation work for its customers. | Emergency Planning & Preparedness | 7.3.10 | Community engagement |  |  | DEP-4 | Emergency Planning & Preparedness_Community engagement_DEP-4_2022 | 507 | N/A | No | # of surveys | SCE plans to conduct at least five PSPS‐related customer studies in 2023 | Begin PSPS Tracker data collection | Administer community meeting feedback surveys (contingent upon meeting dates) | 0 | Administer community meeting feedback surveys (contingent upon PSPS event) | PSPS tracker questionnaire was finalized, and data collection has begun. Residential and Non-Residential customers will be contacted via phone and web-based surveys. | Completed 4 out of six surveys. SCE plans to conduct a total of six surveys, However, two of the surveys haven't yet been administered because there have not been any PSPS de-energization events. | Completed 4 out of six surveys. SCE plans to conduct a total of six surveys, This activity is on-going and remaining surveys will be administered as PSPS de-energization events occur. | SCE met target in Q4 by conducting 6 PSPS related surveys, including PSPS Tracker Survey, Wildfire Safety Community Meeting Feedback Survey, CRC/CCV Feedback Survey, In‐Language Wildfire Mitigation Communications Effectiveness Survey, PSPS Working Group and Advisory Board Survey, and the Voice of | Quantitative Initiative |  |  |  |  | Completed
SCE | 2023-02-01 | Project | 2022-01-01 | 2022-12-31 | Aerial Suppression | SCE funds up to four aerial firefighting helicopters, support personnel and equipment to bolster firefighting capabilities | Fire suppression within SCE’s service area | Emergency Planning & Preparedness | 7.3.10 | Cooperation with suppression agencies |  |  | DEP-5 | Emergency Planning & Preparedness_Cooperation with suppression agencies_DEP-5_2022 | 512 | N/A | No | # of MOU | Will enter into a Memorandum of Understanding (MOU) with local county fire departments to provide standby cost funding for up to five aerial suppression resources strategically placed around the SCE service area | 0 | 6 | 6 | 6 | Draft MOUs were sent to Los Angeles County Fire Department, Orange County Fire Association and Ventura County Fire Department; and all three counties provided MOU draft comments in late Q1. | SCE has met funding target of five aerial suppression resources by having three Memoranda of Understanding (MOUs) signed by SCE and each respective county. | Activity completed in Q2 | Activity completed in Q2 | Quantitative Initiative |  |  |  |  | Completed
SCE | 2023-02-01 | Project | 2022-01-01 | 2023-12-31 | Wildfire Safety Data Mart and Data Management (WiSDM / Ezy) | Centralized wildfire data repository (WiSDM) and SCE's asset inventory (Ezy) | Streamline collection of and reporting out of SCE's wildfire mitigation efforts | Data Governance | 7.3.7 | Centralized repository for data |  |  | DG-1 | Data Governance_Centralized repository for data _DG-1_2022 | 462 | N/A | No | Qualitative Initiative | Qualitative Initiative | [8 empty] | Ezy Data: 1) Expand cloud Artificial Intelligence (AI) platform 2) Enable LIDAR data storage capability WiSDM: 1) Complete wildfire data repository design 2) Consolidate wildfire data storage onto wildfire data repository platform | Ezy Data deployed the Digital Accelerator (DA) image quality model integration on cloud platform and working to refine model capabilities, and finalizing LiDAR business capability definition. WiSDM: Process revalidation and data mapping continues. Common data repository design in progress to baseline system requirements for OEIS data reporting in Q2. | Ezy Data: 1) Activity scope was completed in May following the deployment of two new Distribution defect detection models. 2) LiDAR Data Storage and Integration project's preliminary analysis is in progress. WiSDM: 1) Completed wildfire data repository design 2) Completed ~70 Energy Safety dataset mapping for Q2. Identified >70 datasets needed to be worked on in WiSDM | Ezy Data: 1) Activity scope was completed in May following the deployment of two new Distribution defect detection models. 2) Initiated solution design for the LiDAR data integration scope. Working to complete Architecture Vision Diagram (AVD) by end of Q44 WiSDM: 1) Completed wildfire data repository design 2) Ingestion and ontology mapping for OEIS datasets has been completed and currently working to complete validation and acceptance datasets. | Ezy Data: 1) Activity scope was completed in Q2 following the deployment of two new Distribution defect detection models. 2) Completed the solution design and analysis for Lidar data. WiSDM: 1) Completed wildfire data repository design 2) Successfully met in Q4 with the data mapping, ingestion, and verification of 70+ datasets into the WiSDM platform. | Completed
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Transmission High Fire Risk Informed Inspections in HFRA | Transmission equipment and structures inspections beyond the GO 95 and GO 165 requirements | Detect equipment anomalies and mitigate ignition risks that cannot be detected during compliance ‐ driven programs alone | Asset Management & Inspections | 7.3.4 | Other discretionary inspection of transmission electric lines and equipment, beyond inspections mandated by rules and regulations |  |  | IN-1.2 | Asset Management & Inspections_Other discretionary inspection of transmission electric lines and equipment, beyond inspections mandated by rules and regulations_IN-1.2_2022 | 375 | N/A | No | # of structures in HFRA | Inspect 16,000 structures in HFRA via both ground and aerial inspections. Subject to resource constraints and other factors SCE will strive to inspect up to 19,000 structures in HFRA via both ground and aerial inspections. This target includes HFRI inspections, compliance due structures in HFRA and emergent risks identified during the fire season | Ground: 2947 Aerial: 4915 | Ground: 10526 Aerial: 12723 | Ground: 15579 Aerial: 14965 | Ground: 16000 Aerial: 16000 | Ground: 3138 Aerial: 6461 | Ground: 13,132 Aerial: 13,787 | Ground: 17,131 Aerial: 16,702 | Ground: 17,225 Aerial: 17,133 | Quantitative Initiative |  |  |  |  | Completed
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Detailed inspections and management practices for vegetation clearances around transmission infrastructure lines, and equipment | Visual inspections and maintenance of vegetation around the transmission right‐of‐ way, where individual trees are carefully examined, visually, and the condition of each rated and recorded. | Reduce CFO Veg | Vegetation Management & Inspections | 7.3.5 | Detailed inspections of vegetation around transmission electric lines and equipment |  |  | N/A | Vegetation Management & Inspections_Detailed inspections of vegetation around transmission electric lines and equipment _N/A_2022 | 396 | N/A | No | # of trees inspected | In its HFRA for 2022, SCE plans to inspect approximately 100,000 trees adjacent to transmission lines, based on current unique tree inventory count. Tree inventory is subject to fluctuations based on actual field conditions. | 7053 | 71462 | 97316 | 100000 | 17523 | 64969 | 71886 | 74025 | Quantitative Initiative |  |  |  |  | Completed
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Emergency response vegetation management due to red flag warning or other urgent climate condition | Plan and execution of vegetation management activities, such as trimming or removal, executed based upon and in advance of forecast weather conditions that indicate high fire threat in terms of ignition probability and wildfire consequence. | Reduce CFO Veg | Vegetation Management & Inspections | 7.3.5 | Emergency response vegetation management due to red flag warning or other urgent conditions |  |  | N/A | Vegetation Management & Inspections_Emergency response vegetation management due to red flag warning or other urgent conditions _N/A_2022 | 400 | N/A | No | # poles brushed | SCE will inspect and clear (where clearance is needed) approximately 26,400 poles in identified Areas of Concern (AOC), with the exception of poles for which there are customer access or environmental constraints. These poles are included in the count of the Expanded Pole Brushing (VM-2) goal. | 15050 | 20903 | 27870 | 27870 | 15161 | 23475 | 27087 | 27518 | Quantitative Initiative |  |  |  |  | Completed
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Poles Brushed per PRC 4292 | SCE inspects and clears (where clearance is needed) poles in State Responsibility Area with the equipment identified by PRC 4292 | Reduce CFO Veg | Vegetation Management & Inspections | 7.3.5 | Fuel management and reduction of “slash” from vegetation management activities |  |  | N/A | Vegetation Management & Inspections_Fuel management and reduction of “slash” from vegetation management activities _N/A_2022 | 407 | N/A | No | # of poles brushed (cleared) | SCE will inspect and clear (where clearance is needed) 55,100 poles in State Responsibility Area with the equipment identified by PRC 4292, with the exception of poles for which there are customer access or environmental constraints, or poles that are exempt under 14 Cal. Code of Regulations 1255 (e.g., poles in fruit orchards that are plowed or cultivated). | 20938 | 44080 | 55100 | 55100 | 21796 | 49211 | 58127 | 72328 | Quantitative Initiative |  |  |  |  | Completed
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | LiDAR Vegetation Inspections – Distribution | SCE is piloting the use of remote sensing LiDAR to conduct vegetation inspections around distribution electric lines and equipment | Reduce CFO Veg | Vegetation Management & Inspections | 7.3.5 | LiDAR inspections of vegetation around distribution electric lines and equipment |  |  | N/A | Vegetation Management & Inspections_LiDAR inspections of vegetation around distribution electric lines and equipment _N/A_2022 | 410 | N/A | No | # of Circuit Miles | SCE will inspect at least 500 HFRA circuit miles | 0 | 317 | 500 | 500 | 0 | 785 | 1207 | Met Target in Q3 | Quantitative Initiative | Completed inspection of 0 HFRA circuit miles. Inspections planned to begin in May and be completed in Q3 |  |  |  | Completed
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | LiDAR Vegetation Inspections – Transmission | SCE utilizes LiDAR technology to inspect select transmission and sub‐transmission lines for appropriate clearances between SCE’s lines and vegetation. | Reduce CFO Veg | Vegetation Management & Inspections | 7.3.5 | LiDAR inspections of vegetation around transmission electric lines and equipment |  |  | N/A | Vegetation Management & Inspections_LiDAR inspections of vegetation around transmission electric lines and equipment _N/A_2022 | 412 | N/A | No | # of Circuit Miles | SCE will inspect at least 1600 HFRA circuit miles | 708 | 1386 | 1539 | 1600 | 748 | 1481 | 1628 | 1696 | Quantitative Initiative |  |  |  |  | Completed
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Vegetation Inspections Audited Annually | Quality Control audits of Vegetation Management Inspections | Ensure vegetation management inspections are performed to standard | Vegetation Management & Inspections | 7.3.5 | Quality assurance / quality control of inspections |  |  | N/A | Vegetation Management & Inspections_Quality assurance / quality control of inspections_N/A_2022 | 416 | N/A | No | % of vegetation inspections audited | SCE plans to perform risk-based circuit mile Quality Control (QC) inspections on approximately 15% of SCEs total tree inventory. | 63000 | 126000 | 189000 | 252000 | 111729 | 215492 | 320779 | 468857 | Quantitative Initiative |  |  |  |  | Completed
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Recruiting and training of vegetation management personnel | SCE recruits and trains qualified personnel, including ISA‐certified arborists | Training in intended to ensure arborists perform quality and timely vegetation management work | Vegetation Management & Inspections | 7.3.5 | Recruiting and training of vegetation management personnel |  |  | N/A | Vegetation Management & Inspections_Recruiting and training of vegetation management personnel_N/A_2022 | 420 | N/A | No | # ISA Certified Arborists | Maintain the current staffing levels of 95 International Society of Arboriculture (ISA) certified arborists performing work within SCEs service territory. Inclusive of SCE personnel and contractors. | 95 | 95 | 95 | 95 | 148 | 169 | 173 | 175 | Quantitative Initiative |  |  |  |  | Completed
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Substation Inspections | SCE inspects vegetation around its substations for potential mitigation. | Reduce CFO Veg | Vegetation Management & Inspections | 7.3.5 | Substation inspections |  |  | N/A | Vegetation Management & Inspections_Substation inspections_N/A_2022 | 428 | N/A | No | # of inspections | SCE performs substation inspections on 169 substations in HFRA. SCE plans to inspect all 169 substations, 5 times a year for GO174 Substations (146 Substations) and ISO & FERC Substations (23 Substations), for a total of 845 inspections. | 277 | 553 | 772 | 845 | 297 | 587 | 919 | 1283 | Quantitative Initiative |  |  |  |  | Completed
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Substation vegetation management | SCE manages vegetation-caused risks around its substation | Reduce CFO Veg | Vegetation Management & Inspections | 7.3.5 | Substation vegetation management |  |  | N/A | Vegetation Management & Inspections_Substation vegetation management _N/A_2022 | 429 | N/A | No | # of inspections | SCE will perform Vegetation Management substation inspections in Tier 2 & Tier 3 totaling 169 substations. | 25 | 97 | 169 | 169 | 26 | 103 | 175 | 175 | Quantitative Initiative |  |  |  |  | Completed
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Customer Care Programs | SCE offers customer care programs to help mitigate the impacts of PSPS to our customers including CRCs, Community Resiliency Programs, and Customer Resiliency Equipment. | Helps customers mitigate the impacts and consequences of PSPS and other emergencies | Grid Operations & Operating Protocols | 7.3.6 | PSPS events and mitigation of PSPS impacts |  |  | PSPS-2 | Grid Operations & Operating Protocols_PSPS events and mitigation of PSPS impacts _PSPS-2_2022 | 448 | N/A | No | # of enrollments # of rebates | Customer Resiliency Equipment: CCBB: Enroll 2,750 customers in the CCBB program (35% of forecasted eligible population). Continue to identify new eligible customers each month to offer program. Portable Power Station Rebates and Portable Generator Rebates: SCE to issue 3,000 rebates and will strive to issue 4,000 rebates. | CCBB: 659 Rebates: 487 | CCBB: 1719 Rebates: 1369 | CCBB: 2427 Rebates: 2281 | CCBB: 2750 Rebates: 3000 | CCBB: 468 Rebates: 379 | CCBB: Enrollments: 965 CCBB Deployments: 853 Rebates: 986 | CCBB: Enrollments: 1,888 CCBB Deployments: 853 Rebates: 2,040 | CCBB: Enrollments: 3,733 CCBB Deployments: 3,466 Rebates: 3,145 | Quantitative Initiative |  |  |  |  | Completed
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Weather Stations | Validate real‐time conditions in the field during elevated fire conditions and are used to provide critical situational awareness for PSPS decision‐making and help improve weather models. | Help SCE make decisions during potential fire conditions, including PSPS de-energization and re-energizations | Situational Awareness and Forecasting | 7.3.2 | Advanced weather monitoring and weather stations |  |  | SA-1 | SCE_Situational Awareness and Forecasting_Advanced weather monitoring and weather stations_SA1_2022 | 265 | N/A | No | # of weather stations installed | Install 150 weather stations in SCE's HFRA. SCE will strive to install up to 175 weather stations in SCE's HFRA, subject to resource and execution constraints | 0 | 50 | 110 | 150 | 26 | 115 | 136 | 160 | Quantitative Initiative |  |  |  |  | Completed
SCE | 2023-02-01 | Project | 2022-01-01 | 2023-12-31 | High Definition (HD) Cameras | HD camera installations resolves gaps in SCE’s spatial data and provides improved fire confirmation capabilities | Helps IMTs and first responders more quickly assess and respond to reported fires | Situational Awareness and Forecasting | 7.3.2 | High Definition (HD) Cameras |  |  | SA-10 | SCE_Situational Awareness and Forecasting_High Definition (HD) Cameras_SA10_2022 |  | N/A | No | # of HD cameras installations | Install 10 HD Cameras. SCE will strive to install up to 20 HD Cameras, subject to resource and execution restraints.​ | [5 empty] | 6 | 8 | 16 |  | Worked with local Fire Management Officers and Alert Wildfire PI to identify and validate installation locations. Installations to begin in Q2.​ |  |  |  | Completed
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Weather and Fuels Modeling | Weather and fuels modeling including weather forecasts and historic weather data spanning the entire SCE service area | Maintain and enhance operational weather and fuel forecasting capabilities | Situational Awareness and Forecasting | 7.3.2 | Weather forecasting and estimating impacts on electric lines and equipment |  |  | SA-3 | SCE_Situational Awareness and Forecasting_Weather forecasting and estimating impacts on electric lines and equipment_SA3_2022 | 283 | N/A | No | Qualitative Initiative | Qualitative Initiative | [6 empty] | 564 | 564 | Equip 400 weather station locations with machine learning capabilities. SCE will strive to equip up to 500 weather station locations with machine learning capabilities, subject to resource and execution constraints. | Point locations were provided to vendor to assess data quality and suitability to build new machine learning models. Vendor began training new machine learning models across SCE territory and performed new model verifications. . Machine learning to be operationalized in Q3. | Completed testing of new machine learning models in the test environment and successfully operationalized all new machine learning models in the production environment. Completed testing the new machine learning output within existing tools in the Foundry platform and Legacy tools without issue. Operationalizing of the software to all 400 stations simultaneously is scheduled for November 2022. | SCE met target in Q3 by equipping 564 weather station locations with machine learning capabilities. | SCE met target in Q3 by equipping 564 weather station locations with machine learning capabilities. | Completed
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Fire Science Enhancements | Various modeling tools to predict fire ignition and consequence outputs such as fire perimeter size, structures impacted, populations affected, and injury and death | Expand data analysis, emphasize fire potential forecasting, and improve modeling efforts as it relates to fire science | Situational Awareness and Forecasting | 7.3.2 | Forecast of a fire risk index, fire potential index, or similar |  |  | SA-8 | SCE_Situational Awareness and Forecasting_Forecast of a fire risk index, fire potential index, or similar_SA8_2022 | 275 | N/A | No | Qualitative Initiative | Qualitative Initiative | [8 empty] | Calibrate FPI 2.0 and evaluate its performance over the 2022 fire season. Improve fire spread modeling applications (i.e., FireSim and FireCast) to include 1) fire suppression and 2) buildings destroyed by fire | Calibration of FPI 2.0 by Fire Climate Zones using historical fire occurrence data continues. The calibration has been completed for the Fuels Index component. The Purchase Order (PO) to support fire spread modeling application work was issued and signed in Q1. Coordination with vendor to draft a project plan to support development of the Building Loss Factor metric for evaluation has begun. | Calibration of FPI 2.0: Continuing with the development of a Fire Behavior Metric related to FPI2's components. Development of the metrics to evaluate FPI 2.0 against the current FPI is on schedule. Fire Spread Modeling: The Building Loss Factor and Suppression Effectiveness Simulation metrics are under development and will be evaluated for reliability in Q4. | FPI 2.0 continues to be evaluated at circuit level during critical fire weather events. Fire Behavior Matrix is complete and operational; 41-year historical perspective data is also available. Building Loss Factor has been integrated into FireCast and Suppression Effectiveness Simulation, metrics are currently being assessed by Fire Science team | SCE met target by updating the FPI 2.0 methodology to include calibration and verification statistics. Building Loss Factor and a metric measuring suppression effectiveness have also been integrated into FireCast and is being evaluated for integration of fire spread modeling into the PSPS decision-making process. | Completed
SCE | 2023-02-01 | Project | 2022-01-01 | 2022-12-31 | Distribution Fault Anticipation (DFA) | DFA technology incorporates electrical system measurements to detect the potential for pending equipment failures. These devices continually monitor circuits to detect and assist with locating and categorizing electrical events (e.g., incipient and traditional faults). | DFA installations can assist in detecting incipient fault conditions and provide remote access to fault data. The remote fault data can help locate faults where conventional circuit patrols were unable to determine a cause. | Situational Awareness and Forecasting | 7.3.2 | Continuous monitoring sensors |  |  | SA-9 | SCE_Situational Awareness and Forecasting_Continuous Monitoring sensors_SA9_2022 | 269 | N/A | No | Qualitative Initiative | Qualitative Initiative | [8 empty] | SCE will evaluate the performance of installed fault anticipation technology and develop recommendations for future use by year-end 2022 | Distribution Fault Anticipation (DFA) events reviewed internal to SCE in Q1 and 4 events reviewed external with the vendor. 50% of the first draft report is complete. | All DFA events were reviewed internal to SCE; prepared first draft of report. | SCE met target in Q3 by completing evaluation of performance of installed fault anticipation technology and developing recommendations for future use. Overall, there were 1,121 total events reviewed internally; and 18 events with the vendor. Recommended improvements to future use have been summarized in final report. | SCE met target in Q3 by completing evaluation of the performance of installed fault anticipation technology and developing recommendations for future use. Overall, there were 1,121 total events reviewed internally; and 18 events with the vendor. Recommended improvements for future use have been summarized in a final report | Completed
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Covered Conductor | Replacing bare wire with conductor / components (fire-resistant poles, composite crossarms, FR3 transformers, wildlife covers, surge arresters, polymer insulators and vibration dampers) to protect against the arcing, faults, or energy release that can come from incidental contact. | Reduce CFO, EFF and Wire-to-Wire Risk | Grid Design & System Hardening | 7.3.3 | Covered conductor installation |  |  | SH-1 | Grid Design & System Hardening_Covered conductor installation _SH-1_2022 | 294 | N/A | No | # of circuit miles in HFRA | Install 1,100 circuit miles of covered conductor in SCE’s HFRA. SCE will strive to install up to as many as 1,250 circuit miles of covered conductor in SCE’s HFRA, subject to resource constraints and other execution risks. | 250 | 555 | 855 | 1100 | 274 | 649 | 1073.99 | ~1,412 | Quantitative Initiative |  |  |  |  | Completed
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Tree Attachment Remediation | Program removes electrical equipment from trees and installs them on new fire-resistant poles | Reduce EFF Risk | Grid Design & System Hardening | 7.3.3 | Covered conductor installation |  |  | SH-10 | Grid Design & System Hardening_Covered conductor installation _SH-10_2022 | 301 | N/A | No | # of tree attachment remediations | Remediate 500 tree attachments in SCE’s HFRA. SCE will strive to complete up to 700 tree attachment remediations in SCE’s HFRA, subject to resource constraints and other execution risks. | 20 | 184 | 480 | 500 | 266 | 338 | 562 | 964 | Quantitative Initiative |  |  |  |  | Completed
SCE | 2023-02-01 | Project | 1//1/2022 | 2022-12-31 | Legacy Facilities | Risk assessment and hardening of high and low voltage equipment supporting hydroelectric operations. | Reduce wildfire risk on legacy facilities | Grid Design & System Hardening | 7.3.3 | Updates to grid topology to minimize risk of ignition in HFTDs |  |  | SH-11 | Grid Design & System Hardening_Updates to grid topology to minimize risk of ignition in HFTDs _SH-11_2022 | 340 | N/A | No | # sites | Hydro Control Circuits: Based on 2021 assessments, perform grid hardening on three control circuits at three legacy facility sites. Low Voltage Site Hardening: Based on 2021 assessment, perform one grid hardening project at a legacy facility site Grounding Studies/Lightning Arrestor Assessments and Remediations: Based on 2021 assessments perform four remediation projects at legacy facility sites. Additionally, complete 13 assessments. | 2 0 0 | 7 0 0 | 22 0 0 | 32 0 17 | 0 0 0 | Hydro Control Circuits: Two of the three assessments finalized approved and scheduled for completion in 2022. Remediations scheduled for Q4 Low Voltage Site Hardening: Internal resources secured to complete grid hardening in Q3 Grounding Studies/Lightning Arrestor: 2 circuits are pending expense charges to begin construction. One circuit design has been approved and is in Environmental review. | Hydro Control Circuits: : 2 out of 3 circuits to be completed by YE. Low Voltage Site Hardening: Isolation of disconnect panel from bare conductor is complete. Pending removal of bare conductor by T&D in Q4. Grounding Studies/Lightning Arrestor: 4 assessments completed, 6 preliminary assessments under T&D review. 4 remediation projects scheduled for completion in Q4. Please see appendix slide for further details. | Grounding Studies/Lightning Arrestor: SCE met target in Q4 by completing 4 remediation projects and 13 assessments. Low Voltage Site Hardening: SCE met target in Q4 by performing one grid hardening project at a legacy facility. Hydro Control Circuits: Work at 2 of 3 control circuits completed. Remaining control circuit project will be completed in Q3 2023. Please see appendix slide for further details. | Quantitative Initiative |  |  |  |  | Delayed | Hydro Control Circuit: Remaining control circuit project will be completed in Q3 2023. SCE submitted water permitting request to the water agency, California Department of Fish and Wildlife (CDFW) on 9/2; draft agreement under review by SCE. Feedback from CDFW expected in January 2023 The remaining project must be completed in conjunction with another covered conductor project that is pending environmental permitting and is scheduled to complete in Q3 2023.
SCE | 2023-02-01 | Project | 2022-01-01 | 2022-12-31 | Microgrid Assessment | SCE is planning to install a microgrid to reduce the consequence of PSPS in a location heavily impacted by PSPS. | Having a microgrid maintains system reliability and minimize customer impact during deenergization events. | Grid Design & System Hardening | 7.3.3 | Grid topology improvements to mitigate or reduce PSPS events |  |  | SH-12 | Grid Design & System Hardening_Grid topology improvements to mitigate or reduce PSPS events _SH-12_2022 | 311 | N/A | No | Qualitative Initiative | Qualitative Initiative | [8 empty] | SCE will actively attempt to obtain approval of easement with the landowner of the microgrid site, and if approval is received, SCE will move forward with microgrid project. If an approval is not received by June 30, 2022, or rejected, SCE will start to pursue other microgrid opportunities | SCE continues to discuss with land owner approval of easement for microgrid site. The site location requires a vote and approval to grant easement. Vote was postponed from Q1 to Q2. | Prospective customer elected not to move forward with the land lease agreement. Project team will be conducting assessment to determine feasibility of pursuing other microgrid opportunities | Prospective customer elected not to move forward with the land lease agreement. Resource constraints has caused assessment to determine feasibility of pursuing other microgrid opportunities to fall behind plan.. However, resources will be made available to screen for sites and expect to return on-track status in Q4. Please see appendix slide for further details. | SCE met target in Q4 by completing assessments on other potential microgrid sites after unsuccessfully obtaining an easement agreement with the landowner of the proposed microgrid site. No new sites were identified in the subsequent assessment. SCE will continue to re-evaluate its approach, re-run its assessment, and explore potential cooperative opportunities for microgrids. | Completed
SCE | 2023-02-01 | Project | 2022-01-01 | 2022-12-31 | C-Hooks | Replacement of C‐Hooks installed in the SCE's system. | Replacing C-Hooks before they failure, which could lead to downed high voltage wire which can pose wildfire and public safety risks. | Grid Design & System Hardening | 7.3.3 | Transmission tower maintenance and replacement |  |  | SH-13 | Grid Design & System Hardening_Transmission tower maintenance and replacement _SH-13_2022 | 331 | N/A | No | # of C-hooks | SCE will replace C‐Hooks on 10 structures in SCE’s HFRA and strive to replace up to 21 C‐Hooks, subject to execution risks such as environmental clearance | 3 | 6 | 10 | 10 | 3 | 6 | 9 | 10 | Quantitative Initiative |  |  |  |  | Completed
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Long Span Initiative | LiDAR on distribution long spans helps to identify locations with potential conductor clash issues and remediates the highest risk locations upon field validation | Reduce Wire to Wire Risk | Grid Design & System Hardening | 7.3.3 | Other corrective action |  |  | SH-14 | Grid Design & System Hardening_Other corrective action _SH-14_2022 | 321 | N/A | No | # of assessments | Remediate 1,400 spans in SCE’s HFRA. SCE will strive to remediate up to 1,800 spans in SCE’s HFRA, subject to resource constraints and other execution risks. | 210 | 490 | 980 | 1400 | 935 | 1482 | 1618 | 1694 | Quantitative Initiative |  |  |  |  | Completed
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Vertical Switches | Upgrading switches in need of replacement as older switches may generate incandescent particles if not properly adjusted or constructed. | Reduce EFF Risk | Grid Design & System Hardening | 7.3.3 | Updates to grid topology to minimize risk of ignition in HFTDs |  |  | SH-15 | Grid Design & System Hardening_Updates to grid topology to minimize risk of ignition in HFTDs _SH-15_2022 | 341 | N/A | No | # of switches | Install 15 vertical switches in SCE’s HFRA. SCE will strive to install 25 vertical switches in SCE’s HFRA | 4 | 7 | 11 | 15 | 4 | 4 | 10 | 16 | Quantitative Initiative |  |  |  |  | Completed
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Vibration Damper Retrofit | Retrofit aims to stop wind-driven vibration (known as Aeolian vibration) that may lead to conductor abrasion or fatigue over time. | Reduce Wire to Wire Risk | Grid Design & System Hardening | 7.3.3 | Covered conductor installation |  |  | SH-16 | Grid Design & System Hardening_Covered conductor installation _SH-16_2022 | 303 | N/A | No | # structures | Retrofit vibration dampers on 100 structures where covered conductor is already installed in SCE’s HFRA. SCE will strive to retrofit vibration dampers on up to 115 structures where covered conductor is already installed in SCE’s HFRA. | 0 | 15 | 50 | 100 | Construction began in Q1, completed 33 installations. There are some back-office activities continuing to be addressed including monitoring material availability. | 36 | 62 | 127 | Quantitative Initiative |  |  |  |  | Completed
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Rapid Earth Fault Current Limiter | Detects ground faults on one phase of a three-phase powerline and rapidly reduces the voltage on the faulted conductor while boosting the voltage on the two remaining phases. Ignitions caused by single phase to ground faults can be mitigated with the use of the Ground Fault Neutralizer which reduces fault energy. | Reduce CFO and EFF Risk | Grid Design & System Hardening | 7.3.3 | Other corrective action |  |  | SH-17 | Grid Design & System Hardening_Other corrective action _SH-17_2022 | 323 | N/A | No | Qualitative Initiative | SCE will produce a report summarizing performance and lessons learned from previous REFCL installations. SCE will also initiate engineering and material purchase for the ground fault neutralizers (GFNs) to be constructed in 2023 at Acton and Phelan Substations. | [8 empty] | SCE will produce a report summarizing performance and lessons learned from previous REFCL installations. SCE will also initiate engineering and material purchase for the ground fault neutralizers (GFNs) to be constructed in 2023 at Acton and Phelan Substations. | Ground fault neutralizer is in service, and performance continues to be monitored. Finalized specifications and material order to initiate engineering and material purchase for ground neutralizers, and. engineering design contract awarded. | REFCL: Ground fault neutralizer is in service, and performance continues to be monitored. Assessment to be completed in Q3. GFN: Acton circuit balancing plans complete and work scope currently in design. Continuing work on lightning arrestor replacement scope finalization at Phelan substation. | Designs in progress for phase-to-neutral conversions and Capacitive Balancing Unit (CBU) installs. Factory Acceptance Testing for the ground fault neutralizer scheduled for Q4. Continue documentation of lessons learned for in-service ground fault neutralizer with report scheduled for completion in Q4. | SCE met target in Q4 to produce report summarizing performance from previous REFCL installations and initiated engineering and material purchase for the ground fault neutralizers (GFNs) to be constructed in 2023 at Acton and Phelan substations. | Completed
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Undergrounding Overhead Conductor | Undergrounding greatly reduces wildfire and PSPS risk by virtually eliminating the possibility for objects to contact energized conductor as well as greatly limiting the ignition-causing potential from equipment failures | Reduce CFO, EFF and Wire-to-Wire Risk | Grid Design & System Hardening | 7.3.3 | Undergrounding of electric lines and/or equipment |  |  | SH-2 | Grid Design & System Hardening_Undergrounding of electric lines and/or equipment _SH-2_2022 | 334 | N/A | No | # of circuit miles in HFRA | Install 11 circuit miles of targeted undergrounding in SCE’s HFRA. SCE will strive to install up to 13 miles of targeted undergrounding in SCE’s HFRA, subject to resource constraints and other execution risks. | 0 | 8 | 9 | 11 | Currently 3 underground miles are in construction and will be completed in Q2. 9 underground miles have been authorized to proceed with an overall year end target of 11. | ~2 | 5.34 | ~14 | Quantitative Initiative |  |  |  |  | Completed
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Branch Line Protection Strategy | Proactively installing CLFs on branch lines where no fusing previously existed and replacing conventional fuses with CLFs or other CAL FIRE “Exempt” fuse designs | Refine circuit protection strategies to further reduce wildfire risk while balancing system reliability | Grid Design & System Hardening | 7.3.3 | Expulsion fuse replacement |  |  | SH-4 | Grid Design & System Hardening_Expulsion fuse replacement _SH-4_2022 | 308 | N/A | No | # of locations with installed / replaced fuses | Install or replace fusing at 350 fuse locations that serve HFRA circuitry. SCE will strive to install or replace fusing at up to 483 locations that serve HFRA circuitry, subject to resource constraints and other execution risks. | 45 | 175 | 350 | 350 | 24 | 208 | 391 | 369 | Quantitative Initiative |  |  |  |  | Completed
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Installation of System Automation Equipment - RAR / RCS | Installing RARs and RCSs to accommodate enhanced settings which can help to sectionalize circuits and control the flow of electricity remotely | Reduce CFO and Wire-to-Wire Risk | Grid Design & System Hardening | 7.3.3 | Installation of system automation equipment |  |  | SH-5 | Grid Design & System Hardening_Installation of system automation equipment _SH-5_2022 | 313 | N/A | No | # of RARs / RCSs installed and operationalized | Install 15 sectionalizing devices such as RARs/RCSs driven by the results of evaluations / assessments conducted under SH-6 and SH-7. SCE will strive to install up to 31 sectionalizing devices such as RARs/RCSs driven by the results of evaluations / assessments conducted under SH-6 and SH-7, subject to resource constraints and other execution risks | 0 | 3 | 12 | 15 | Scope and design have been received. Installations to begin in Q2 | 3 | 11 | 15 | Quantitative Initiative |  |  |  |  | Completed
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Circuit Breaker Relay Hardware for Fast Curve | Upgrading circuit breakers and installing fast curve settings to increase the speed of the relay detecting a fault and deenergizes a circuit | Reduce CFO and Wire-to-Wire Risk | Grid Design & System Hardening | 7.3.3 | Circuit breaker maintenance and installation to de-energize lines upon detecting a fault |  |  | SH-6 | SCE_Grid Design & System Hardening_Circuit breaker maintenance and installation to de-energize lines upon detecting a fault_SH6_2022 | 292 | N/A | No | # of installations and placed into service | Replace/upgrade 104 relay units in SCE’s HFRA. SCE will strive to replace/ upgrade up to 125 relay units in SCE’s HFRA, subject to resource constraints and other execution risks | 0 | 12 | 81 | 104 | Design completed in Q1 with installations to begin in Q2. Procurement delays have shifted some projects into later quarters in 2022 but still expect to meet year end target. | 20 | 36 | 117 | Quantitative Initiative |  |  |  |  | Completed
SCE | 2023-02-01 | Project | 2022-01-01 | 2022-12-31 | PSPS-Driven Grid Hardening Work | Evaluating circuits highly impacted by PSPS to develop targeted plans for grid hardening and circuit modifications to reduce PSPS impact. | Reduce PSPS Risk | Grid Design & System Hardening | 7.3.3 | Grid topology improvements to mitigate or reduce PSPS events |  |  | SH-7 | Grid Design & System Hardening_Grid topology improvements to mitigate or reduce PSPS events _SH-7_2022 | 310 | N/A | No | # of highly impacted circuits evaluated | Evaluate approximately 70 highly impacted circuits including 2021 PSPS events to determine additional deployment of PSPS mitigations | 72 | 72 | 72 | 72 | 104 | Activity Completed in Q1 | Activity Completed in Q1 | Activity Completed in Q1 | Quantitative Initiative |  |  |  |  | Completed
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Transmission Open Phase Detection | Facilitates detection and de-energization of an open phase (broken transmission conductor) before it can contact a grounded object and create a fault event. | Refine circuit protection strategies to further reduce wildfire risk while balancing system reliability | Grid Design & System Hardening | 7.3.3 | Updates to grid topology to minimize risk of ignition in HFTDs |  |  | SH-8 | Grid Design & System Hardening_Updates to grid topology to minimize risk of ignition in HFTDs _SH-8_2022 | 337 | N/A | No | # of installations | Deploy open phase logic on five transmission lines. SCE will strive to deploy open phase logic on up to 11 transmission lines, subject to resource constraints and other execution risks. | 0 | 0 | 0 | 6 | Preliminary settings review completed. Currently developing finalized design packages and relay setting plans with field activities commencing in Q3. Deployment to occur in Q4. | Relay settings for six and the strive target of 11 lines have been developed, approved and issued. Wiring activities in progress on two of the lines. | SCE met target in Q3 by deploying open phase logic on 6 transmission lines. | SCE met target in Q3 by deploying open phase logic on 6 transmission lines. In Q4, open phase logic was deployed on an additional 5 transmission lines for a total of 11 transmission lines deployed with open phase logic. | Quantitative Initiative |  |  |  |  | Completed
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Hazard Tree Management Program | Identifies trees that pose a risk to electric facilities based on the tree’s observed structural integrity and site conditions. | Reduce Contact From Vegetation Risk | Vegetation Management & Inspections | 7.3.5 | Removal and remediation of trees with strike potential to electric lines and equipment |  |  | VM-1 | Vegetation Management & Inspections_Removal and remediation of trees with strike potential to electric lines and equipment _VM-1_2022 | 425 | N/A | No |  | Inspect 330 circuits and assess any trees with strike potential along those circuits. | 103 | 193 | 279 | 330 | 129 | 197 | 328 | 467 | Quantitative Initiative |  |  |  |  | Completed
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Pole Brushing | Removal of vegetation around all poles and structures subject to PRC 4292 | Reduce EFF Risk | Vegetation Management & Inspections | 7.3.5 | Fuel management and reduction of “slash” from vegetation management activities |  |  | VM-2 | Vegetation Management & Inspections_Fuel management and reduction of “slash” from vegetation management activities _VM-2_2022 | 404 | N/A | No | # of poles cleared | SCE will inspect and clear (where clearance is needed) 78,700 poles in HFRA, with the exception of poles for which there are customer access or environmental constraints. SCE will strive to inspect and clear (where clearance is needed) up to 170,000 distribution poles in HFRA. These poles are in addition to poles subject to PRC 4292. | 29906 | 47220 | 66108 | 78700 | 30749 | 52652 | 80379 | 105377 | Quantitative Initiative |  |  |  |  | Completed
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Expanded Clearances for Legacy Facilities | Remove / clear additional vegetation using the standard remediation methods of trims, removals, and/or weed abatement to render the defensible space around a generation facility even more vegetation free | Reduce Contact From Vegetation and EFF Risk | Vegetation Management & Inspections | 7.3.5 | Fuel management and reduction of “slash” from vegetation management activities |  |  | VM-3 | Vegetation Management & Inspections_Fuel management and reduction of “slash” from vegetation management activities _VM-3_2022 | 407 | N/A | No | # of sites treated | Perform expanded clearances at 32 legacy facility location | 2 | 8 | 18 | 32 | 2 | 8 | 12 | 32 | Quantitative Initiative | Completed expanded clearance at 2 sites. The majority of expanded clearances are scheduled in the summertime to capture all new growth and avoid snow and weather issues. |  |  |  | Completed
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Dead and Dying Tree Removal | Patrols in HFRA to identify and remove dead, dying, or diseased trees affected by drought conditions and/or insect infestation. | Reduce Contact From Vegetation Risk | Vegetation Management & Inspections | 7.3.5 | Removal and remediation of trees with strike potential to electric lines and equipment |  |  | VM-4 | Vegetation Management & Inspections_Removal and remediation of trees with strike potential to electric lines and equipment _VM-4_2022 | 427 | N/A | No | # of grids | Inspect 900 unique circuits and prescribe mitigation for dead and dying trees with strike potential along those circuits. | 334 | 676 | 805 | 900 | 359 | 566 | 765 | 926 | Quantitative Initiative |  |  |  |  | Completed
SCE | 2023-02-01 | Project | 2022-01-01 | 2023-12-31 | VM Work Management Tool | Data Warehouse used for Routine Vegetation Management inspections and resulting mitigations | Consolidated work tracking and reporting to optimize operations and improve data accuracy | Vegetation Management & Inspections | 7.3.5 | Vegetation inventory system |  |  | VM-6 | Vegetation Management & Inspections_Vegetation inventory system _VM-6_2022 | 430 | N/A | No | Qualitative Initiative | Qualitative Initiative | [8 empty] | SCE will implement the following programs within the VM Work Management Tool, Arbora: (1) Hazardous Tree Program (HTP) (including: Dead & Dying Tree Removal and Hazard Tree Mitigation) and (2) Routine Line Clearing | HTP pilot launch in Q1 was successful. HTP full roll out is on track and expected to completed in Q2 | Full roll-out to HTMP completed in Q1 and the team continues to support implementation stabilization. Development of Routine Line Clearing functionality continues with launch date in Q3. | Full roll-out to HTMP completed in Q2 and the team continues to support implementation stabilization. In September decision was made to extend pilot period for Routine Line deployment to allow for complete testing and validation of entire Vegetation Management workflow. Routine Line will be taking phased rollout approach to begin in Q4 with full completion before year-end to meet WMP target. Please see appendix slide for further details. | SCE met target in Q4 by implementing the Vegetation Management work management tool for the Hazard Tree Program (HTP), which includes HTMP and Dead and Dying Tree removal, and for Routine Line Clearing. As with other large system implementations, SCE will continue to monitor performance, and as applicable, run legacy systems in parallel. | Completed
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Distribution High Fire Risk Informed Inspections in HFRA | Distribution equipment and structures inspections beyond the GO 95 and GO 165 requirements | Detect equipment anomalies and mitigate ignition risks that cannot be detected during compliance ‐ driven programs alone | Asset Management & Inspections | 7.3.4 | Other discretionary inspection of distribution electric lines and equipment, beyond inspections mandated by rules and regulations |  |  | IN-1.1 | Asset Management & Inspections_Other discretionary inspection of distribution electric lines and equipment, beyond inspections mandated by rules and regulations _IN-1.1_2022 | 362 | N/A | No | # of structures in HFRA | Inspect 150,000 structures in HFRA via both ground and aerial inspections. Subject to resource constraints and other factors. SCE will strive to inspect up to 180,000 structures in HFRA via both ground and aerial inspections. This target includes HFRI inspections, compliance due structures in HFRA and emergent risks identified during the fire season | Ground: 77179 Aerial: 43916 | Ground: 150000 Aerial: 120726 | Ground: 150000 Aerial: 142285 | Ground: 150000 Aerial: 150000 | Ground: 71822 Aerial: 46446 | Ground: 138807 Aerial: 136944 | Ground: 162,192 Aerial: 158,604 | Ground: 162,721 Aerial: 157,144 | Quantitative Initiative |  |  |  |  | Completed
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Infrared Inspection of Energized Overhead Distribution Facilities and Equipment | Infrared (IR) inspections on its distribution circuits that can detect conditions often not visible to the human eye | Detect deteriorated connection points on electrical equipment such as conductors, insulators, splices or connectors that over time can lead to failures if left unmitigated and pose ignition risks | Asset Management & Inspections | 7.3.4 | Infrared inspections of distribution electric lines and equipment |  |  | IN-3 | Asset Management & Inspections_Infrared inspections of distribution electric lines and equipment _IN-3_2022 | 352 | N/A | No | # of distribution circuit miles in HFRA | Inspect 4,408 distribution overhead circuit miles in HFRA | 3480 | 4408 | 4408 | 4408 | 4408 | SCE met target miles after remaining flights were completed the first week of June. ~4,408 miles of inspections were completed in 2022 against the 2-year, ~8,816 mile inspection target; ~4,409 miles of inspections completed in 2021. Approximately 50% of HFRA distribution miles were inspected in 2021 with the remainder inspected in 2022. | Met target in Q2 | Met target in Q2 | Quantitative Initiative |  |  |  |  | Completed
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Infrared Inspection, Corona Scanning, and High-Definition Imagery of Energized Overhead Transmission facilitates and Equipment | Infrared (IR) inspections on its transmission circuits that can detect conditions often not visible to the human eye | Detect deteriorated connection points on electrical equipment such as conductors, insulators, splices or connectors that over time can lead to failures if left unmitigated and pose ignition risks | Asset Management & Inspections | 7.3.4 | Infrared inspections of transmission electric lines and equipment |  |  | IN-4 | Asset Management & Inspections_Infrared inspections of transmission electric lines and equipment _IN-4_2022 | 354 | N/A | No | # of transmission circuit miles in HFRA | Inspect 1,000 transmission overhead circuit miles in HFRA | 150 | 600 | 900 | 1000 | 176 | 948 | 1075 | Met Target in Q3 | Quantitative Initiative |  |  |  |  | Completed
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Generation High Fire Risk Informed Inspections in HFRA | Inspections of generation-related assets in HFRA | Identify potential ignition risks on generation-related assets and mitigate the ignition driver risks through system hardening | Asset Management & Inspections | 7.3.4 | Generation High Fire Risk-Informed inspections and remediations in HFRA |  |  | IN-5 | Asset Management & Inspections_Generation High Fire Risk-Informed inspections and remediations in HFRA_IN-5_2022 | 373 | N/A | No | # of structures in HFRA | Inspect 190 generation-related assets in HFRA | 0 | 70 | 190 | 190 | 36 | 69 | 222 | Met target in Q3 | Quantitative Initiative |  |  |  |  | Completed
SCE | 2023-02-01 | Project | 2022-01-01 | 2023-12-31 | Inspection Work Management Tools | InspectForce is the centralized asset inspection product used for planning and executing inspections | Improves the effectiveness and speed of inspections, data quality and record accuracy, and helps ensure that information is available, accessible, and timely to support wildfire mitigation activities. | Asset Management & Inspections | 7.3.4 | Improvement of inspections |  |  | IN-8 | Asset Management & Inspections_Improvement of inspections _IN-8_2022 | 347 | N/A | No | Qualitative Initiative | Qualitative Initiative | [8 empty] | Design capability for the legacy Distribution Ground inspection application in 2022 to transition to a single digital inspection platform in a future year In support of remediation efforts, conduct assessment to identify enhancements for Field Crew application, and evaluate applicability of enhancements by year-end 2022 | InspectForce Transmission Ground was implemented in February and released in Q1, which included new survey questions and updates to notification validation logic and google maps. Completed production upgrade of the field crew iPad application with capabilities; and planning deployment of distribution activities for Q2 and Q3. | Feasibility study to migrate Inspect App to InspectForce for Ground Distribution is complete and findings are being socialized across key functional teams. Preliminary rollout plan has been developed with deployment of the iPad-based field crew application to begin Q4. | SCE has completed target to design capability for the legacy distribution ground inspection application. Inspection & Maintenance Tools Field Crew Application is On-Track towards completion for year-end target. Completed identification of enhancement capabilities, including areas of assignment, work order updates in the field, and gatekeeper workflow. Migration from InspectApp to InspectForce is tentatively scheduled for Q1 2024. Preliminary rollout plan has been developed with deployment of the iPad-based field crew application to begin Q4. | IN-8.a: SCE met target in Q3 to design capability for the legacy Distribution Ground Inspection application. Completed identification and feasibility assessment of enhancement capabilities, and migration to a single digital inspection platform is tentatively scheduled for 2024. IN-8.b: SCE met target in Q4 with the assessment, identification, and evaluation of applicability of enhancements for Field Crew application. Field Crew application enhancements were rolled out to ~60 Distribution contract users, resulting in the real time closure of notification issues in the field. | Completed
SCE | 2023-02-01 | Project | 2022-01-01 | 2023-12-31 | Transmission Conductor and Splice Assessment | Identification of anomalies / issues in order to replace or remediate conductors and/or splices that have a higher probability of failure | Reduce transmission conductor wire down events | Asset Management & Inspections | 7.3.4 | Infrared inspections of transmission electric lines and equipment |  |  | IN-9 | Asset Management & Inspections_Infrared inspections of transmission electric lines and equipment _IN-9_2022 | 356 | N/A | No | # Spans/splices Inspections | Will inspect 75 spans with Line Vue, inspect 50 splices with X-Ray and obtain 5 Conductor Samples; SCE will strive to inspect up to 150 spans with Line Vue, inspect up to 70 splices with Xray, and obtain up to 15 Conductor Samples, subject to execution constraints. | Line Vue: 0 Splices w/X-ray: 5 Conductor Samples: 0 | Line Vue: 30 Splices w/X-ray: 35 Conductor Samples: 1 | Line Vue: 60 Splices w/X-ray: 50 Conductor Samples: 4 | Line Vue: 75 Splices w/X-ray: 50 Conductor Samples: 5 | Line Vue: 0 Splices w/X-ray: 19 Conductor Samples: 0 | Line Vue: 50 Splices w/X-ray: 57 Conductor Samples: 3 | Line Vue: 60 Splices w/X-ray: 63 Conductor Samples: SCE met target by inspecting five Conductor Samples, completed in Q3. | Line Vue: 79 Splices w/X-ray: 63 Conductor Samples: SCE met target by inspecting six Conductor Samples, completed in Q3. | Quantitative Initiative |  |  |  |  | Completed
SCE | 2023-02-01 | Program | N/A, activity classified as program | N/A, activity classified as program | Detailed inspections and management practices for vegetation clearances around distribution electrical lines, and equipment | Visual inspections and maintenance of vegetation around the distribution right‐of‐ way, where individual trees are carefully examined, visually, and the condition of each rated and recorded. | Reduce CFO Veg | Asset Management & Inspections | 7.3.5 | Detailed inspections of vegetation around distribution electric lines and equipment |  |  | N/A | Asset Management & Inspections_Detailed inspections of vegetation around distribution electric lines and equipment _N/A_2022 | 396 | N/A | No | # of trees inspected | In its HFRA for 2022, SCE plans to inspect approximately 600,000 trees adjacent to distribution lines, based on current unique tree inventory count. Tree inventory is subject to fluctuations based on actual field conditions. | 140365 | 346966 | 532922 | 600000 | 238022 | 455039 | 606402 | 656691 | Quantitative Initiative |  |  |  |  | Completed

## IPI+IR_NEW (hidden)
Actuals
[5 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Program Name | HFTD Tier | Line Type | Inspection Type | Inspection Method | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022
IR-Aerial | HFTD Tier 2 | Distribution | Other Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | 1003 | 0 | 0
IPI | HFTD Tier 2 | Distribution | Other Inspection | other | 4156.88 | 4156.88 | 4156.88 | 4156.88 | 1272.96 | 4916.08 | 3961.36 | 5194.28 | 288.6 | 1198.08 | 1133.6 | 1147.64
IR Ground | HFTD Tier 2 | Distribution | Other Inspection | other | 17057.3147 | 17057.3147 | 17057.3147 | 17057.3147 | 37811.4035 | 27362.9644 | 0 | 0 | 63105.9286 | 3507 | 0 | 0
Total | HFTD Tier 2 | Distribution | Other Inspection | other | 21214.1947 | 21214.1947 | 21214.1947 | 21214.1947 | 39084.3635 | 32456.0444 | 3961.36 | 5194.28 | 63394.5286 | 5708.08 | 1133.6 | 1147.64
IR-Aerial | HFTD Tier 3 | Distribution | Other Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 118 | 0 | 0 | 0 | 826 | 0 | 0
IPI | HFTD Tier 3 | Distribution | Other Inspection | other | 3837.12 | 3837.12 | 3837.12 | 3837.12 | 1175.04 | 4537.92 | 3656.64 | 4794.72 | 266.4 | 1105.92 | 1046.4 | 1059.36
IR Ground | HFTD Tier 3 | Distribution | Other Inspection | other | 15745.2136 | 15745.2136 | 15745.2136 | 15745.2136 | 34902.834 | 29716.9614 | 0 | 0 | 58251.6264 | 3336.8532 | 0 | 0
Total | HFTD Tier 3 | Distribution | Other Inspection | other | 19582.3336 | 19582.3336 | 19582.3336 | 19582.3336 | 36077.874 | 34372.8814 | 3656.64 | 4794.72 | 58518.0264 | 5268.7732 | 1046.4 | 1059.36
IR-Aerial | Non-HFTD | Distribution | Other Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IPI | Non-HFTD | Distribution | Other Inspection | other | 24214 | 24214 | 24214 | 24214 | 30434 | 58552 | 28910 | 19301 | 35405 | 17460 | 16198 | 29472
IR Ground | Non-HFTD | Distribution | Other Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | Non-HFTD | Distribution | Other Inspection | other | 24214 | 24214 | 24214 | 24214 | 30434 | 58552 | 28910 | 19301 | 35405 | 17460 | 16198 | 29472
IR-Aerial | HFTD Tier 2 | Transmission | Other Inspection | Aerial | 1099.3455 | 1099.3455 | 1099.3455 | 1099.3455 | 0 | 319.73 | 1664.3477 | 2601.6382 | 772.6077 | 3383.0057 | 551.8627 | 0
IPI | HFTD Tier 2 | Transmission | Other Inspection | other | 218.92 | 218.92 | 218.92 | 218.92 | 296.92 | 630.24 | 175.76 | 435.76 | 66.04 | 169.52 | 72.8 | 76.96
Total | HFTD Tier 2 | Transmission | Other Inspection | other | 1318.2655 | 1318.2655 | 1318.2655 | 1318.2655 | 296.92 | 949.97 | 1840.1077 | 3037.3982 | 838.6477 | 3552.5257 | 624.6627 | 76.96
IR-Aerial | HFTD Tier 3 | Transmission | Other Inspection | Aerial | 1014.7804 | 1014.7804 | 1014.7804 | 1014.7804 | 0 | 295.1353 | 1536.3209 | 2401.5122 | 713.1764 | 3122.7745 | 509.4117 | 0
IPI | HFTD Tier 3 | Transmission | Other Inspection | other | 202.08 | 202.08 | 202.08 | 202.08 | 274.08 | 581.76 | 162.24 | 402.24 | 60.96 | 156.48 | 67.2 | 71.04
Total | HFTD Tier 3 | Transmission | Other Inspection | other | 1216.8604 | 1216.8604 | 1216.8604 | 1216.8604 | 274.08 | 876.8953 | 1698.5609 | 2803.7522 | 774.1364 | 3279.2545 | 576.6117 | 71.04
IR-Aerial | Non-HFTD | Transmission | Other Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IPI | Non-HFTD | Transmission | Other Inspection | other | 1594 | 1594 | 1594 | 1594 | 2939 | 4291 | 2054 | 1438 | 2685 | 1045 | 1551 | 3615
Total | Non-HFTD | Transmission | Other Inspection | other | 1594 | 1594 | 1594 | 1594 | 2939 | 4291 | 2054 | 1438 | 2685 | 1045 | 1551 | 3615
|  |  | Distribution | 0.0339
[5 empty] | 1112 | 1112 | 1112 | 1112 | 2465 | 1945 | 10-flown |  | 4114 | 294 | (62-Flown)
|  |  |  | t2 | 578.24 | 578.24 | 578.24 | 578.24 | 1281.8 | 933.6 | 6 |  | 2139.28 | 152.88 | 34
|  |  |  | t3 | 533.76 | 533.76 | 533.76 | 533.76 | 1183.2 | 1011.4 | 4 |  | 1974.72 | 141.12 | 28
|  |  |  | t2 | 17057.3147 | 17057.3147 | 17057.3147 | 17057.3147 | 37811.4035 | 27539.9644 | 176.9921 |  | 63105.9286 | 4509.7577 | 1002.955
|  |  |  | t3 | 15745.2136 | 15745.2136 | 15745.2136 | 15745.2136 | 34902.834 | 29834.9614 | 117.9947 |  | 58251.6264 | 4162.8532 | 825.9629
|  |  | Transmission | 0.11873
[5 empty] | 251 | 251 | 251 | 251 |  | 73 | 380 | 594 | 176.4 | 772.4 | 126
|  |  |  | t2 | 130.52 | 130.52 | 130.52 | 130.52 |  | 37.96 | 197.6 | 308.88 | 91.728 | 401.648 | 65.52
|  |  |  | t3 | 120.48 | 120.48 | 120.48 | 120.48 |  | 35.04 | 182.4 | 285.12 | 84.672 | 370.752 | 60.48
|  |  |  | t2 | 1099.3455 | 1099.3455 | 1099.3455 | 1099.3455 |  | 319.73 | 1664.3477 | 2601.6382 | 772.6077 | 3383.0057 | 551.8627
|  |  |  | t3 | 1014.7804 | 1014.7804 | 1014.7804 | 1014.7804 |  | 295.1353 | 1536.3209 | 2401.5122 | 713.1764 | 3122.7745 | 509.4117

## RegDraft3 (hidden)
|  | Utility | X
|  | Table No. | 3
Date Modified
[7 empty] | Actual | Actual | Actual |  |  |  | Projected
|  | Table 3: List and description of additional metrics | [6 empty] | 1 | 2 | 3 | 4
SME / Source within QDR | Metric Status | Metric | Definition | Purpose | Assumptions made to connect metric to purpose | Third-party validation (if any) | 2020 | 2021 | 2022 | 2022 | 2022 | 2022 | 2023 | 2024 | 2025 | Unit(s) | Comments | Blank Meaning
Historical: Table 2, Metric 13a, Sum of all Tier 2 & 3 ignitions (AS LONG AS 13A IS FOR CPUC REPORTABLE IGNITIONS) Forecast: Jonathan Wuo, based on risk model results?? |  | 1. Number of CPUC reportable ignitions in HFRA
Historical: Table 2, Metric 1b, Sum of all Tier 2 & 3 wire downs Forecast: Jonathan Wuo, based on risk model results?? |  | 2. Number of wire downs in HFRA
Historical: Table 2, Metrics 1c and 1d, Sum of all Tier 2 & 3 outages (ASSUME WE DON'T NEED TO BRING IN METRIC 1E AS THAT WOULD BE DUPLICATIVE?) Forecast: Jonathan Wuo, based on risk model results?? |  | 3. Number of outages in HFRA
Amber Beaulieu |  | 4. # of asset management ignition risk-related work orders that are past due (excluding GO95 exceptions)
Songhum Yon |  | 5. Number of Tree-Caused Circuit Interruptions (TCCIs)
Songhum Yon Table 2​, Metric 16, Include Routine Transmission & Distribution in both HFRA Tier 2 & 3 |  | 6. Number of trees inspected where at least some vegetation was found in a non-compliant condition
Sum of subparts to Table 10, Metric 1a |  | 7. Frequency of PSPS events (total)
Sum of subparts to Table 10, Metric 1b |  | 8. Scope of PSPS events (total)
Sum of subparts to Table 10, Metric 1c |  | 9. Duration of PSPS (total)
Table 10, Metric 4a |  | 10. # of customers impacted by PSPS
Ryan Bullard |  | 11. Customer wildfire awareness
Amber Beaulieu '= # of total past due T&D ignition risk work orders / # of total T&D ignition risk work orders open |  | 4. % of asset management ignition risk-related work orders that are past due

## Table 2
Utility | Southern California Edison | Notes:
Table No. | 2 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.
Date Modified | 2023-02-01 | HWW = High wind warning
RFW = Red flag warning
[9 empty] | Actuals | [15 empty] | Note: These columns are placeholders for future QR submissions. | [7 empty] | Projected
Table 2: Performance Metrics | [8 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Metric name | Wind Warning Status | Program Name | HFTD Tier | Line Type | Inspection Type | Inspection Method | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | 2023 | 2023 | 2023 | 2023 | 2024 | 2024 | 2024 | 2024 | 2025 | 2025 | 2025 | 2025 | 2023 | 2024 | 2025 | Unit(s) | Comments | Blank Meaning
1. Risk Events | 1.a. | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | RFW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 6; Actuals 3: 27; Actuals 4: 21; Actuals 1: 12; Actuals 2: 4; Actuals 3: 0; Actuals 4: 2; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 5 |  |  |  | Number of events
1. Risk Events | 1.a. | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 55; Actuals 2: 9; Actuals 3: 0; Actuals 4: 5; Actuals 1: 32; Actuals 2: 0; Actuals 3: 0; Actuals 4: 8; Actuals 1: 23; Actuals 2: 9; Actuals 3: 1; Actuals 4: 24 |  |  |  | Number of events
1. Risk Events | 1.a. | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW & RFW | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 33; Actuals 1: 15; Actuals 2: 3; Actuals 3: 0; Actuals 4: 4; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 2 |  |  |  | Number of events
1. Risk Events | 1.a. | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | None | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 320; Actuals 2: 356; Actuals 3: 428; Actuals 4: 271; Actuals 1: 295; Actuals 2: 295; Actuals 3: 318; Actuals 4: 327; Actuals 1: 184; Actuals 2: 349; Actuals 3: 333; Actuals 4: 240 |  |  |  | Number of events
1. Risk Events | 1.a. | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | RFW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 6; Actuals 3: 27; Actuals 4: 49; Actuals 1: 7; Actuals 2: 2; Actuals 3: 0; Actuals 4: 12; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 5 |  |  |  | Number of events
1. Risk Events | 1.a. | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 61; Actuals 2: 7; Actuals 3: 0; Actuals 4: 0; Actuals 1: 33; Actuals 2: 1; Actuals 3: 0; Actuals 4: 7; Actuals 1: 29; Actuals 2: 0; Actuals 3: 8; Actuals 4: 16 |  |  |  | Number of events
1. Risk Events | 1.a. | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW & RFW | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 2; Actuals 3: 0; Actuals 4: 40; Actuals 1: 56; Actuals 2: 0; Actuals 3: 0; Actuals 4: 4; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 15 |  |  |  | Number of events
1. Risk Events | 1.a. | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | None | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 408; Actuals 2: 522; Actuals 3: 594; Actuals 4: 403; Actuals 1: 410; Actuals 2: 342; Actuals 3: 394; Actuals 4: 458; Actuals 1: 364; Actuals 2: 430; Actuals 3: 493; Actuals 4: 363 |  |  |  | Number of events
1. Risk Events | 1.a. | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | RFW only | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 24; Actuals 3: 173; Actuals 4: 182; Actuals 1: 74; Actuals 2: 7; Actuals 3: 0; Actuals 4: 110; Actuals 1: 0; Actuals 2: 11; Actuals 3: 0; Actuals 4: 21 |  |  |  | Number of events
1. Risk Events | 1.a. | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW only | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 134; Actuals 2: 15; Actuals 3: 0; Actuals 4: 0; Actuals 1: 200; Actuals 2: 2; Actuals 3: 0; Actuals 4: 86; Actuals 1: 277; Actuals 2: 83; Actuals 3: 16; Actuals 4: 111 |  |  |  | Number of events
1. Risk Events | 1.a. | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW & RFW | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 6; Actuals 3: 0; Actuals 4: 296; Actuals 1: 119; Actuals 2: 17; Actuals 3: 0; Actuals 4: 118; Actuals 1: 0; Actuals 2: 36; Actuals 3: 0; Actuals 4: 4 |  |  |  | Number of events
1. Risk Events | 1.a. | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | None | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 2480; Actuals 2: 3103; Actuals 3: 4510; Actuals 4: 2566; Actuals 1: 2577; Actuals 2: 3093; Actuals 3: 3219; Actuals 4: 2975; Actuals 1: 2390; Actuals 2: 3779; Actuals 3: 3651; Actuals 4: 2200 |  |  |  | Number of events
1. Risk Events | 1.b. | Number of wires down | RFW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 2; Actuals 4: 8; Actuals 1: 2; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | Number of events
1. Risk Events | 1.b. | Number of wires down | HWW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 5; Actuals 2: 2; Actuals 3: 0; Actuals 4: 0; Actuals 1: 2; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 5; Actuals 2: 1; Actuals 3: 0; Actuals 4: 0 |  |  |  | Number of events
1. Risk Events | 1.b. | Number of wires down | HWW & RFW | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 4; Actuals 1: 1; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | Number of events
1. Risk Events | 1.b. | Number of wires down | None | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 29; Actuals 2: 31; Actuals 3: 26; Actuals 4: 36; Actuals 1: 48; Actuals 2: 38; Actuals 3: 60; Actuals 4: 56; Actuals 1: 16; Actuals 2: 28; Actuals 3: 25; Actuals 4: 33 |  |  |  | Number of events | Note: A portion of this data includes "Unknown" HWW/RFW.
1. Risk Events | 1.b. | Number of wires down | RFW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 1; Actuals 3: 4; Actuals 4: 11; Actuals 1: 3; Actuals 2: 0; Actuals 3: 0; Actuals 4: 2; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | Number of events
1. Risk Events | 1.b. | Number of wires down | HWW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 4; Actuals 2: 4; Actuals 3: 0; Actuals 4: 0; Actuals 1: 6; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 2; Actuals 2: 0; Actuals 3: 3; Actuals 4: 2 |  |  |  | Number of events
1. Risk Events | 1.b. | Number of wires down | HWW & RFW | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 7; Actuals 1: 13; Actuals 2: 0; Actuals 3: 0; Actuals 4: 1; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | Number of events
1. Risk Events | 1.b. | Number of wires down | None | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 45; Actuals 2: 64; Actuals 3: 57; Actuals 4: 39; Actuals 1: 74; Actuals 2: 37; Actuals 3: 36; Actuals 4: 89; Actuals 1: 69; Actuals 2: 36; Actuals 3: 48; Actuals 4: 48 |  |  |  | Number of events | Note: A portion of this data includes "Unknown" HWW/RFW.
1. Risk Events | 1.b. | Number of wires down | RFW only | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 4; Actuals 3: 15; Actuals 4: 26; Actuals 1: 17; Actuals 2: 1; Actuals 3: 0; Actuals 4: 19; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 3 |  |  |  | Number of events
1. Risk Events | 1.b. | Number of wires down | HWW only | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 18; Actuals 2: 2; Actuals 3: 0; Actuals 4: 0; Actuals 1: 20; Actuals 2: 1; Actuals 3: 0; Actuals 4: 6; Actuals 1: 26; Actuals 2: 5; Actuals 3: 4; Actuals 4: 22 |  |  |  | Number of events
1. Risk Events | 1.b. | Number of wires down | HWW & RFW | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 1; Actuals 3: 0; Actuals 4: 53; Actuals 1: 24; Actuals 2: 2; Actuals 3: 0; Actuals 4: 16; Actuals 1: 0; Actuals 2: 1; Actuals 3: 0; Actuals 4: 0 |  |  |  | Number of events
1. Risk Events | 1.b. | Number of wires down | None | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 295; Actuals 2: 430; Actuals 3: 421; Actuals 4: 425; Actuals 1: 419; Actuals 2: 409; Actuals 3: 310; Actuals 4: 351; Actuals 1: 281; Actuals 2: 410; Actuals 3: 428; Actuals 4: 301 |  |  |  | Number of events | Note: A portion of this data includes "Unknown" HFTD & "Unknown" HWW/RFW.
1. Risk Events | 1.c. | Number of outage events not caused by contact with vegetation | RFW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 5; Actuals 3: 22; Actuals 4: 10; Actuals 1: 9; Actuals 2: 4; Actuals 3: 0; Actuals 4: 2; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 5 |  |  |  | Number of events | SCE interprets these Outages to be a subset of the metric above which captures those Risk Events that have the potential to cause ignition only, as such, these are subset of those reported on Table 5.
1. Risk Events | 1.c. | Number of outage events not caused by contact with vegetation | HWW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 31; Actuals 2: 5; Actuals 3: 0; Actuals 4: 5; Actuals 1: 21; Actuals 2: 0; Actuals 3: 0; Actuals 4: 8; Actuals 1: 14; Actuals 2: 6; Actuals 3: 1; Actuals 4: 16 |  |  |  | Number of events | SCE interprets these Outages to be a subset of the metric above which captures those Risk Events that have the potential to cause ignition only, as such, these are subset of those reported on Table 5.
1. Risk Events | 1.c. | Number of outage events not caused by contact with vegetation | HWW & RFW | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 24; Actuals 1: 12; Actuals 2: 2; Actuals 3: 0; Actuals 4: 4; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 1 |  |  |  | Number of events | SCE interprets these Outages to be a subset of the metric above which captures those Risk Events that have the potential to cause ignition only, as such, these are subset of those reported on Table 5.
1. Risk Events | 1.c. | Number of outage events not caused by contact with vegetation | None | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 246; Actuals 2: 269; Actuals 3: 362; Actuals 4: 208; Actuals 1: 203; Actuals 2: 235; Actuals 3: 247; Actuals 4: 227; Actuals 1: 146; Actuals 2: 296; Actuals 3: 300; Actuals 4: 172 |  |  |  | Number of events | SCE interprets these Outages to be a subset of the metric above which captures those Risk Events that have the potential to cause ignition only, as such, these are subset of those reported on Table 5.
1. Risk Events | 1.c. | Number of outage events not caused by contact with vegetation | RFW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 4; Actuals 3: 20; Actuals 4: 32; Actuals 1: 4; Actuals 2: 2; Actuals 3: 0; Actuals 4: 8; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 5 |  |  |  | Number of events | SCE interprets these Outages to be a subset of the metric above which captures those Risk Events that have the potential to cause ignition only, as such, these are subset of those reported on Table 5.
1. Risk Events | 1.c. | Number of outage events not caused by contact with vegetation | HWW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 26; Actuals 2: 1; Actuals 3: 0; Actuals 4: 0; Actuals 1: 25; Actuals 2: 1; Actuals 3: 0; Actuals 4: 7; Actuals 1: 19; Actuals 2: 0; Actuals 3: 4; Actuals 4: 13 |  |  |  | Number of events | SCE interprets these Outages to be a subset of the metric above which captures those Risk Events that have the potential to cause ignition only, as such, these are subset of those reported on Table 5.
1. Risk Events | 1.c. | Number of outage events not caused by contact with vegetation | HWW & RFW | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 1; Actuals 3: 0; Actuals 4: 29; Actuals 1: 37; Actuals 2: 0; Actuals 3: 0; Actuals 4: 3; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 10 |  |  |  | Number of events | SCE interprets these Outages to be a subset of the metric above which captures those Risk Events that have the potential to cause ignition only, as such, these are subset of those reported on Table 5.
1. Risk Events | 1.c. | Number of outage events not caused by contact with vegetation | None | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 277; Actuals 2: 360; Actuals 3: 462; Actuals 4: 324; Actuals 1: 283; Actuals 2: 280; Actuals 3: 337; Actuals 4: 309; Actuals 1: 263; Actuals 2: 367; Actuals 3: 426; Actuals 4: 277 |  |  |  | Number of events | SCE interprets these Outages to be a subset of the metric above which captures those Risk Events that have the potential to cause ignition only, as such, these are subset of those reported on Table 5.
1. Risk Events | 1.c. | Number of outage events not caused by contact with vegetation | RFW only | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 17; Actuals 3: 150; Actuals 4: 134; Actuals 1: 48; Actuals 2: 5; Actuals 3: 0; Actuals 4: 84; Actuals 1: 0; Actuals 2: 7; Actuals 3: 0; Actuals 4: 18 |  |  |  | Number of events | SCE interprets these Outages to be a subset of the metric above which captures those Risk Events that have the potential to cause ignition only, as such, these are subset of those reported on Table 5.
1. Risk Events | 1.c. | Number of outage events not caused by contact with vegetation | HWW only | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 97; Actuals 2: 8; Actuals 3: 0; Actuals 4: 0; Actuals 1: 155; Actuals 2: 1; Actuals 3: 0; Actuals 4: 65; Actuals 1: 215; Actuals 2: 64; Actuals 3: 11; Actuals 4: 80 |  |  |  | Number of events | SCE interprets these Outages to be a subset of the metric above which captures those Risk Events that have the potential to cause ignition only, as such, these are subset of those reported on Table 5.
1. Risk Events | 1.c. | Number of outage events not caused by contact with vegetation | HWW & RFW | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 2; Actuals 3: 0; Actuals 4: 209; Actuals 1: 93; Actuals 2: 10; Actuals 3: 0; Actuals 4: 82; Actuals 1: 0; Actuals 2: 25; Actuals 3: 0; Actuals 4: 4 |  |  |  | Number of events | SCE interprets these Outages to be a subset of the metric above which captures those Risk Events that have the potential to cause ignition only, as such, these are subset of those reported on Table 5.
1. Risk Events | 1.c. | Number of outage events not caused by contact with vegetation | None | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 2009; Actuals 2: 2486; Actuals 3: 3908; Actuals 4: 1969; Actuals 1: 1990; Actuals 2: 2525; Actuals 3: 2724; Actuals 4: 2416; Actuals 1: 1875; Actuals 2: 3027; Actuals 3: 3155; Actuals 4: 1734 |  |  |  | Number of events | SCE interprets these Outages to be a subset of the metric above which captures those Risk Events that have the potential to cause ignition only, as such, these are subset of those reported on Table 5.
1. Risk Events | 1.d. | Number of outage events caused by contact with vegetation | RFW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 2; Actuals 1: 1; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | Number of events
1. Risk Events | 1.d. | Number of outage events caused by contact with vegetation | HWW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 4; Actuals 2: 1; Actuals 3: 0; Actuals 4: 0; Actuals 1: 1; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 3; Actuals 2: 0; Actuals 3: 0; Actuals 4: 1 |  |  |  | Number of events
1. Risk Events | 1.d. | Number of outage events caused by contact with vegetation | HWW & RFW | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 5; Actuals 1: 2; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 1 |  |  |  | Number of events
1. Risk Events | 1.d. | Number of outage events caused by contact with vegetation | None | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 12; Actuals 2: 5; Actuals 3: 4; Actuals 4: 2; Actuals 1: 7; Actuals 2: 3; Actuals 3: 4; Actuals 4: 9; Actuals 1: 5; Actuals 2: 5; Actuals 3: 3; Actuals 4: 10 |  |  |  | Number of events
1. Risk Events | 1.d. | Number of outage events caused by contact with vegetation | RFW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 6; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 2; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | Number of events
1. Risk Events | 1.d. | Number of outage events caused by contact with vegetation | HWW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 13; Actuals 2: 1; Actuals 3: 0; Actuals 4: 0; Actuals 1: 2; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 2; Actuals 2: 0; Actuals 3: 1; Actuals 4: 1 |  |  |  | Number of events
1. Risk Events | 1.d. | Number of outage events caused by contact with vegetation | HWW & RFW | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 3; Actuals 1: 4; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 2 |  |  |  | Number of events
1. Risk Events | 1.d. | Number of outage events caused by contact with vegetation | None | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 14; Actuals 2: 16; Actuals 3: 3; Actuals 4: 10; Actuals 1: 9; Actuals 2: 2; Actuals 3: 5; Actuals 4: 35; Actuals 1: 8; Actuals 2: 6; Actuals 3: 4; Actuals 4: 11 |  |  |  | Number of events
1. Risk Events | 1.d. | Number of outage events caused by contact with vegetation | RFW only | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 3; Actuals 3: 1; Actuals 4: 7; Actuals 1: 6; Actuals 2: 0; Actuals 3: 0; Actuals 4: 5; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | Number of events
1. Risk Events | 1.d. | Number of outage events caused by contact with vegetation | HWW only | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 7; Actuals 2: 5; Actuals 3: 0; Actuals 4: 0; Actuals 1: 3; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 24; Actuals 2: 0; Actuals 3: 1; Actuals 4: 6 |  |  |  | Number of events
1. Risk Events | 1.d. | Number of outage events caused by contact with vegetation | HWW & RFW | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 1; Actuals 3: 0; Actuals 4: 29; Actuals 1: 1; Actuals 2: 0; Actuals 3: 0; Actuals 4: 18; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | Number of events
1. Risk Events | 1.d. | Number of outage events caused by contact with vegetation | None | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 54; Actuals 2: 37; Actuals 3: 14; Actuals 4: 47; Actuals 1: 56; Actuals 2: 16; Actuals 3: 23; Actuals 4: 100; Actuals 1: 49; Actuals 2: 18; Actuals 3: 31; Actuals 4: 51 |  |  |  | Number of events
1. Risk Events | 1.e. | Number of outage events on circuits with adjusted settings for protective devices enabled. | RFW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 1; Actuals 3: 3; Actuals 4: 1; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | Number of events
1. Risk Events | 1.e. | Number of outage events on circuits with adjusted settings for protective devices enabled. | HWW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 15; Actuals 2: 1; Actuals 3: 0; Actuals 4: 0; Actuals 1: 8; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 1; Actuals 2: 2; Actuals 3: 0; Actuals 4: 7 |  |  |  | Number of events
1. Risk Events | 1.e. | Number of outage events on circuits with adjusted settings for protective devices enabled. | HWW & RFW | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 1; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | Number of events
1. Risk Events | 1.e. | Number of outage events on circuits with adjusted settings for protective devices enabled. | None | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 32; Actuals 2: 44; Actuals 3: 31; Actuals 4: 23; Actuals 1: 36; Actuals 2: 7; Actuals 3: 4; Actuals 4: 32; Actuals 1: 14; Actuals 2: 13; Actuals 3: 3; Actuals 4: 24 | 58 | 49 | 41 | Number of events
1. Risk Events | 1.e. | Number of outage events on circuits with adjusted settings for protective devices enabled. | RFW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 1; Actuals 3: 3; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | Number of events
1. Risk Events | 1.e. | Number of outage events on circuits with adjusted settings for protective devices enabled. | HWW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 18; Actuals 2: 1; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 6; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | Number of events
1. Risk Events | 1.e. | Number of outage events on circuits with adjusted settings for protective devices enabled. | HWW & RFW | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 1; Actuals 3: 0; Actuals 4: 0; Actuals 1: 2; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 2 |  |  |  | Number of events
1. Risk Events | 1.e. | Number of outage events on circuits with adjusted settings for protective devices enabled. | None | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 70; Actuals 2: 67; Actuals 3: 61; Actuals 4: 24; Actuals 1: 38; Actuals 2: 12; Actuals 3: 5; Actuals 4: 24; Actuals 1: 19; Actuals 2: 12; Actuals 3: 5; Actuals 4: 25 | 62 | 49 | 36 | Number of events
1. Risk Events | 1.e. | Number of outage events on circuits with adjusted settings for protective devices enabled. | RFW only | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 6; Actuals 4: 14; Actuals 1: 1; Actuals 2: 1; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 3; Actuals 3: 0; Actuals 4: 0 |  |  |  | Number of events
1. Risk Events | 1.e. | Number of outage events on circuits with adjusted settings for protective devices enabled. | HWW only | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 12; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 21; Actuals 2: 0; Actuals 3: 0; Actuals 4: 15; Actuals 1: 11; Actuals 2: 14; Actuals 3: 0; Actuals 4: 3 |  |  |  | Number of events
1. Risk Events | 1.e. | Number of outage events on circuits with adjusted settings for protective devices enabled. | HWW & RFW | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 2; Actuals 3: 0; Actuals 4: 3; Actuals 1: 1; Actuals 2: 5; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 10; Actuals 3: 0; Actuals 4: 0 |  |  |  | Number of events
1. Risk Events | 1.e. | Number of outage events on circuits with adjusted settings for protective devices enabled. | None | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 109; Actuals 2: 114; Actuals 3: 140; Actuals 4: 107; Actuals 1: 92; Actuals 2: 100; Actuals 3: 118; Actuals 4: 97; Actuals 1: 167; Actuals 2: 292; Actuals 3: 14; Actuals 4: 106 | 491 | 471 | 450 | Number of events
2. Time between vegetation inspection finding and resulting trimming activity | 2.d.2.a. | Median time | N/A |  | HFTD Tier 2 | Distribution | N/A | N/A | Actuals 1: 43; Actuals 2: 36; Actuals 3: 53; Actuals 4: 43; Actuals 1: 42; Actuals 2: 91; Actuals 3: 94; Actuals 4: 70; Actuals 1: 60; Actuals 2: 48; Actuals 3: 49; Actuals 4: 37 |  |  |  | days
2. Time between vegetation inspection finding and resulting trimming activity | 2.d.2.b. | 95 percentile time | N/A |  | HFTD Tier 2 | Distribution | N/A | N/A | Actuals 1: 127; Actuals 2: 144; Actuals 3: 741; Actuals 4: 131; Actuals 1: 360; Actuals 2: 379; Actuals 3: 280.2; Actuals 4: 274; Actuals 1: 175; Actuals 2: 138; Actuals 3: 118; Actuals 4: 64 |  |  |  | days
2. Time between vegetation inspection finding and resulting trimming activity | 2.d.3.a. | Median time | N/A |  | HFTD Tier 3 | Distribution | N/A | N/A | Actuals 1: 40; Actuals 2: 41; Actuals 3: 50; Actuals 4: 43; Actuals 1: 35; Actuals 2: 98; Actuals 3: 94; Actuals 4: 62; Actuals 1: 48; Actuals 2: 50; Actuals 3: 54; Actuals 4: 36 |  |  |  | days
2. Time between vegetation inspection finding and resulting trimming activity | 2.d.3.b. | 95 percentile time | N/A |  | HFTD Tier 3 | Distribution | N/A | N/A | Actuals 1: 127; Actuals 2: 175; Actuals 3: 133; Actuals 4: 219; Actuals 1: 307; Actuals 2: 280; Actuals 3: 300; Actuals 4: 194; Actuals 1: 196; Actuals 2: 147; Actuals 3: 119; Actuals 4: 71 |  |  |  | days
2. Time between vegetation inspection finding and resulting trimming activity | 2.d.4.a. | Median time | N/A |  | Non- HFTD | Distribution | N/A | N/A | Actuals 1: 36; Actuals 2: 37; Actuals 3: 50; Actuals 4: 41; Actuals 1: 38; Actuals 2: 52; Actuals 3: 64; Actuals 4: 50; Actuals 1: 39; Actuals 2: 35; Actuals 3: 35.5; Actuals 4: 21 |  |  |  | days
2. Time between vegetation inspection finding and resulting trimming activity | 2.d.4.b. | 95 percentile time | N/A |  | Non- HFTD | Distribution | N/A | N/A | Actuals 1: 102; Actuals 2: 120; Actuals 3: 112; Actuals 4: 100; Actuals 1: 189; Actuals 2: 169; Actuals 3: 206; Actuals 4: 159.4; Actuals 1: 126.3; Actuals 2: 107; Actuals 3: 96; Actuals 4: 62 |  |  |  | days
2. Time between vegetation inspection finding and resulting trimming activity | 2.t.2.a. | Median time | N/A |  | HFTD Tier 2 | Transmission | N/A | N/A | Actuals 1: 62; Actuals 2: 118; Actuals 3: 42; Actuals 4: 44; Actuals 1: 53; Actuals 2: 367; Actuals 3: 114; Actuals 4: 221; Actuals 1: 102; Actuals 2: 76; Actuals 3: 71.5; Actuals 4: 27 |  |  |  | days
2. Time between vegetation inspection finding and resulting trimming activity | 2.t.2.b. | 95 percentile time | N/A |  | HFTD Tier 2 | Transmission | N/A | N/A | Actuals 1: 161; Actuals 2: 163; Actuals 3: 145; Actuals 4: 342.5; Actuals 1: 426; Actuals 2: 479; Actuals 3: 434.8; Actuals 4: 294.7; Actuals 1: 248.7; Actuals 2: 179; Actuals 3: 127; Actuals 4: 71 |  |  |  | days
2. Time between vegetation inspection finding and resulting trimming activity | 2.t.3.a. | Median time | N/A |  | HFTD Tier 3 | Transmission | N/A | N/A | Actuals 1: 41; Actuals 2: 60; Actuals 3: 12; Actuals 4: 48; Actuals 1: 129; Actuals 2: 147; Actuals 3: 87; Actuals 4: 157; Actuals 1: 136; Actuals 2: 70; Actuals 3: 58; Actuals 4: 51 |  |  |  | days
2. Time between vegetation inspection finding and resulting trimming activity | 2.t.3.b. | 95 percentile time | N/A |  | HFTD Tier 3 | Transmission | N/A | N/A | Actuals 1: 253; Actuals 2: 273; Actuals 3: 99; Actuals 4: 351.25; Actuals 1: 492; Actuals 2: 440.9; Actuals 3: 363; Actuals 4: 343; Actuals 1: 238; Actuals 2: 189; Actuals 3: 151.5; Actuals 4: 73 |  |  |  | days
2. Time between vegetation inspection finding and resulting trimming activity | 2.t.4.a. | Median time | N/A |  | Non- HFTD | Transmission | N/A | N/A | Actuals 1: 54; Actuals 2: 44; Actuals 3: 56; Actuals 4: 44; Actuals 1: 55; Actuals 2: 69; Actuals 3: 69; Actuals 4: 62; Actuals 1: 62; Actuals 2: 56.5; Actuals 3: 65; Actuals 4: 16 |  |  |  | days
2. Time between vegetation inspection finding and resulting trimming activity | 2.t.4.b. | 95 percentile time | N/A |  | Non- HFTD | Transmission | N/A | N/A | Actuals 1: 176; Actuals 2: 161; Actuals 3: 171; Actuals 4: 189.4; Actuals 1: 338; Actuals 2: 300.2; Actuals 3: 245.1; Actuals 4: 223; Actuals 1: 180; Actuals 2: 148.85; Actuals 3: 108; Actuals 4: 61.4 |  |  |  | days
3. Time between level 1 asset inspection finding and resulting maintenance activity | 3.d.2.a. | Median time | N/A | N/A | HFTD Tier 2 | Distribution | N/A | N/A | Actuals 1: 1; Actuals 2: 0; Actuals 3: 1; Actuals 4: 1; Actuals 1: 0; Actuals 2: 0; Actuals 3: 1; Actuals 4: 1; Actuals 1: 1; Actuals 2: 0; Actuals 3: 1; Actuals 4: 1 |  |  |  | hours | Notifications created 1/1/20 and later
3. Time between level 1 asset inspection finding and resulting maintenance activity | 3.d.2.b. | 95 percentile time | N/A | N/A | HFTD Tier 2 | Distribution | N/A | N/A | Actuals 1: 14; Actuals 2: 40; Actuals 3: 6; Actuals 4: 13; Actuals 1: 247; Actuals 2: 8; Actuals 3: 26; Actuals 4: 416; Actuals 1: 14; Actuals 2: 11; Actuals 3: 68; Actuals 4: 217 |  |  |  | hours
3. Time between level 1 asset inspection finding and resulting maintenance activity | 3.d.3.a. | Median time | N/A | N/A | HFTD Tier 3 | Distribution | N/A | N/A | Actuals 1: 1; Actuals 2: 1; Actuals 3: 0.5; Actuals 4: 1; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 1; Actuals 1: 1; Actuals 2: 1; Actuals 3: 0; Actuals 4: 1 |  |  |  | hours
3. Time between level 1 asset inspection finding and resulting maintenance activity | 3.d.3.b. | 95 percentile time | N/A | N/A | HFTD Tier 3 | Distribution | N/A | N/A | Actuals 1: 23; Actuals 2: 57; Actuals 3: 9; Actuals 4: 5; Actuals 1: 4; Actuals 2: 5; Actuals 3: 12; Actuals 4: 97; Actuals 1: 4; Actuals 2: 17; Actuals 3: 5.5; Actuals 4: 125 |  |  |  | hours
3. Time between level 1 asset inspection finding and resulting maintenance activity | 3.d.4.a. | Median time | N/A | N/A | Non- HFTD | Distribution | N/A | N/A | Actuals 1: 1; Actuals 2: 1; Actuals 3: 0; Actuals 4: 1; Actuals 1: 1; Actuals 2: 1; Actuals 3: 1; Actuals 4: 1; Actuals 1: 1; Actuals 2: 1; Actuals 3: 1; Actuals 4: 1 |  |  |  | hours
3. Time between level 1 asset inspection finding and resulting maintenance activity | 3.d.4.b. | 95 percentile time | N/A | N/A | Non- HFTD | Distribution | N/A | N/A | Actuals 1: 387; Actuals 2: 13; Actuals 3: 44; Actuals 4: 11; Actuals 1: 76; Actuals 2: 12; Actuals 3: 11; Actuals 4: 23; Actuals 1: 113; Actuals 2: 13; Actuals 3: 77; Actuals 4: 27 |  |  |  | hours
3. Time between level 1 asset inspection finding and resulting maintenance activity | 3.t.2.a. | Median time | N/A | N/A | HFTD Tier 2 | Transmission | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0.5; Actuals 1: 0.5; Actuals 2: 0.5; Actuals 3: 0; Actuals 4: 0 |  |  |  | hours
3. Time between level 1 asset inspection finding and resulting maintenance activity | 3.t.2.b. | 95 percentile time | N/A | N/A | HFTD Tier 2 | Transmission | N/A | N/A | Actuals 1: 3; Actuals 2: 3; Actuals 3: 1; Actuals 4: 3; Actuals 1: 1; Actuals 2: 4; Actuals 3: 1; Actuals 4: 1; Actuals 1: 1; Actuals 2: 1; Actuals 3: 0; Actuals 4: 0 |  |  |  | hours
3. Time between level 1 asset inspection finding and resulting maintenance activity | 3.t.3.a. | Median time | N/A | N/A | HFTD Tier 3 | Transmission | N/A | N/A | Actuals 1: 0; Actuals 2: 1; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 1.5; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | hours
3. Time between level 1 asset inspection finding and resulting maintenance activity | 3.t.3.b. | 95 percentile time | N/A | N/A | HFTD Tier 3 | Transmission | N/A | N/A | Actuals 1: 8; Actuals 2: 18; Actuals 3: 1; Actuals 4: 112; Actuals 1: 1; Actuals 2: 3; Actuals 3: 14; Actuals 4: 3; Actuals 1: 3; Actuals 2: 1; Actuals 3: 0; Actuals 4: 0 |  |  |  | hours
3. Time between level 1 asset inspection finding and resulting maintenance activity | 3.t.4.a. | Median time | N/A | N/A | Non- HFTD | Transmission | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0.5; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0.5; Actuals 4: 1; Actuals 1: 1; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | hours
3. Time between level 1 asset inspection finding and resulting maintenance activity | 3.t.4.b. | 95 percentile time | N/A | N/A | Non- HFTD | Transmission | N/A | N/A | Actuals 1: 1; Actuals 2: 2; Actuals 3: 4; Actuals 4: 26; Actuals 1: 2; Actuals 2: 1; Actuals 3: 2; Actuals 4: 15; Actuals 1: 1; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | hours
4. Time between level 2 asset inspection finding and resulting maintenance activity | 4.d.2.a. | Median time | N/A | N/A | HFTD Tier 2 | Distribution | N/A | N/A | Actuals 1: 329; Actuals 2: 279; Actuals 3: 248; Actuals 4: 300; Actuals 1: 314.5; Actuals 2: 224.5; Actuals 3: 320.5; Actuals 4: 312.5; Actuals 1: 263; Actuals 2: 266; Actuals 3: 56; Actuals 4: 282 |  |  |  | hours
4. Time between level 2 asset inspection finding and resulting maintenance activity | 4.d.2.b. | 95 percentile time | N/A | N/A | HFTD Tier 2 | Distribution | N/A | N/A | Actuals 1: 415; Actuals 2: 1030; Actuals 3: 681; Actuals 4: 652; Actuals 1: 711; Actuals 2: 799; Actuals 3: 905; Actuals 4: 1010.5; Actuals 1: 1069; Actuals 2: 1092; Actuals 3: 713; Actuals 4: 1326 |  |  |  | hours
4. Time between level 2 asset inspection finding and resulting maintenance activity | 4.d.3.a. | Median time | N/A | N/A | HFTD Tier 3 | Distribution | N/A | N/A | Actuals 1: 148; Actuals 2: 145; Actuals 3: 142; Actuals 4: 160; Actuals 1: 171; Actuals 2: 113; Actuals 3: 142; Actuals 4: 171; Actuals 1: 177; Actuals 2: 72; Actuals 3: 68; Actuals 4: 154 |  |  |  | hours
4. Time between level 2 asset inspection finding and resulting maintenance activity | 4.d.3.b. | 95 percentile time | N/A | N/A | HFTD Tier 3 | Distribution | N/A | N/A | Actuals 1: 1357; Actuals 2: 1014; Actuals 3: 547; Actuals 4: 610; Actuals 1: 753; Actuals 2: 799; Actuals 3: 892; Actuals 4: 1004; Actuals 1: 1087; Actuals 2: 1068; Actuals 3: 182; Actuals 4: 961 |  |  |  | hours
4. Time between level 2 asset inspection finding and resulting maintenance activity | 4.d.4.a. | Median time | N/A | N/A | Non- HFTD | Distribution | N/A | N/A | Actuals 1: 338; Actuals 2: 422.5; Actuals 3: 370; Actuals 4: 501; Actuals 1: 612; Actuals 2: 236; Actuals 3: 469; Actuals 4: 207; Actuals 1: 130; Actuals 2: 510; Actuals 3: 22; Actuals 4: 7 |  |  |  | hours
4. Time between level 2 asset inspection finding and resulting maintenance activity | 4.d.4.b. | 95 percentile time | N/A | N/A | Non- HFTD | Distribution | N/A | N/A | Actuals 1: 1117; Actuals 2: 1138; Actuals 3: 1407; Actuals 4: 1152; Actuals 1: 1107; Actuals 2: 1078; Actuals 3: 1515; Actuals 4: 1075; Actuals 1: 825; Actuals 2: 2442; Actuals 3: 783; Actuals 4: 714 |  |  |  | hours
4. Time between level 2 asset inspection finding and resulting maintenance activity | 4.t.2.a. | Median time | N/A | N/A | HFTD Tier 2 | Transmission | N/A | N/A | Actuals 1: 386; Actuals 2: 453; Actuals 3: 278.5; Actuals 4: 214; Actuals 1: 286; Actuals 2: 372; Actuals 3: 381; Actuals 4: 490; Actuals 1: 455; Actuals 2: 535; Actuals 3: 474; Actuals 4: 268 |  |  |  | hours
4. Time between level 2 asset inspection finding and resulting maintenance activity | 4.t.2.b. | 95 percentile time | N/A | N/A | HFTD Tier 2 | Transmission | N/A | N/A | Actuals 1: 493; Actuals 2: 1078; Actuals 3: 617; Actuals 4: 645; Actuals 1: 528; Actuals 2: 885; Actuals 3: 923; Actuals 4: 1017; Actuals 1: 846; Actuals 2: 957; Actuals 3: 1291; Actuals 4: 1011.5 |  |  |  | hours
4. Time between level 2 asset inspection finding and resulting maintenance activity | 4.t.3.a. | Median time | N/A | N/A | HFTD Tier 3 | Transmission | N/A | N/A | Actuals 1: 330; Actuals 2: 207; Actuals 3: 110; Actuals 4: 173; Actuals 1: 215.5; Actuals 2: 103.5; Actuals 3: 123; Actuals 4: 368; Actuals 1: 307; Actuals 2: 398; Actuals 3: 387; Actuals 4: 180 |  |  |  | hours
4. Time between level 2 asset inspection finding and resulting maintenance activity | 4.t.3.b. | 95 percentile time | N/A | N/A | HFTD Tier 3 | Transmission | N/A | N/A | Actuals 1: 574; Actuals 2: 652; Actuals 3: 301; Actuals 4: 441; Actuals 1: 629; Actuals 2: 526; Actuals 3: 583; Actuals 4: 794; Actuals 1: 1091; Actuals 2: 910; Actuals 3: 1037; Actuals 4: 965 |  |  |  | hours
4. Time between level 2 asset inspection finding and resulting maintenance activity | 4.t.4.a. | Median time | N/A | N/A | Non- HFTD | Transmission | N/A | N/A | Actuals 1: 599; Actuals 2: 784; Actuals 3: 563; Actuals 4: 655; Actuals 1: 817; Actuals 2: 691; Actuals 3: 601; Actuals 4: 684; Actuals 1: 794; Actuals 2: 754; Actuals 3: 715; Actuals 4: 593.5 |  |  |  | hours
4. Time between level 2 asset inspection finding and resulting maintenance activity | 4.t.4.b. | 95 percentile time | N/A | N/A | Non- HFTD | Transmission | N/A | N/A | Actuals 1: 1135; Actuals 2: 1348; Actuals 3: 1256; Actuals 4: 1538; Actuals 1: 1292; Actuals 2: 1172; Actuals 3: 1289; Actuals 4: 2056; Actuals 1: 1182.5; Actuals 2: 1249; Actuals 3: 1451; Actuals 4: 1405 |  |  |  | hours
5. Time between level 3 asset inspection finding and resulting maintenance activity | 5.d.2.a. | Median time | N/A | N/A | HFTD Tier 2 | Distribution | N/A | N/A | Actuals 1: 2681; Actuals 2: 2665; Actuals 3: 2013; Actuals 4: 2197; Actuals 1: 1780; Actuals 2: 1862; Actuals 3: 1471; Actuals 4: 1467.5; Actuals 1: 1165; Actuals 2: 1223; Actuals 3: 1296; Actuals 4: 869 |  |  |  | hours
5. Time between level 3 asset inspection finding and resulting maintenance activity | 5.d.2.b. | 95 percentile time | N/A | N/A | HFTD Tier 2 | Distribution | N/A | N/A | Actuals 1: 6545; Actuals 2: 6631; Actuals 3: 6701; Actuals 4: 6737; Actuals 1: 6916; Actuals 2: 6921; Actuals 3: 7091; Actuals 4: 6657; Actuals 1: 6761; Actuals 2: 7285; Actuals 3: 6909; Actuals 4: 6964 |  |  |  | hours
5. Time between level 3 asset inspection finding and resulting maintenance activity | 5.d.3.a. | Median time | N/A | N/A | HFTD Tier 3 | Distribution | N/A | N/A | Actuals 1: 2266; Actuals 2: 2302.5; Actuals 3: 1981; Actuals 4: 1950; Actuals 1: 1769; Actuals 2: 1694; Actuals 3: 1396; Actuals 4: 1270; Actuals 1: 1444; Actuals 2: 1232; Actuals 3: 940; Actuals 4: 1219 |  |  |  | hours
5. Time between level 3 asset inspection finding and resulting maintenance activity | 5.d.3.b. | 95 percentile time | N/A | N/A | HFTD Tier 3 | Distribution | N/A | N/A | Actuals 1: 6628; Actuals 2: 6663; Actuals 3: 6768; Actuals 4: 6885; Actuals 1: 6956; Actuals 2: 7035; Actuals 3: 7093; Actuals 4: 7162; Actuals 1: 6786; Actuals 2: 7311; Actuals 3: 6977; Actuals 4: 7098 |  |  |  | hours
5. Time between level 3 asset inspection finding and resulting maintenance activity | 5.d.4.a. | Median time | N/A | N/A | Non- HFTD | Distribution | N/A | N/A | Actuals 1: 2598; Actuals 2: 2515; Actuals 3: 2769; Actuals 4: 2688; Actuals 1: 2674; Actuals 2: 3100; Actuals 3: 3507; Actuals 4: 3167; Actuals 1: 2953; Actuals 2: 3136; Actuals 3: 3323; Actuals 4: 3276 |  |  |  | hours
5. Time between level 3 asset inspection finding and resulting maintenance activity | 5.d.4.b. | 95 percentile time | N/A | N/A | Non- HFTD | Distribution | N/A | N/A | Actuals 1: 6583; Actuals 2: 6659; Actuals 3: 6770; Actuals 4: 6859; Actuals 1: 6949; Actuals 2: 7053; Actuals 3: 7155; Actuals 4: 7223; Actuals 1: 7336; Actuals 2: 7389; Actuals 3: 7489; Actuals 4: 7543 |  |  |  | hours
5. Time between level 3 asset inspection finding and resulting maintenance activity | 5.t.2.a. | Median time | N/A | N/A | HFTD Tier 2 | Transmission | N/A | N/A | Actuals 1: 420; Actuals 2: 523; Actuals 3: 553; Actuals 4: 210; Actuals 1: 732; Actuals 2: 828; Actuals 3: 416; Actuals 4: 247; Actuals 1: 341; Actuals 2: 495; Actuals 3: 798; Actuals 4: 618 |  |  |  | hours
5. Time between level 3 asset inspection finding and resulting maintenance activity | 5.t.2.b. | 95 percentile time | N/A | N/A | HFTD Tier 2 | Transmission | N/A | N/A | Actuals 1: 6557; Actuals 2: 5821; Actuals 3: 940; Actuals 4: 3628; Actuals 1: 6815; Actuals 2: 6857; Actuals 3: 4484; Actuals 4: 3345; Actuals 1: 3675; Actuals 2: 5862; Actuals 3: 1968; Actuals 4: 3670 |  |  |  | hours
5. Time between level 3 asset inspection finding and resulting maintenance activity | 5.t.3.a. | Median time | N/A | N/A | HFTD Tier 3 | Transmission | N/A | N/A | Actuals 1: 378; Actuals 2: 2184; Actuals 3: 151; Actuals 4: 638; Actuals 1: 435.5; Actuals 2: 296; Actuals 3: 356; Actuals 4: 546; Actuals 1: 403; Actuals 2: 477; Actuals 3: 717; Actuals 4: 649 |  |  |  | hours
5. Time between level 3 asset inspection finding and resulting maintenance activity | 5.t.3.b. | 95 percentile time | N/A | N/A | HFTD Tier 3 | Transmission | N/A | N/A | Actuals 1: 5518; Actuals 2: 7051; Actuals 3: 7001; Actuals 4: 4775; Actuals 1: 6186; Actuals 2: 6186; Actuals 3: 6267; Actuals 4: 6352; Actuals 1: 5226; Actuals 2: 5584; Actuals 3: 4525; Actuals 4: 5473 |  |  |  | hours
5. Time between level 3 asset inspection finding and resulting maintenance activity | 5.t.4.a. | Median time | N/A | N/A | Non- HFTD | Transmission | N/A | N/A | Actuals 1: 411; Actuals 2: 1831; Actuals 3: 1807.5; Actuals 4: 1977; Actuals 1: 362; Actuals 2: 2294; Actuals 3: 1707.5; Actuals 4: 529; Actuals 1: 0; Actuals 2: 0; Actuals 3: 909; Actuals 4: 0 |  |  |  | hours
5. Time between level 3 asset inspection finding and resulting maintenance activity | 5.t.4.b. | 95 percentile time | N/A | N/A | Non- HFTD | Transmission | N/A | N/A | Actuals 1: 6468; Actuals 2: 6575; Actuals 3: 6585; Actuals 4: 6088; Actuals 1: 6740; Actuals 2: 6880; Actuals 3: 6940; Actuals 4: 6367; Actuals 1: 7179; Actuals 2: 7237; Actuals 3: 7360; Actuals 4: 4515 |  |  |  | hours
6. Vegetation management work orders | 6.a. | Number of vegetation management open work orders (total) | N/A | N/A | N/A | N/A | Routine | N/A | Actuals 1: 88565; Actuals 2: 136303; Actuals 3: 163245; Actuals 4: 109126; Actuals 1: 123958; Actuals 2: 200426; Actuals 3: 239165; Actuals 4: 196029; Actuals 1: 198958; Actuals 2: 169478; Actuals 3: 151778; Actuals 4: 110507 | 163543 | 163543 | 163543 | Number of orders
6. Vegetation management work orders | 6.b. | Number of vegetation management past due work orders (total) | N/A | N/A | N/A | N/A | Routine | N/A | Actuals 1: 2; Actuals 2: 6080; Actuals 3: 19697; Actuals 4: 10545; Actuals 1: 16186; Actuals 2: 41966; Actuals 3: 71376; Actuals 4: 64141; Actuals 1: 56393; Actuals 2: 41182; Actuals 3: 31932; Actuals 4: 26999 | 35136.0909 | 35136.0909 | 35136.0909 | Number of orders | For Veg Past Due WOs, SCE reports the number of open work points in 6a that have exceeded internal targets of 30 days <Regulatory Clearance Distance (RCD) and 90 days between RCD and Trigger Clearance Distance (TCD).
7. Asset management work orders | 7.a. | Number of asset management open work orders (total) | N/A | N/A | N/A | N/A | N/A | N/A | Actuals 1: 885960; Actuals 2: 887595; Actuals 3: 891160; Actuals 4: 896169; Actuals 1: 892741; Actuals 2: 891474; Actuals 3: 898701; Actuals 4: 902964; Actuals 1: 883951; Actuals 2: 886693; Actuals 3: 878100; Actuals 4: 884043 | 889962.5833 | 889962.5833 | 889962.5833 | Number of orders
7. Asset management work orders | 7.b. | Number of asset management past due work orders (total) | N/A | N/A | N/A | N/A | N/A | N/A | Actuals 1: 22287; Actuals 2: 21514; Actuals 3: 22582; Actuals 4: 22933; Actuals 1: 25098; Actuals 2: 26085; Actuals 3: 27131; Actuals 4: 26325; Actuals 1: 25977; Actuals 2: 23473; Actuals 3: 23861; Actuals 4: 24782 | 24337.3333 | 24337.3333 | 24337.3333 | Number of orders
8. Response Time | 8.a. | Response time to locked open circuit breaker | N/A | N/A | N/A | N/A | N/A | N/A | [27 empty] | Hours | For metric 8a, data for crew response time to a locked circuit breaker incident is not readily available for instances not involving hazard conditions such as 911 or wire down calls. SCE will continue to review the available information in its outage systems to provide this information in a future filing. Currently, any quarterly data would reflect only 911 and wire down events and is not a good representation of our overall response time. | Metric Not Available at this Time.
9. Fatalities and injuries due to utility-related ignitions | 9.a. | Fatalities due to utility-related ignitions (total) | N/A | N/A | N/A | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 2; Actuals 4: 0 |  |  |  | Number of fatalities | The information provided in conjunction with all of the “utility-ignited” wildfire statistics in tables 1-15 should not be construed as an admission of any wrongdoing or liability by SCE. SCE further notes that the damages metrics provided may be tracked by other agencies and thus, SCE does not guarantee the accuracy of such information. Additionally, in many instances the cause of wildfires are still under investigation and even where an Authority Having Jurisdiction (AHJ) has issued a report on the cause, SCE may dispute the conclusions of such report.
9. Fatalities and injuries due to utility-related ignitions | 9.b. | Injuries due to utility-related ignitions (total) | N/A | N/A | N/A | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 6; Actuals 4: 2; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 2; Actuals 3: 3; Actuals 4: 0 |  |  |  | Number of injuries | The information provided in conjunction with all of the “utility-ignited” wildfire statistics in tables 1-15 should not be construed as an admission of any wrongdoing or liability by SCE. SCE further notes that the damages metrics provided may be tracked by other agencies and thus, SCE does not guarantee the accuracy of such information. Additionally, in many instances the cause of wildfires are still under investigation and even where an Authority Having Jurisdiction (AHJ) has issued a report on the cause, SCE may dispute the conclusions of such report.
10. Value of assets destroyed by utility-related ignitions, listed by asset type | 10.a. | Value of assets destroyed by utility-related ignitions (total) | N/A | N/A | N/A | N/A | N/A | N/A | Actuals 1: 150400; Actuals 2: 300800; Actuals 3: 120688284; Actuals 4: 12082300; Actuals 1: 188000; Actuals 2: 451200; Actuals 3: 2739090; Actuals 4: 338400; Actuals 1: 338400; Actuals 2: 24354000; Actuals 3: 33817422; Actuals 4: 3308800 |  |  |  | 1000 | The information provided in conjunction with all of the “utility-ignited” wildfire statistics in tables 1-13 should not be construed as an admission of any wrongdoing or liability by SCE. SCE further notes that the damages metrics provided may be tracked by other agencies and thus, SCE does not guarantee the accuracy of such information. Additionally, in many instances the cause of wildfires are still under investigation and even where an Authority Having Jurisdiction (AHJ) has issued a report on the cause, SCE may dispute the conclusions of such report.
11. Structures damaged or destroyed by utility-related ignitions | 11.a. | Number of structures destroyed by utility-related ignitions (total) | N/A | N/A | N/A | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 171; Actuals 4: 13; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 20; Actuals 3: 36; Actuals 4: 0 |  |  |  | Number of structures | The information provided in conjunction with all of the “utility-ignited” wildfire statistics in tables 1-15 should not be construed as an admission of any wrongdoing or liability by SCE. SCE further notes that the damages metrics provided may be tracked by other agencies and thus, SCE does not guarantee the accuracy of such information. Additionally, in many instances the cause of wildfires are still under investigation and even where an Authority Having Jurisdiction (AHJ) has issued a report on the cause, SCE may dispute the conclusions of such report.
11. Structures damaged or destroyed by utility-related ignitions | 11.b. | Critical infrastructure damaged/destroyed by utility-related ignitions (total) | N/A | N/A | N/A | N/A | N/A | N/A | [27 empty] | Number of structures | The information provided in conjunction with all of the “utility-ignited” wildfire statistics in tables 1-15 should not be construed as an admission of any wrongdoing or liability by SCE. SCE further notes that the damages metrics provided may be tracked by other agencies and thus, SCE does not guarantee the accuracy of such information. Additionally, in many instances the cause of wildfires are still under investigation and even where an Authority Having Jurisdiction (AHJ) has issued a report on the cause, SCE may dispute the conclusions of such report. | Data point is not currently tracked. | bar: Actuals 1 to Actuals 4
12. Acreage burned by utility-ignited wildfires | 12.a. | Acreage burned by utility-ignited wildfires | N/A | N/A | N/A | N/A | N/A | N/A | Actuals 1: 4; Actuals 2: 574; Actuals 3: 115871; Actuals 4: 12863; Actuals 1: 12; Actuals 2: 513; Actuals 3: 30; Actuals 4: 41; Actuals 1: 4.5; Actuals 2: 225; Actuals 3: 28337; Actuals 4: 22.23 |  |  |  | Acres | The information provided in conjunction with all of the “utility-ignited” wildfire statistics in tables 1-15 should not be construed as an admission of any wrongdoing or liability by SCE. SCE further notes that the damages metrics provided may be tracked by other agencies and thus, SCE does not guarantee the accuracy of such information. Additionally, in many instances the cause of wildfires are still under investigation and even where an Authority Having Jurisdiction (AHJ) has issued a report on the cause, SCE may dispute the conclusions of such report.
13. Number of utility0related ignitions | 13.a. | Number of ignitions | RFW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | Number of ignitions
13. Number of utility0related ignitions | 13.a. | Number of ignitions | HWW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | Number of ignitions
13. Number of utility0related ignitions | 13.a. | Number of ignitions | HWW & RFW | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | Number of ignitions
13. Number of utility0related ignitions | 13.a. | Number of ignitions | None | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 1; Actuals 2: 7; Actuals 3: 5; Actuals 4: 2; Actuals 1: 1; Actuals 2: 12; Actuals 3: 3; Actuals 4: 3; Actuals 1: 3; Actuals 2: 7; Actuals 3: 2; Actuals 4: 1 |  |  |  | Number of ignitions
13. Number of utility0related ignitions | 13.a. | Number of ignitions | RFW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | Number of ignitions
13. Number of utility0related ignitions | 13.a. | Number of ignitions | HWW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | Number of ignitions
13. Number of utility0related ignitions | 13.a. | Number of ignitions | HWW & RFW | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 1; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 1 |  |  |  | Number of ignitions
13. Number of utility0related ignitions | 13.a. | Number of ignitions | None | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 2; Actuals 2: 15; Actuals 3: 11; Actuals 4: 6; Actuals 1: 6; Actuals 2: 11; Actuals 3: 11; Actuals 4: 1; Actuals 1: 5; Actuals 2: 9; Actuals 3: 10; Actuals 4: 2 |  |  |  | Number of ignitions
13. Number of utility-related ignitions | 13.a. | Number of ignitions | RFW only | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 1; Actuals 4: 1; Actuals 1: 2; Actuals 2: 0; Actuals 3: 0; Actuals 4: 2; Actuals 1: 0; Actuals 2: 1; Actuals 3: 0; Actuals 4: 0 |  |  |  | Number of ignitions
13. Number of utility-related ignitions | 13.a. | Number of ignitions | HWW only | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 1; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 1; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | Number of ignitions
13. Number of utility-related ignitions | 13.a. | Number of ignitions | HWW & RFW | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 2; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 2; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | Number of ignitions
13. Number of utility-related ignitions | 13.a. | Number of ignitions | None | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 13; Actuals 2: 36; Actuals 3: 27; Actuals 4: 18; Actuals 1: 20; Actuals 2: 43; Actuals 3: 44; Actuals 4: 11; Actuals 1: 18; Actuals 2: 32; Actuals 3: 23; Actuals 4: 8 |  |  |  | Number of ignitions
14. Grid condition findings from inspection | 14.d.2.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.2.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Aerial | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.2.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.2.a.i | Number of assets inspected | N/A | AGP Inspections | HFTD Tier 2 | Distribution | Patrol Inspection | other | Actuals 1: 13982; Actuals 2: 86859; Actuals 3: 10578; Actuals 4: 627; Actuals 1: 48079; Actuals 2: 59510; Actuals 3: 2513; Actuals 4: 5; Actuals 1: 32847; Actuals 2: 72199; Actuals 3: 3105; Actuals 4: 3046 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
14. Grid condition findings from inspection | 14.d.2.a.ii | Number of assets inspected | N/A | Aerial (Matt N) | HFTD Tier 2 | Distribution | Detailed Inspection | Drone | Actuals 1: 36512.5768; Actuals 2: 36512.5768; Actuals 3: 36512.5768; Actuals 4: 36512.5768; Actuals 1: 3237; Actuals 2: 50711.85; Actuals 3: 36126; Actuals 4: 1167; Actuals 1: 23316; Actuals 2: 59148; Actuals 3: 15456; Actuals 4: 2192 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | For 2020, SCE tracked the completed aerial inspections by the year and in order to represent the 2020 completed asset inspection by quarter, SCE evenly distributed the completed inspections to each of the four quarters in 2020.
14. Grid condition findings from inspection | 14.d.2.a.ii | Number of assets inspected | N/A | Aerial (Matt N) | HFTD Tier 2 | Distribution | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 7; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 8 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | SCE Dist Aerial inspections completed using drone. Aerial only used for "Hard To Access" structures.
14. Grid condition findings from inspection | 14.d.2.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.2.a.ii | Number of assets inspected | N/A | ODI + HFRI | HFTD Tier 2 | Distribution | Detailed Inspection | other | Actuals 1: 14078; Actuals 2: 23863; Actuals 3: 19843; Actuals 4: 6117; Actuals 1: 43843; Actuals 2: 24977; Actuals 3: 2052; Actuals 4: 314; Actuals 1: 31410; Actuals 2: 26251; Actuals 3: 7857; Actuals 4: 280 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
14. Grid condition findings from inspection | 14.d.2.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.2.a.iii | Number of assets inspected | N/A | IR0Aerial | HFTD Tier 2 | Distribution | Other Inspection | Aerial | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 177; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 1003; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | SCE's Dist IR Scan uses Aerial (helicopter) for HFTD "Hard to Access" structures only.
14. Grid condition findings from inspection | 14.d.2.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.2.a.iii | Number of assets inspected | N/A | IPI + IR0Ground | HFTD Tier 2 | Distribution | Other Inspection | other | Actuals 1: 21214.1947; Actuals 2: 21214.1947; Actuals 3: 21214.1947; Actuals 4: 21214.1947; Actuals 1: 39084.3635; Actuals 2: 32456.0444; Actuals 3: 3961.36; Actuals 4: 5194.28; Actuals 1: 63394.5286; Actuals 2: 5708.08; Actuals 3: 1133.6; Actuals 4: 1147.64 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | For 2020, SCE tracked the completed other inspections by the year and in order to represent the 2020 completed asset inspection by quarter, SCE evenly distributed the completed inspections to each of the four quarters in 2020. Dist "Other" contains Dist IR Scan and Intrusive Pole Inspection (both ground inspection programs).
14. Grid condition findings from inspection | 14.d.2.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.2.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Aerial | [27 empty] | # of circuit miles inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.2.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.2.b.i | Number of circuit miles inspected | N/A | AGP Inspections | HFTD Tier 2 | Distribution | Patrol Inspection | other | Actuals 1: 473.9874; Actuals 2: 2944.505; Actuals 3: 358.5924; Actuals 4: 21.2552; Actuals 1: 1629.8697; Actuals 2: 2017.3786; Actuals 3: 85.1903; Actuals 4: 0.1695; Actuals 1: 1113.5076; Actuals 2: 2447.5335; Actuals 3: 105.259; Actuals 4: 103.2589 |  |  |  | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected.
14. Grid condition findings from inspection | 14.d.2.b.ii | Number of circuit miles inspected | N/A | Aerial (Matt N) | HFTD Tier 2 | Distribution | Detailed Inspection | Drone | Actuals 1: 1237.77; Actuals 2: 1237.77; Actuals 3: 1237.77; Actuals 4: 1237.77; Actuals 1: 109.7337; Actuals 2: 1719.1229; Actuals 3: 1224.6651; Actuals 4: 39.5611; Actuals 1: 790.4083; Actuals 2: 2005.1069; Actuals 3: 523.9557; Actuals 4: 74.3084 |  |  |  | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected.
14. Grid condition findings from inspection | 14.d.2.b.ii | Number of circuit miles inspected | N/A | Aerial (Matt N) | HFTD Tier 2 | Distribution | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0.2373; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0.2712 |  |  |  | # of circuit miles inspected by the utility | SCE Dist Aerial inspections completed using drone. Aerial only used for "Hard To Access" structures.
14. Grid condition findings from inspection | 14.d.2.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.2.b.ii | Number of circuit miles inspected | N/A | ODI + HFRI | HFTD Tier 2 | Distribution | Detailed Inspection | other | Actuals 1: 477.2418; Actuals 2: 808.9515; Actuals 3: 672.6742; Actuals 4: 207.3652; Actuals 1: 1486.2701; Actuals 2: 846.716; Actuals 3: 69.5624; Actuals 4: 10.6445; Actuals 1: 1064.7935; Actuals 2: 889.9043; Actuals 3: 266.3509; Actuals 4: 9.492 |  |  |  | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected.
14. Grid condition findings from inspection | 14.d.2.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.2.b.iii | Number of circuit miles inspected | N/A | IR0Aerial | HFTD Tier 2 | Distribution | Other Inspection | Aerial | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 6.0003; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 34.0015; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of circuit miles inspected by the utility | SCE's Dist IR Scan uses Aerial (helicopter) for HFTD "Hard to Access" structures only.
14. Grid condition findings from inspection | 14.d.2.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.2.b.iii | Number of circuit miles inspected | N/A | IPI + IR0Ground | HFTD Tier 2 | Distribution | Other Inspection | other | Actuals 1: 719.1575; Actuals 2: 719.1575; Actuals 3: 719.1575; Actuals 4: 719.1575; Actuals 1: 1324.9531; Actuals 2: 1100.2543; Actuals 3: 134.2894; Actuals 4: 176.0852; Actuals 1: 2149.0635; Actuals 2: 193.5029; Actuals 3: 38.4288; Actuals 4: 38.9048 |  |  |  | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected.
14. Grid condition findings from inspection | 14.d.2.c.i | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.2.c.i | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.2.c.i | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.2.c.i | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | other | Actuals 1: 0; Actuals 2: 7; Actuals 3: 0; Actuals 4: 0; Actuals 1: 1; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.2.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Drone | Actuals 1: 72; Actuals 2: 25; Actuals 3: 21; Actuals 4: 5; Actuals 1: 13; Actuals 2: 55; Actuals 3: 29; Actuals 4: 4; Actuals 1: 52; Actuals 2: 72; Actuals 3: 17; Actuals 4: 3 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.2.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.2.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.2.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | other | Actuals 1: 0; Actuals 2: 2; Actuals 3: 4; Actuals 4: 10; Actuals 1: 34; Actuals 2: 13; Actuals 3: 1; Actuals 4: 2; Actuals 1: 12; Actuals 2: 11; Actuals 3: 4; Actuals 4: 1 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.2.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.2.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.2.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.2.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | other | Actuals 1: 2; Actuals 2: 3; Actuals 3: 1; Actuals 4: 6; Actuals 1: 1; Actuals 2: 1; Actuals 3: 1; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 1; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.2.d.i | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.2.d.i | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.2.d.i | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.2.d.i | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | other | Actuals 1: 0; Actuals 2: 4; Actuals 3: 0; Actuals 4: 1; Actuals 1: 5; Actuals 2: 2; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.2.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Drone | Actuals 1: 1342; Actuals 2: 744; Actuals 3: 740; Actuals 4: 138; Actuals 1: 166; Actuals 2: 1011; Actuals 3: 639; Actuals 4: 50; Actuals 1: 732; Actuals 2: 773; Actuals 3: 91; Actuals 4: 17 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.2.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.2.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.2.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | other | Actuals 1: 1510; Actuals 2: 2159; Actuals 3: 866; Actuals 4: 448; Actuals 1: 3688; Actuals 2: 4049; Actuals 3: 312; Actuals 4: 607; Actuals 1: 8904; Actuals 2: 5298; Actuals 3: 2898; Actuals 4: 362 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.2.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.2.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.2.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.2.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | other | Actuals 1: 87; Actuals 2: 91; Actuals 3: 162; Actuals 4: 281; Actuals 1: 32; Actuals 2: 168; Actuals 3: 44; Actuals 4: 27; Actuals 1: 18; Actuals 2: 40; Actuals 3: 13; Actuals 4: 22 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.2.e.i | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.2.e.i | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.2.e.i | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.2.e.i | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | other | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.2.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Drone | Actuals 1: 9; Actuals 2: 21; Actuals 3: 24; Actuals 4: 4; Actuals 1: 2; Actuals 2: 7; Actuals 3: 2; Actuals 4: 1; Actuals 1: 7; Actuals 2: 3; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.2.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.2.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.2.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | other | Actuals 1: 2819; Actuals 2: 3426; Actuals 3: 2084; Actuals 4: 229; Actuals 1: 6253; Actuals 2: 3154; Actuals 3: 354; Actuals 4: 313; Actuals 1: 8045; Actuals 2: 4199; Actuals 3: 1240; Actuals 4: 137 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.2.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.2.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.2.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.2.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | other | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 1; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.3.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.3.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Aerial | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.3.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.3.a.i | Number of assets inspected | N/A | AGP Inspections | HFTD Tier 3 | Distribution | Patrol Inspection | other | Actuals 1: 33148; Actuals 2: 115234; Actuals 3: 25246; Actuals 4: 1969; Actuals 1: 54791; Actuals 2: 93433; Actuals 3: 25871; Actuals 4: 111; Actuals 1: 65525; Actuals 2: 79865; Actuals 3: 24699; Actuals 4: 4223 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
14. Grid condition findings from inspection | 14.d.3.a.ii | Number of assets inspected | N/A | Aerial (Matt N) | HFTD Tier 3 | Distribution | Detailed Inspection | Drone | Actuals 1: 35080.711; Actuals 2: 35080.711; Actuals 3: 35080.711; Actuals 4: 35080.711; Actuals 1: 3112.48; Actuals 2: 48722; Actuals 3: 34709; Actuals 4: 1125; Actuals 1: 22187; Actuals 2: 30220; Actuals 3: 4060; Actuals 4: 555 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | For 2020, SCE tracked the completed aerial inspections by the year and in order to represent the 2020 completed asset inspection by quarter, SCE evenly distributed the completed inspections to each of the four quarters in 2020.
14. Grid condition findings from inspection | 14.d.3.a.ii | Number of assets inspected | N/A | Aerial (Matt N) | HFTD Tier 3 | Distribution | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 5; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 2 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | SCE Dist Aerial inspections completed using drone. Aerial only used for "Hard To Access" structures.
14. Grid condition findings from inspection | 14.d.3.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.3.a.ii | Number of assets inspected | N/A | ODI + HFRI | HFTD Tier 3 | Distribution | Detailed Inspection | other | Actuals 1: 38510; Actuals 2: 44743; Actuals 3: 33297; Actuals 4: 25393; Actuals 1: 63609; Actuals 2: 40870; Actuals 3: 9955; Actuals 4: 332; Actuals 1: 42913; Actuals 2: 51425; Actuals 3: 16584; Actuals 4: 899 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
14. Grid condition findings from inspection | 14.d.3.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.3.a.iii | Number of assets inspected | N/A | IR0Aerial | HFTD Tier 3 | Distribution | Other Inspection | Aerial | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 118; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 826; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | SCE's Dist IR Scan uses Aerial (helicopter) for HFTD "Hard to Access" structures only.
14. Grid condition findings from inspection | 14.d.3.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.3.a.iii | Number of assets inspected | N/A | IPI + IR0Ground | HFTD Tier 3 | Distribution | Other Inspection | other | Actuals 1: 19582.3336; Actuals 2: 19582.3336; Actuals 3: 19582.3336; Actuals 4: 19582.3336; Actuals 1: 36077.874; Actuals 2: 34372.8814; Actuals 3: 3656.64; Actuals 4: 4794.72; Actuals 1: 58518.0264; Actuals 2: 5268.7732; Actuals 3: 1046.4; Actuals 4: 1059.36 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | For 2020, SCE tracked the completed other inspections by the year and in order to represent the 2020 completed asset inspection by quarter, SCE evenly distributed the completed inspections to each of the four quarters in 2020. Dist "Other" contains Dist IR Scan and Intrusive Pole Inspection (both ground inspection programs).
14. Grid condition findings from inspection | 14.d.3.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.3.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Aerial | [27 empty] | # of circuit miles inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.3.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.3.b.i | Number of circuit miles inspected | N/A | AGP Inspections | HFTD Tier 3 | Distribution | Patrol Inspection | other | Actuals 1: 1123.7114; Actuals 2: 3906.4125; Actuals 3: 855.835; Actuals 4: 66.7488; Actuals 1: 1857.4054; Actuals 2: 3167.3624; Actuals 3: 877.0224; Actuals 4: 3.7629; Actuals 1: 2221.2861; Actuals 2: 2707.4096; Actuals 3: 837.2918; Actuals 4: 143.159 |  |  |  | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected.
14. Grid condition findings from inspection | 14.d.3.b.ii | Number of circuit miles inspected | N/A | Aerial (Matt N) | HFTD Tier 3 | Distribution | Detailed Inspection | Drone | Actuals 1: 1189.23; Actuals 2: 1189.23; Actuals 3: 1189.23; Actuals 4: 1189.23; Actuals 1: 105.5125; Actuals 2: 1651.6673; Actuals 3: 1176.6291; Actuals 4: 38.1373; Actuals 1: 752.1354; Actuals 2: 1024.4527; Actuals 3: 137.6333; Actuals 4: 18.8144 |  |  |  | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected.
14. Grid condition findings from inspection | 14.d.3.b.ii | Number of circuit miles inspected | N/A | Aerial (Matt N) | HFTD Tier 3 | Distribution | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of circuit miles inspected by the utility | SCE Dist Aerial inspections completed using drone. Aerial only used for "Hard To Access" structures.
14. Grid condition findings from inspection | 14.d.3.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.3.b.ii | Number of circuit miles inspected | N/A | ODI + HFRI | HFTD Tier 3 | Distribution | Detailed Inspection | other | Actuals 1: 1305.4823; Actuals 2: 1516.7799; Actuals 3: 1128.7625; Actuals 4: 860.8183; Actuals 1: 2156.334; Actuals 2: 1385.4859; Actuals 3: 337.4728; Actuals 4: 11.2547; Actuals 1: 1454.7432; Actuals 2: 1743.2986; Actuals 3: 562.1947; Actuals 4: 30.4759 |  |  |  | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected.
14. Grid condition findings from inspection | 14.d.3.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.3.b.iii | Number of circuit miles inspected | N/A | IR0Aerial | HFTD Tier 3 | Distribution | Other Inspection | Aerial | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 4.0002; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 28.0013; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of circuit miles inspected by the utility | SCE's Dist IR Scan uses Aerial (helicopter) for HFTD "Hard to Access" structures only.
14. Grid condition findings from inspection | 14.d.3.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.3.b.iii | Number of circuit miles inspected | N/A | IPI + IR0Ground | HFTD Tier 3 | Distribution | Other Inspection | other | Actuals 1: 663.8377; Actuals 2: 663.8377; Actuals 3: 663.8377; Actuals 4: 663.8377; Actuals 1: 1223.0337; Actuals 2: 1165.2347; Actuals 3: 123.9595; Actuals 4: 162.5402; Actuals 1: 1983.7509; Actuals 2: 178.6105; Actuals 3: 35.4728; Actuals 4: 35.9121 |  |  |  | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected.
14. Grid condition findings from inspection | 14.d.3.c.i | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.3.c.i | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.3.c.i | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.3.c.i | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | other | Actuals 1: 0; Actuals 2: 9; Actuals 3: 0; Actuals 4: 0; Actuals 1: 3; Actuals 2: 3; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.3.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Drone | Actuals 1: 75; Actuals 2: 29; Actuals 3: 39; Actuals 4: 11; Actuals 1: 4; Actuals 2: 92; Actuals 3: 43; Actuals 4: 7; Actuals 1: 61; Actuals 2: 96; Actuals 3: 34; Actuals 4: 18 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.3.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.3.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.3.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | other | Actuals 1: 2; Actuals 2: 2; Actuals 3: 1; Actuals 4: 50; Actuals 1: 22; Actuals 2: 9; Actuals 3: 3; Actuals 4: 0; Actuals 1: 12; Actuals 2: 17; Actuals 3: 5; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.3.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.3.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.3.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.3.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | other | Actuals 1: 1; Actuals 2: 2; Actuals 3: 4; Actuals 4: 1; Actuals 1: 5; Actuals 2: 2; Actuals 3: 1; Actuals 4: 2; Actuals 1: 1; Actuals 2: 0; Actuals 3: 2; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.3.d.i | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.3.d.i | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.3.d.i | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.3.d.i | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | other | Actuals 1: 2; Actuals 2: 1; Actuals 3: 2; Actuals 4: 0; Actuals 1: 5; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.3.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Drone | Actuals 1: 2631; Actuals 2: 1363; Actuals 3: 1714; Actuals 4: 347; Actuals 1: 98; Actuals 2: 1929; Actuals 3: 1278; Actuals 4: 82; Actuals 1: 982; Actuals 2: 1623; Actuals 3: 205; Actuals 4: 88 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.3.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.3.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.3.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | other | Actuals 1: 3260; Actuals 2: 3527; Actuals 3: 1821; Actuals 4: 1931; Actuals 1: 3872; Actuals 2: 5608; Actuals 3: 1745; Actuals 4: 349; Actuals 1: 8641; Actuals 2: 12169; Actuals 3: 5240; Actuals 4: 142 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.3.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.3.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.3.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.3.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | other | Actuals 1: 343; Actuals 2: 217; Actuals 3: 78; Actuals 4: 790; Actuals 1: 65; Actuals 2: 86; Actuals 3: 201; Actuals 4: 320; Actuals 1: 28; Actuals 2: 186; Actuals 3: 23; Actuals 4: 38 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.3.e.i | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.3.e.i | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.3.e.i | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.3.e.i | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | other | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 1; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.3.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Drone | Actuals 1: 8; Actuals 2: 31; Actuals 3: 73; Actuals 4: 7; Actuals 1: 1; Actuals 2: 53; Actuals 3: 8; Actuals 4: 0; Actuals 1: 6; Actuals 2: 31; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.3.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.3.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.3.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | other | Actuals 1: 5677; Actuals 2: 5363; Actuals 3: 4054; Actuals 4: 485; Actuals 1: 5791; Actuals 2: 4539; Actuals 3: 1155; Actuals 4: 242; Actuals 1: 6244; Actuals 2: 7349; Actuals 3: 2078; Actuals 4: 121 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.3.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.3.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Aerial | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.3.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.3.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | other | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.4.a.i | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.4.a.i | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Aerial | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.4.a.i | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.4.a.i | Number of assets inspected | N/A | AGP Inspections | Non-HFTD | Distribution | Patrol Inspection | other | Actuals 1: 48029; Actuals 2: 571601; Actuals 3: 315663; Actuals 4: 76575; Actuals 1: 56376; Actuals 2: 302501; Actuals 3: 507642; Actuals 4: 143569; Actuals 1: 129657; Actuals 2: 276444; Actuals 3: 394039; Actuals 4: 203524 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
14. Grid condition findings from inspection | 14.d.4.a.ii | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE Dist Aerial completed in HFRA only
14. Grid condition findings from inspection | 14.d.4.a.ii | Number of assets inspected | N/A | Aerial (Matt N) | Non-HFTD | Distribution | Detailed Inspection | Aerial | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE Dist Aerial inspections completed using drone. Aerial only used for "Hard To Access" structures.
14. Grid condition findings from inspection | 14.d.4.a.ii | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.4.a.ii | Number of assets inspected | N/A | ODI + HFRI | Non-HFTD | Distribution | Detailed Inspection | other | Actuals 1: 11549; Actuals 2: 33546; Actuals 3: 56817; Actuals 4: 103824; Actuals 1: 15701; Actuals 2: 39557; Actuals 3: 78391; Actuals 4: 76425; Actuals 1: 15037; Actuals 2: 32210; Actuals 3: 63510; Actuals 4: 81427 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
14. Grid condition findings from inspection | 14.d.4.a.iii | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.4.a.iii | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Aerial | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE's Dist IR Scan uses Aerial (helicopter) for HFTD "Hard to Access" structures only.
14. Grid condition findings from inspection | 14.d.4.a.iii | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Other Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.4.a.iii | Number of assets inspected | N/A | IPI + IR-Ground | Non-HFTD | Distribution | Other Inspection | other | Actuals 1: 24214; Actuals 2: 24214; Actuals 3: 24214; Actuals 4: 24214; Actuals 1: 30434; Actuals 2: 58552; Actuals 3: 28910; Actuals 4: 19301; Actuals 1: 35405; Actuals 2: 17460; Actuals 3: 16198; Actuals 4: 29472 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | For 2020, SCE tracked the completed other inspections by the year and in order to represent the 2020 completed asset inspection by quarter, SCE evenly distributed the completed inspections to each of the four quarters in 2020. Dist "Other" for non-HFTD contains Intrusive Pole Inspection counts only, as Dist IR is only conducted in HFRA.
14. Grid condition findings from inspection | 14.d.4.b.i | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.4.b.i | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Aerial | [27 empty] | # of circuit miles inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.4.b.i | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.4.b.i | Number of circuit miles inspected | N/A | AGP Inspections | Non-HFTD | Distribution | Patrol Inspection | other | Actuals 1: 1436.0893; Actuals 2: 17091.1346; Actuals 3: 9438.4699; Actuals 4: 2289.628; Actuals 1: 1685.6685; Actuals 2: 9044.92; Actuals 3: 15178.7308; Actuals 4: 4292.7796; Actuals 1: 3876.8043; Actuals 2: 8265.8036; Actuals 3: 11781.9485; Actuals 4: 6085.4618 |  |  |  | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected.
14. Grid condition findings from inspection | 14.d.4.b.ii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. | SCE Dist Aerial completed in HFRA only
14. Grid condition findings from inspection | 14.d.4.b.ii | Number of circuit miles inspected | N/A | Aerial (Matt N) | Non-HFTD | Distribution | Detailed Inspection | Aerial | [27 empty] | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. | SCE Dist Aerial inspections completed using drone. Aerial only used for "Hard To Access" structures.
14. Grid condition findings from inspection | 14.d.4.b.ii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.4.b.ii | Number of circuit miles inspected | N/A | ODI + HFRI | Non-HFTD | Distribution | Detailed Inspection | other | Actuals 1: 345.3204; Actuals 2: 1003.0409; Actuals 3: 1698.8546; Actuals 4: 3104.3857; Actuals 1: 469.4672; Actuals 2: 1182.7726; Actuals 3: 2343.9272; Actuals 4: 2285.1429; Actuals 1: 449.6133; Actuals 2: 963.0939; Actuals 3: 1898.9784; Actuals 4: 2434.705 |  |  |  | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected.
14. Grid condition findings from inspection | 14.d.4.b.iii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.4.b.iii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Aerial | [27 empty] | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.4.b.iii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Other Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.4.b.iii | Number of circuit miles inspected | N/A | IPI + IR-Ground | Non-HFTD | Distribution | Other Inspection | other | Actuals 1: 724.0098; Actuals 2: 724.0098; Actuals 3: 724.0098; Actuals 4: 724.0098; Actuals 1: 909.9907; Actuals 2: 1750.7319; Actuals 3: 864.4224; Actuals 4: 577.1088; Actuals 1: 1058.6259; Actuals 2: 522.0621; Actuals 3: 484.3277; Actuals 4: 881.2264 |  |  |  | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected.
14. Grid condition findings from inspection | 14.d.4.c.i | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.4.c.i | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.4.c.i | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.4.c.i | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | other | Actuals 1: 0; Actuals 2: 58; Actuals 3: 0; Actuals 4: 4; Actuals 1: 10; Actuals 2: 7; Actuals 3: 1; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 2 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.4.c.ii | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Drone | Actuals 1: 3; Actuals 2: 4; Actuals 3: 4; Actuals 4: 1; Actuals 1: 0; Actuals 2: 3; Actuals 3: 0; Actuals 4: 0; Actuals 1: 2; Actuals 2: 1; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.4.c.ii | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.4.c.ii | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.4.c.ii | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | other | Actuals 1: 1; Actuals 2: 54; Actuals 3: 111; Actuals 4: 198; Actuals 1: 43; Actuals 2: 125; Actuals 3: 164; Actuals 4: 154; Actuals 1: 33; Actuals 2: 38; Actuals 3: 60; Actuals 4: 79 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.4.c.iii | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.4.c.iii | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.4.c.iii | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.4.c.iii | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | other | Actuals 1: 12; Actuals 2: 28; Actuals 3: 22; Actuals 4: 20; Actuals 1: 16; Actuals 2: 32; Actuals 3: 21; Actuals 4: 10; Actuals 1: 15; Actuals 2: 22; Actuals 3: 22; Actuals 4: 12 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.4.d.i | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.4.d.i | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.4.d.i | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.4.d.i | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | other | Actuals 1: 3; Actuals 2: 246; Actuals 3: 107; Actuals 4: 109; Actuals 1: 20; Actuals 2: 32; Actuals 3: 17; Actuals 4: 2; Actuals 1: 0; Actuals 2: 2; Actuals 3: 5; Actuals 4: 21 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.4.d.ii | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Drone | Actuals 1: 55; Actuals 2: 18; Actuals 3: 30; Actuals 4: 14; Actuals 1: 2; Actuals 2: 6; Actuals 3: 14; Actuals 4: 2; Actuals 1: 0; Actuals 2: 0; Actuals 3: 1; Actuals 4: 1 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.4.d.ii | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.4.d.ii | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.4.d.ii | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | other | Actuals 1: 1795; Actuals 2: 3708; Actuals 3: 5831; Actuals 4: 9595; Actuals 1: 1939; Actuals 2: 8267; Actuals 3: 17953; Actuals 4: 23016; Actuals 1: 4483; Actuals 2: 8769; Actuals 3: 17208; Actuals 4: 26138 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.4.d.iii | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.4.d.iii | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.4.d.iii | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.4.d.iii | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | other | Actuals 1: 1428; Actuals 2: 876; Actuals 3: 683; Actuals 4: 1281; Actuals 1: 1518; Actuals 2: 1000; Actuals 3: 788; Actuals 4: 787; Actuals 1: 938; Actuals 2: 603; Actuals 3: 754; Actuals 4: 1330 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.4.e.i | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.4.e.i | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.4.e.i | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.4.e.i | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | other | Actuals 1: 6; Actuals 2: 3; Actuals 3: 3; Actuals 4: 0; Actuals 1: 0; Actuals 2: 3; Actuals 3: 3; Actuals 4: 0; Actuals 1: 3; Actuals 2: 3; Actuals 3: 1; Actuals 4: 4 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.4.e.ii | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 1; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.4.e.ii | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.4.e.ii | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.4.e.ii | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | other | Actuals 1: 2690; Actuals 2: 7067; Actuals 3: 10533; Actuals 4: 15630; Actuals 1: 2916; Actuals 2: 7829; Actuals 3: 14730; Actuals 4: 16563; Actuals 1: 3140; Actuals 2: 5443; Actuals 3: 15117; Actuals 4: 19801 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.4.e.iii | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.d.4.e.iii | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.4.e.iii | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.d.4.e.iii | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | other | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.2.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.2.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Aerial | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.2.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.2.a.i | Number of assets inspected | N/A | Trans Routine | HFTD Tier 2 | Transmission | Patrol Inspection | other | Actuals 1: 52; Actuals 2: 52; Actuals 3: 52; Actuals 4: 52; Actuals 1: 21.32; Actuals 2: 50.96; Actuals 3: 58.24; Actuals 4: 41.08; Actuals 1: 10; Actuals 2: 40.56; Actuals 3: 56.68; Actuals 4: 42.64 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | For 2020, SCE tracked the completed inspections by the year and in order to represent the 2020 completed asset inspection by quarter, SCE evenly distributed the completed inspections to each of the four quarters in 2020. For Trans Patrol Inspections, SCE tracks counts of circuits inspected.
14. Grid condition findings from inspection | 14.t.2.a.ii | Number of assets inspected | N/A | Aerial (Matt N) | HFTD Tier 2 | Transmission | Detailed Inspection | Drone | Actuals 1: 4167.2706; Actuals 2: 4167.2706; Actuals 3: 4167.2706; Actuals 4: 4167.2706; Actuals 1: 2622; Actuals 2: 7246.98; Actuals 3: 1712.28; Actuals 4: 139.08; Actuals 1: 3655; Actuals 2: 3738; Actuals 3: 1726; Actuals 4: 209 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
14. Grid condition findings from inspection | 14.t.2.a.ii | Number of assets inspected | N/A | Aerial (Matt N) | HFTD Tier 2 | Transmission | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 11 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | SCE Trans Detailed inspections use Aerial (helicopter) for "Hard to Access" structures only.
14. Grid condition findings from inspection | 14.t.2.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.2.a.ii | Number of assets inspected | N/A | Trans Det +Trans HFRA | HFTD Tier 2 | Transmission | Detailed Inspection | other | Actuals 1: 97.24; Actuals 2: 181.48; Actuals 3: 76.96; Actuals 4: 76.44; Actuals 1: 2480.92; Actuals 2: 6302.92; Actuals 3: 2201.68; Actuals 4: 19.76; Actuals 1: 1648.4; Actuals 2: 5391.36; Actuals 3: 1023.36; Actuals 4: 69.68 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. Trans Detailed and Trans HFRA inspections use different conversion methods as such the count to circuit mi relationship is varied.
14. Grid condition findings from inspection | 14.t.2.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.2.a.iii | Number of assets inspected | N/A | IR0Aerial | HFTD Tier 2 | Transmission | Other Inspection | Aerial | Actuals 1: 1099.3455; Actuals 2: 1099.3455; Actuals 3: 1099.3455; Actuals 4: 1099.3455; Actuals 1: 0; Actuals 2: 319.73; Actuals 3: 1664.3477; Actuals 4: 2601.6382; Actuals 1: 772.6077; Actuals 2: 3383.0057; Actuals 3: 551.8627; Actuals 4: 0 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | For 2020, SCE tracked the completed other inspections by the year and in order to represent the 2020 completed asset inspection by quarter, SCE evenly distributed the completed inspections to each of the four quarters in 2020. SCE Trans "Other" type inspections consists of Trans IR Scan (in which scans are completed 100% by helicopter) and Intrusive Pole Inspections (Ground).
14. Grid condition findings from inspection | 14.t.2.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.2.a.iii | Number of assets inspected | N/A | IPI | HFTD Tier 2 | Transmission | Other Inspection | other | Actuals 1: 218.92; Actuals 2: 218.92; Actuals 3: 218.92; Actuals 4: 218.92; Actuals 1: 296.92; Actuals 2: 333.32; Actuals 3: 175.76; Actuals 4: 435.76; Actuals 1: 66.04; Actuals 2: 169.52; Actuals 3: 72.8; Actuals 4: 76.96 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | For 2020, SCE tracked the completed other inspections by the year and in order to represent the 2020 completed asset inspection by quarter, SCE evenly distributed the completed inspections to each of the four quarters in 2020. SCE Trans "Other" type inspections consists of Trans IR Scan (in which scans are completed 100% by helicopter) and Intrusive Pole Inspections (Ground).
14. Grid condition findings from inspection | 14.t.2.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.2.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Aerial | [27 empty] | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.2.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.2.b.i | Number of circuit miles inspected | N/A | Trans Routine | HFTD Tier 2 | Transmission | Patrol Inspection | other | Actuals 1: 578.3285; Actuals 2: 578.3285; Actuals 3: 578.3285; Actuals 4: 578.3285; Actuals 1: 237.1147; Actuals 2: 566.7619; Actuals 3: 647.7279; Actuals 4: 456.8795; Actuals 1: 111.217; Actuals 2: 451.0962; Actuals 3: 630.3781; Actuals 4: 474.2294 |  |  |  | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected.
14. Grid condition findings from inspection | 14.t.2.b.ii | Number of circuit miles inspected | N/A | Aerial (Matt N) | HFTD Tier 2 | Transmission | Detailed Inspection | Drone | Actuals 1: 494.76; Actuals 2: 494.76; Actuals 3: 494.76; Actuals 4: 494.76; Actuals 1: 311.2975; Actuals 2: 860.3991; Actuals 3: 203.2908; Actuals 4: 16.5123; Actuals 1: 433.9406; Actuals 2: 443.7948; Actuals 3: 204.9197; Actuals 4: 24.8136 |  |  |  | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected.
14. Grid condition findings from inspection | 14.t.2.b.ii | Number of circuit miles inspected | N/A | Aerial (Matt N) | HFTD Tier 2 | Transmission | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of circuit miles inspected by the utility | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.2.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.2.b.ii | Number of circuit miles inspected | N/A | Trans Det +Trans HFRA | HFTD Tier 2 | Transmission | Detailed Inspection | other | Actuals 1: 1080.04; Actuals 2: 2021.24; Actuals 3: 853.84; Actuals 4: 847.6; Actuals 1: 374; Actuals 2: 911; Actuals 3: 517; Actuals 4: 148; Actuals 1: 312; Actuals 2: 723; Actuals 3: 296; Actuals 4: 146 |  |  |  | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. Trans Detailed and Trans HFRA inspections use different conversion methods as such the count to circuit mi relationship is varied.
14. Grid condition findings from inspection | 14.t.2.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.2.b.iii | Number of circuit miles inspected | N/A | IR0Aerial | HFTD Tier 2 | Transmission | Other Inspection | Aerial | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected.
14. Grid condition findings from inspection | 14.t.2.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.2.b.iii | Number of circuit miles inspected | N/A | IPI | HFTD Tier 2 | Transmission | Other Inspection | other | Actuals 1: 16.6439; Actuals 2: 16.6439; Actuals 3: 16.6439; Actuals 4: 16.6439; Actuals 1: 22.5741; Actuals 2: 25; Actuals 3: 13.3626; Actuals 4: 33.1297; Actuals 1: 5.0209; Actuals 2: 12.8882; Actuals 3: 5.5348; Actuals 4: 5.8511 |  |  |  | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected.
14. Grid condition findings from inspection | 14.t.2.c.i | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.2.c.i | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.2.c.i | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.2.c.i | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | other | Actuals 1: 5; Actuals 2: 4; Actuals 3: 10; Actuals 4: 17; Actuals 1: 5; Actuals 2: 11; Actuals 3: 4; Actuals 4: 2; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.2.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Drone | Actuals 1: 3; Actuals 2: 9; Actuals 3: 20; Actuals 4: 21; Actuals 1: 8; Actuals 2: 16; Actuals 3: 7; Actuals 4: 0; Actuals 1: 6; Actuals 2: 4; Actuals 3: 0; Actuals 4: 1 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.2.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.2.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.2.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | other | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.2.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.2.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.2.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.2.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | other | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 1; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.2.d.i | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.2.d.i | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.2.d.i | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.2.d.i | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | other | Actuals 1: 312; Actuals 2: 934; Actuals 3: 203; Actuals 4: 77; Actuals 1: 126; Actuals 2: 351; Actuals 3: 198; Actuals 4: 91; Actuals 1: 80; Actuals 2: 157; Actuals 3: 148; Actuals 4: 91 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.2.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Drone | Actuals 1: 181; Actuals 2: 220; Actuals 3: 314; Actuals 4: 184; Actuals 1: 100; Actuals 2: 156; Actuals 3: 54; Actuals 4: 9; Actuals 1: 8; Actuals 2: 93; Actuals 3: 15; Actuals 4: 12 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.2.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.2.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.2.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | other | Actuals 1: 409; Actuals 2: 1859; Actuals 3: 493; Actuals 4: 135; Actuals 1: 135; Actuals 2: 302; Actuals 3: 56; Actuals 4: 1; Actuals 1: 72; Actuals 2: 245; Actuals 3: 45; Actuals 4: 2 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.2.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.2.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.2.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.2.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | other | Actuals 1: 6; Actuals 2: 37; Actuals 3: 35; Actuals 4: 48; Actuals 1: 7; Actuals 2: 32; Actuals 3: 19; Actuals 4: 1; Actuals 1: 5; Actuals 2: 9; Actuals 3: 7; Actuals 4: 5 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.2.e.i | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.2.e.i | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.2.e.i | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.2.e.i | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | other | Actuals 1: 68; Actuals 2: 237; Actuals 3: 92; Actuals 4: 22; Actuals 1: 343; Actuals 2: 143; Actuals 3: 90; Actuals 4: 24; Actuals 1: 36; Actuals 2: 22; Actuals 3: 51; Actuals 4: 50 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.2.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Drone | Actuals 1: 3; Actuals 2: 51; Actuals 3: 184; Actuals 4: 40; Actuals 1: 16; Actuals 2: 70; Actuals 3: 11; Actuals 4: 2; Actuals 1: 0; Actuals 2: 1; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.2.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.2.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.2.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | other | Actuals 1: 28; Actuals 2: 83; Actuals 3: 15; Actuals 4: 34; Actuals 1: 54; Actuals 2: 146; Actuals 3: 13; Actuals 4: 0; Actuals 1: 40; Actuals 2: 75; Actuals 3: 15; Actuals 4: 1 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.2.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.2.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.2.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.2.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | other | Actuals 1: 1; Actuals 2: 0; Actuals 3: 0; Actuals 4: 1; Actuals 1: 0; Actuals 2: 0; Actuals 3: 3; Actuals 4: 4; Actuals 1: 1; Actuals 2: 2; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.3.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.3.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Aerial | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.3.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.3.a.i | Number of assets inspected | N/A | Trans Routine | HFTD Tier 3 | Transmission | Patrol Inspection | other | Actuals 1: 48; Actuals 2: 48; Actuals 3: 48; Actuals 4: 48; Actuals 1: 19.68; Actuals 2: 47.04; Actuals 3: 53.76; Actuals 4: 37.92; Actuals 1: 7; Actuals 2: 37.44; Actuals 3: 52.32; Actuals 4: 39.36 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | For 2020, SCE tracked the completed inspections by the year and in order to represent the 2020 completed asset inspection by quarter, SCE evenly distributed the completed inspections to each of the four quarters in 2020. For Trans Patrol Inspections, SCE tracks counts of circuits inspected.
14. Grid condition findings from inspection | 14.t.3.a.ii | Number of assets inspected | N/A | Aerial (Matt N) | HFTD Tier 3 | Transmission | Detailed Inspection | Drone | Actuals 1: 3143.7304; Actuals 2: 3143.7304; Actuals 3: 3143.7304; Actuals 4: 3143.7304; Actuals 1: 1978; Actuals 2: 5467.02; Actuals 3: 1291.72; Actuals 4: 104.92; Actuals 1: 2792; Actuals 2: 3349; Actuals 3: 1437; Actuals 4: 216 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
14. Grid condition findings from inspection | 14.t.3.a.ii | Number of assets inspected | N/A | Aerial (Matt N) | HFTD Tier 3 | Transmission | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | SCE Trans Detailed inspections use Aerial (helicopter) for "Hard to Access" structures only.
14. Grid condition findings from inspection | 14.t.3.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.3.a.ii | Number of assets inspected | N/A | Trans Det +Trans HFRA | HFTD Tier 3 | Transmission | Detailed Inspection | other | Actuals 1: 89.76; Actuals 2: 167.52; Actuals 3: 71.04; Actuals 4: 70.56; Actuals 1: 2290.08; Actuals 2: 5818.08; Actuals 3: 2032.32; Actuals 4: 18.24; Actuals 1: 1521.6; Actuals 2: 4976.64; Actuals 3: 944.64; Actuals 4: 64.32 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. Trans Detailed and Trans HFRA inspections use different conversion methods as such the count to circuit mi relationship is varied.
14. Grid condition findings from inspection | 14.t.3.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.3.a.iii | Number of assets inspected | N/A | IR0Aerial | HFTD Tier 3 | Transmission | Other Inspection | Aerial | Actuals 1: 1014.7804; Actuals 2: 1014.7804; Actuals 3: 1014.7804; Actuals 4: 1014.7804; Actuals 1: 0; Actuals 2: 295.1353; Actuals 3: 1536.3209; Actuals 4: 2401.5122; Actuals 1: 713.1764; Actuals 2: 3122.7745; Actuals 3: 509.4117; Actuals 4: 0 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | For 2020, SCE tracked the completed other inspections by the year and in order to represent the 2020 completed asset inspection by quarter, SCE evenly distributed the completed inspections to each of the four quarters in 2020. SCE Trans "Other" type inspections consists of Trans IR Scan (in which scans are completed 100% by helicopter) and Intrusive Pole Inspections (Ground).
14. Grid condition findings from inspection | 14.t.3.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.3.a.iii | Number of assets inspected | N/A | IPI | HFTD Tier 3 | Transmission | Other Inspection | other | Actuals 1: 202.08; Actuals 2: 202.08; Actuals 3: 202.08; Actuals 4: 202.08; Actuals 1: 274.08; Actuals 2: 307.68; Actuals 3: 162.24; Actuals 4: 402.24; Actuals 1: 60.96; Actuals 2: 156.48; Actuals 3: 67.2; Actuals 4: 71.04 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | For 2020, SCE tracked the completed other inspections by the year and in order to represent the 2020 completed asset inspection by quarter, SCE evenly distributed the completed inspections to each of the four quarters in 2020. SCE Trans "Other" type inspections consists of Trans IR Scan (in which scans are completed 100% by helicopter) and Intrusive Pole Inspections (Ground).
14. Grid condition findings from inspection | 14.t.3.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.3.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Aerial | [27 empty] | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.3.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.3.b.i | Number of circuit miles inspected | N/A | Trans Routine | HFTD Tier 3 | Transmission | Patrol Inspection | other | Actuals 1: 533.8417; Actuals 2: 533.8417; Actuals 3: 533.8417; Actuals 4: 533.8417; Actuals 1: 218.8751; Actuals 2: 523.1649; Actuals 3: 597.9027; Actuals 4: 421.7349; Actuals 1: 77.8519; Actuals 2: 416.3965; Actuals 3: 581.8875; Actuals 4: 437.7502 |  |  |  | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected.
14. Grid condition findings from inspection | 14.t.3.b.ii | Number of circuit miles inspected | N/A | Aerial (Matt N) | HFTD Tier 3 | Transmission | Detailed Inspection | Drone | Actuals 1: 373.24; Actuals 2: 373.24; Actuals 3: 373.24; Actuals 4: 373.24; Actuals 1: 234.8384; Actuals 2: 649.073; Actuals 3: 153.3597; Actuals 4: 12.4566; Actuals 1: 331.4807; Actuals 2: 397.6107; Actuals 3: 170.6081; Actuals 4: 25.6446 |  |  |  | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected.
14. Grid condition findings from inspection | 14.t.3.b.ii | Number of circuit miles inspected | N/A | Aerial (Matt N) | HFTD Tier 3 | Transmission | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of circuit miles inspected by the utility | SCE Trans Detailed inspections use Aerial (helicopter) for "Hard to Access" structures only.
14. Grid condition findings from inspection | 14.t.3.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.3.b.ii | Number of circuit miles inspected | N/A | Trans Det +Trans HFRA | HFTD Tier 3 | Transmission | Detailed Inspection | other | Actuals 1: 996.96; Actuals 2: 1865.76; Actuals 3: 788.16; Actuals 4: 782.4; Actuals 1: 500; Actuals 2: 847; Actuals 3: 712; Actuals 4: 275; Actuals 1: 428; Actuals 2: 1080; Actuals 3: 400; Actuals 4: 278 |  |  |  | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. Trans Detailed and Trans HFRA inspections use different conversion methods as such the count to circuit mi relationship is varied.
14. Grid condition findings from inspection | 14.t.3.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.3.b.iii | Number of circuit miles inspected | N/A | IR0Aerial | HFTD Tier 3 | Transmission | Other Inspection | Aerial | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected.
14. Grid condition findings from inspection | 14.t.3.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.3.b.iii | Number of circuit miles inspected | N/A | IPI | HFTD Tier 3 | Transmission | Other Inspection | other | Actuals 1: 15.3636; Actuals 2: 15.3636; Actuals 3: 15.3636; Actuals 4: 15.3636; Actuals 1: 20.8376; Actuals 2: 23; Actuals 3: 12.3347; Actuals 4: 30.5813; Actuals 1: 4.6346; Actuals 2: 11.8968; Actuals 3: 5.109; Actuals 4: 5.401 |  |  |  | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected.
14. Grid condition findings from inspection | 14.t.3.c.i | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.3.c.i | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.3.c.i | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.3.c.i | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | other | Actuals 1: 6; Actuals 2: 2; Actuals 3: 6; Actuals 4: 8; Actuals 1: 6; Actuals 2: 6; Actuals 3: 16; Actuals 4: 3; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.3.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Drone | Actuals 1: 4; Actuals 2: 6; Actuals 3: 16; Actuals 4: 9; Actuals 1: 9; Actuals 2: 22; Actuals 3: 12; Actuals 4: 1; Actuals 1: 2; Actuals 2: 4; Actuals 3: 2; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.3.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.3.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.3.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | other | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 1; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.3.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.3.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.3.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.3.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | other | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.3.d.i | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.3.d.i | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.3.d.i | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.3.d.i | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | other | Actuals 1: 142; Actuals 2: 852; Actuals 3: 295; Actuals 4: 60; Actuals 1: 204; Actuals 2: 351; Actuals 3: 290; Actuals 4: 57; Actuals 1: 70; Actuals 2: 149; Actuals 3: 160; Actuals 4: 88 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.3.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Drone | Actuals 1: 252; Actuals 2: 178; Actuals 3: 179; Actuals 4: 110; Actuals 1: 70; Actuals 2: 181; Actuals 3: 71; Actuals 4: 23; Actuals 1: 22; Actuals 2: 99; Actuals 3: 45; Actuals 4: 8 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.3.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.3.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.3.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | other | Actuals 1: 302; Actuals 2: 2175; Actuals 3: 438; Actuals 4: 388; Actuals 1: 186; Actuals 2: 630; Actuals 3: 151; Actuals 4: 0; Actuals 1: 162; Actuals 2: 296; Actuals 3: 89; Actuals 4: 19 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.3.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.3.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.3.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.3.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | other | Actuals 1: 10; Actuals 2: 9; Actuals 3: 4; Actuals 4: 30; Actuals 1: 12; Actuals 2: 3; Actuals 3: 1; Actuals 4: 75; Actuals 1: 1; Actuals 2: 2; Actuals 3: 6; Actuals 4: 3 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.3.e.i | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.3.e.i | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.3.e.i | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.3.e.i | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | other | Actuals 1: 62; Actuals 2: 148; Actuals 3: 79; Actuals 4: 27; Actuals 1: 264; Actuals 2: 106; Actuals 3: 74; Actuals 4: 20; Actuals 1: 27; Actuals 2: 31; Actuals 3: 67; Actuals 4: 21 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.3.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Drone | Actuals 1: 2; Actuals 2: 74; Actuals 3: 258; Actuals 4: 53; Actuals 1: 21; Actuals 2: 71; Actuals 3: 18; Actuals 4: 1; Actuals 1: 2; Actuals 2: 4; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.3.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.3.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.3.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | other | Actuals 1: 9; Actuals 2: 184; Actuals 3: 43; Actuals 4: 92; Actuals 1: 96; Actuals 2: 243; Actuals 3: 38; Actuals 4: 0; Actuals 1: 70; Actuals 2: 261; Actuals 3: 35; Actuals 4: 1 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.3.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.3.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.3.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.3.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | other | Actuals 1: 3; Actuals 2: 1; Actuals 3: 2; Actuals 4: 3; Actuals 1: 0; Actuals 2: 1; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.4.a.i | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.4.a.i | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Aerial | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.4.a.i | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.4.a.i | Number of assets inspected | N/A | Trans Routine | Non-HFTD | Transmission | Patrol Inspection | other | Actuals 1: 194; Actuals 2: 194; Actuals 3: 194; Actuals 4: 194; Actuals 1: 117; Actuals 2: 100; Actuals 3: 143; Actuals 4: 146; Actuals 1: 102; Actuals 2: 95; Actuals 3: 146; Actuals 4: 176 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | For 2020, SCE tracked the completed inspections by the year and in order to represent the 2020 completed asset inspection by quarter, SCE evenly distributed the completed inspections to each of the four quarters in 2020. For Trans Patrol Inspections, SCE tracks counts of circuits inspected.
14. Grid condition findings from inspection | 14.t.4.a.ii | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE Trans Aerial inspection is HFTD only
14. Grid condition findings from inspection | 14.t.4.a.ii | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Aerial | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE Trans Aerial inspection is HFTD only
14. Grid condition findings from inspection | 14.t.4.a.ii | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.4.a.ii | Number of assets inspected | N/A | Trans Det +Trans HFRA | Non-HFTD | Transmission | Detailed Inspection | other | Actuals 1: 33.2683; Actuals 2: 77.5061; Actuals 3: 81.1926; Actuals 4: 59.0737; Actuals 1: 167; Actuals 2: 92; Actuals 3: 48; Actuals 4: 40; Actuals 1: 25; Actuals 2: 84; Actuals 3: 297; Actuals 4: 65 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. Trans Detailed and Trans HFRA inspections use different conversion methods as such the count to circuit mi relationship is varied.
14. Grid condition findings from inspection | 14.t.4.a.iii | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.4.a.iii | Number of assets inspected | N/A | IR-Aerial | Non-HFTD | Transmission | Other Inspection | Aerial | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | For 2020, SCE tracked the completed other inspections by the year and in order to represent the 2020 completed asset inspection by quarter, SCE evenly distributed the completed inspections to each of the four quarters in 2020. SCE Trans "Other" type inspections consists of Trans IR Scan (in which scans are completed 100% by helicopter) and Intrusive Pole Inspections (Ground). | SCE Trans IR scan is HFTD only
14. Grid condition findings from inspection | 14.t.4.a.iii | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Other Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.4.a.iii | Number of assets inspected | N/A | IPI | Non-HFTD | Transmission | Other Inspection | other | Actuals 1: 1594; Actuals 2: 1594; Actuals 3: 1594; Actuals 4: 1594; Actuals 1: 2939; Actuals 2: 1352; Actuals 3: 2054; Actuals 4: 1438; Actuals 1: 2685; Actuals 2: 1045; Actuals 3: 1551; Actuals 4: 3615 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | For 2020, SCE tracked the completed other inspections by the year and in order to represent the 2020 completed asset inspection by quarter, SCE evenly distributed the completed inspections to each of the four quarters in 2020. SCE Trans "Other" type inspections consists of Trans IR Scan (in which scans are completed 100% by helicopter) and Intrusive Pole Inspections (Ground).
14. Grid condition findings from inspection | 14.t.4.b.i | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.4.b.i | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Aerial | [27 empty] | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.4.b.i | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.4.b.i | Number of circuit miles inspected | N/A | Trans Routine | Non-HFTD | Transmission | Patrol Inspection | other | Actuals 1: 2157.6102; Actuals 2: 2157.6102; Actuals 3: 2157.6102; Actuals 4: 2157.6102; Actuals 1: 1301.2391; Actuals 2: 1112.1702; Actuals 3: 1590.4034; Actuals 4: 1623.7685; Actuals 1: 1134.4136; Actuals 2: 1056.5617; Actuals 3: 1623.7685; Actuals 4: 1957.4196 |  |  |  | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected.
14. Grid condition findings from inspection | 14.t.4.b.ii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. | SCE Trans Aerial inspection is HFTD only
14. Grid condition findings from inspection | 14.t.4.b.ii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Aerial | [27 empty] | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. | SCE Trans Aerial inspection is HFTD only
14. Grid condition findings from inspection | 14.t.4.b.ii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.4.b.ii | Number of circuit miles inspected | N/A | Trans Det +Trans HFRA | Non-HFTD | Transmission | Detailed Inspection | other | Actuals 1: 370; Actuals 2: 862; Actuals 3: 903; Actuals 4: 657; Actuals 1: 537; Actuals 2: 671; Actuals 3: 369; Actuals 4: 445; Actuals 1: 267; Actuals 2: 494; Actuals 3: 761; Actuals 4: 502 |  |  |  | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. Trans Detailed and Trans HFRA inspections use different conversion methods as such the count to circuit mi relationship is varied.
14. Grid condition findings from inspection | 14.t.4.b.iii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.4.b.iii | Number of circuit miles inspected | N/A | IR-Aerial | Non-HFTD | Transmission | Other Inspection | Aerial | [27 empty] | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. | SCE Trans IR scan is HFTD only
14. Grid condition findings from inspection | 14.t.4.b.iii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Other Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.4.b.iii | Number of circuit miles inspected | N/A | IPI | Non-HFTD | Transmission | Other Inspection | other | Actuals 1: 121.1878; Actuals 2: 121.1878; Actuals 3: 121.1878; Actuals 4: 121.1878; Actuals 1: 223.4448; Actuals 2: 104; Actuals 3: 156.1605; Actuals 4: 109.3275; Actuals 1: 204.1338; Actuals 2: 79.4487; Actuals 3: 117.9186; Actuals 4: 274.8394 |  |  |  | # of circuit miles inspected by the utility | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected.
14. Grid condition findings from inspection | 14.t.4.c.i | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 1; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.4.c.i | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.4.c.i | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.4.c.i | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | other | Actuals 1: 39; Actuals 2: 27; Actuals 3: 48; Actuals 4: 34; Actuals 1: 38; Actuals 2: 50; Actuals 3: 28; Actuals 4: 10; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.4.c.ii | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Drone | Actuals 1: 1; Actuals 2: 3; Actuals 3: 2; Actuals 4: 6; Actuals 1: 1; Actuals 2: 0; Actuals 3: 1; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.4.c.ii | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.4.c.ii | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.4.c.ii | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | other | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.4.c.iii | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.4.c.iii | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.4.c.iii | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.4.c.iii | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | other | Actuals 1: 0; Actuals 2: 0; Actuals 3: 1; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 1; Actuals 1: 1; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.4.d.i | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.4.d.i | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.4.d.i | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.4.d.i | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | other | Actuals 1: 1172; Actuals 2: 939; Actuals 3: 587; Actuals 4: 629; Actuals 1: 1134; Actuals 2: 762; Actuals 3: 577; Actuals 4: 480; Actuals 1: 737; Actuals 2: 725; Actuals 3: 794; Actuals 4: 603 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.4.d.ii | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Drone | Actuals 1: 49; Actuals 2: 45; Actuals 3: 37; Actuals 4: 31; Actuals 1: 4; Actuals 2: 5; Actuals 3: 2; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.4.d.ii | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.4.d.ii | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.4.d.ii | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | other | Actuals 1: 32; Actuals 2: 46; Actuals 3: 13; Actuals 4: 55; Actuals 1: 13; Actuals 2: 4; Actuals 3: 6; Actuals 4: 8; Actuals 1: 2; Actuals 2: 3; Actuals 3: 7; Actuals 4: 12 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.4.d.iii | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.4.d.iii | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.4.d.iii | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.4.d.iii | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | other | Actuals 1: 83; Actuals 2: 82; Actuals 3: 192; Actuals 4: 266; Actuals 1: 88; Actuals 2: 52; Actuals 3: 90; Actuals 4: 82; Actuals 1: 74; Actuals 2: 30; Actuals 3: 101; Actuals 4: 162 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.4.e.i | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.4.e.i | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.4.e.i | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.4.e.i | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | other | Actuals 1: 588; Actuals 2: 447; Actuals 3: 301; Actuals 4: 327; Actuals 1: 230; Actuals 2: 256; Actuals 3: 136; Actuals 4: 312; Actuals 1: 675; Actuals 2: 337; Actuals 3: 364; Actuals 4: 656 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.4.e.ii | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Drone | Actuals 1: 0; Actuals 2: 2; Actuals 3: 20; Actuals 4: 25; Actuals 1: 0; Actuals 2: 1; Actuals 3: 1; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.4.e.ii | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.4.e.ii | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.4.e.ii | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | other | Actuals 1: 4; Actuals 2: 3; Actuals 3: 2; Actuals 4: 0; Actuals 1: 4; Actuals 2: 4; Actuals 3: 3; Actuals 4: 0; Actuals 3: 1 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.4.e.iii | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
14. Grid condition findings from inspection | 14.t.4.e.iii | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.4.e.iii | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | SCE does not track this inspection type by this inspection method.
14. Grid condition findings from inspection | 14.t.4.e.iii | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | other | Actuals 1: 0; Actuals 2: 1; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 2; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of findings from these asset inspections
15. Grid condition fixes in response to inspection findings | 15.b.2.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.2.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.2.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.2.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | other | Actuals 1: 0; Actuals 2: 7; Actuals 3: 0; Actuals 4: 0; Actuals 1: 3; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.2.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Drone | Actuals 1: 73; Actuals 2: 25; Actuals 3: 21; Actuals 4: 5; Actuals 1: 15; Actuals 2: 52; Actuals 3: 32; Actuals 4: 4; Actuals 1: 51; Actuals 2: 73; Actuals 3: 17; Actuals 4: 3 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.2.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.2.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.2.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | other | Actuals 1: 0; Actuals 2: 2; Actuals 3: 4; Actuals 4: 10; Actuals 1: 36; Actuals 2: 13; Actuals 3: 2; Actuals 4: 2; Actuals 1: 10; Actuals 2: 10; Actuals 3: 6; Actuals 4: 2 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.2.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.2.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.2.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.2.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | other | Actuals 1: 1; Actuals 2: 4; Actuals 3: 1; Actuals 4: 6; Actuals 1: 1; Actuals 2: 0; Actuals 3: 2; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 1; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.2.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.2.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.2.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.2.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | other | Actuals 1: 0; Actuals 2: 2; Actuals 3: 1; Actuals 4: 1; Actuals 1: 3; Actuals 2: 3; Actuals 3: 0; Actuals 4: 1; Actuals 1: 1; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.2.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Drone | Actuals 1: 222; Actuals 2: 785; Actuals 3: 698; Actuals 4: 1219; Actuals 1: 504; Actuals 2: 663; Actuals 3: 688; Actuals 4: 267; Actuals 1: 870; Actuals 2: 680; Actuals 3: 276; Actuals 4: 288 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.2.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.2.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.2.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | other | Actuals 1: 2049; Actuals 2: 1172; Actuals 3: 682; Actuals 4: 1069; Actuals 1: 3726; Actuals 2: 2478; Actuals 3: 676; Actuals 4: 604; Actuals 1: 7226; Actuals 2: 3984; Actuals 3: 4282; Actuals 4: 2229 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.2.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.2.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.2.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.2.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | other | Actuals 1: 114; Actuals 2: 196; Actuals 3: 131; Actuals 4: 106; Actuals 1: 121; Actuals 2: 146; Actuals 3: 98; Actuals 4: 138; Actuals 1: 167; Actuals 2: 151; Actuals 3: 157; Actuals 4: 109 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.2.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.2.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.2.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.2.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | other | Actuals 1: 1; Actuals 2: 1; Actuals 3: 0; Actuals 4: 1; Actuals 1: 1; Actuals 2: 5; Actuals 3: 0; Actuals 4: 2; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.2.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 1; Actuals 1: 3; Actuals 2: 5; Actuals 3: 10; Actuals 4: 0; Actuals 1: 3; Actuals 2: 5; Actuals 3: 3; Actuals 4: 2 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.2.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.2.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.2.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | other | Actuals 1: 2579; Actuals 2: 4258; Actuals 3: 2373; Actuals 4: 2667; Actuals 1: 4564; Actuals 2: 3226; Actuals 3: 2087; Actuals 4: 1522; Actuals 1: 5742; Actuals 2: 4311; Actuals 3: 2191; Actuals 4: 1346 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.2.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.2.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.2.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.2.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | other | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 2; Actuals 2: 0; Actuals 3: 0; Actuals 4: 1 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.3.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.3.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.3.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.3.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | other | Actuals 1: 0; Actuals 2: 7; Actuals 3: 1; Actuals 4: 1; Actuals 1: 3; Actuals 2: 3; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.3.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Drone | Actuals 1: 75; Actuals 2: 32; Actuals 3: 40; Actuals 4: 11; Actuals 1: 4; Actuals 2: 92; Actuals 3: 43; Actuals 4: 7; Actuals 1: 58; Actuals 2: 96; Actuals 3: 33; Actuals 4: 21 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.3.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.3.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.3.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | other | Actuals 1: 2; Actuals 2: 2; Actuals 3: 1; Actuals 4: 50; Actuals 1: 22; Actuals 2: 9; Actuals 3: 3; Actuals 4: 0; Actuals 1: 11; Actuals 2: 18; Actuals 3: 5; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.3.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.3.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.3.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.3.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | other | Actuals 1: 1; Actuals 2: 2; Actuals 3: 4; Actuals 4: 1; Actuals 1: 5; Actuals 2: 2; Actuals 3: 1; Actuals 4: 2; Actuals 1: 1; Actuals 2: 0; Actuals 3: 2; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.3.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.3.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.3.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.3.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | other | Actuals 1: 1; Actuals 2: 2; Actuals 3: 1; Actuals 4: 1; Actuals 1: 5; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.3.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Drone | Actuals 1: 1319; Actuals 2: 2849; Actuals 3: 1484; Actuals 4: 1558; Actuals 1: 218; Actuals 2: 1852; Actuals 3: 1687; Actuals 4: 516; Actuals 1: 680; Actuals 2: 669; Actuals 3: 1421; Actuals 4: 652 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.3.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.3.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.3.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | other | Actuals 1: 1604; Actuals 2: 2327; Actuals 3: 2603; Actuals 4: 2784; Actuals 1: 4834; Actuals 2: 6364; Actuals 3: 1549; Actuals 4: 2004; Actuals 1: 4861; Actuals 2: 5596; Actuals 3: 11334; Actuals 4: 3457 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.3.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.3.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.3.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.3.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | other | Actuals 1: 284; Actuals 2: 363; Actuals 3: 269; Actuals 4: 148; Actuals 1: 157; Actuals 2: 522; Actuals 3: 417; Actuals 4: 328; Actuals 1: 218; Actuals 2: 162; Actuals 3: 226; Actuals 4: 181 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.3.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.3.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.3.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.3.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | other | Actuals 1: 0; Actuals 2: 1; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.3.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Drone | Actuals 1: 3; Actuals 2: 1; Actuals 3: 1; Actuals 4: 3; Actuals 1: 2; Actuals 2: 16; Actuals 3: 18; Actuals 4: 6; Actuals 1: 11; Actuals 2: 9; Actuals 3: 10; Actuals 4: 7 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.3.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.3.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.3.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | other | Actuals 1: 3712; Actuals 2: 6852; Actuals 3: 4894; Actuals 4: 4764; Actuals 1: 10175; Actuals 2: 6150; Actuals 3: 5349; Actuals 4: 3345; Actuals 1: 5063; Actuals 2: 6567; Actuals 3: 5259; Actuals 4: 2273 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.3.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.3.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.3.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.3.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | other | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.4.a.i | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.4.a.i | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.4.a.i | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.4.a.i | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | other | Actuals 1: 0; Actuals 2: 54; Actuals 3: 1; Actuals 4: 4; Actuals 1: 10; Actuals 2: 10; Actuals 3: 1; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.4.a.ii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Drone | Actuals 1: 4; Actuals 2: 4; Actuals 3: 4; Actuals 4: 1; Actuals 1: 0; Actuals 2: 3; Actuals 3: 0; Actuals 4: 0; Actuals 1: 2; Actuals 2: 1; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.4.a.ii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.4.a.ii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.4.a.ii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | other | Actuals 1: 0; Actuals 2: 45; Actuals 3: 115; Actuals 4: 201; Actuals 1: 43; Actuals 2: 127; Actuals 3: 169; Actuals 4: 159; Actuals 1: 34; Actuals 2: 40; Actuals 3: 60; Actuals 4: 78 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.4.a.iii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.4.a.iii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.4.a.iii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.4.a.iii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | other | Actuals 1: 11; Actuals 2: 27; Actuals 3: 24; Actuals 4: 19; Actuals 1: 16; Actuals 2: 32; Actuals 3: 20; Actuals 4: 12; Actuals 1: 12; Actuals 2: 24; Actuals 3: 24; Actuals 4: 13 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.4.b.i | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.4.b.i | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.4.b.i | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.4.b.i | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | other | Actuals 1: 13; Actuals 2: 8; Actuals 3: 9; Actuals 4: 87; Actuals 1: 5; Actuals 2: 163; Actuals 3: 55; Actuals 4: 86; Actuals 1: 39; Actuals 2: 37; Actuals 3: 11; Actuals 4: 22 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.4.b.ii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Drone | Actuals 1: 11; Actuals 2: 32; Actuals 3: 23; Actuals 4: 24; Actuals 1: 25; Actuals 2: 20; Actuals 3: 94; Actuals 4: 48; Actuals 1: 26; Actuals 2: 11; Actuals 3: 10; Actuals 4: 3 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.4.b.ii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.4.b.ii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.4.b.ii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | other | Actuals 1: 6137; Actuals 2: 3374; Actuals 3: 2358; Actuals 4: 2258; Actuals 1: 3180; Actuals 2: 6490; Actuals 3: 8584; Actuals 4: 6872; Actuals 1: 23774; Actuals 2: 9699; Actuals 3: 12670; Actuals 4: 17771 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.4.b.iii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.4.b.iii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.4.b.iii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.4.b.iii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | other | Actuals 1: 1264; Actuals 2: 1504; Actuals 3: 1229; Actuals 4: 638; Actuals 1: 1584; Actuals 2: 1278; Actuals 3: 1170; Actuals 4: 1089; Actuals 1: 1145; Actuals 2: 822; Actuals 3: 1412; Actuals 4: 1145 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.4.c.i | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.4.c.i | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.4.c.i | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.4.c.i | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | other | Actuals 1: 6; Actuals 2: 3; Actuals 3: 1; Actuals 4: 0; Actuals 1: 5; Actuals 2: 2; Actuals 3: 3; Actuals 4: 3; Actuals 1: 0; Actuals 2: 3; Actuals 3: 0; Actuals 4: 4 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.4.c.ii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.4.c.ii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.4.c.ii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.4.c.ii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | other | Actuals 1: 8900; Actuals 2: 7883; Actuals 3: 6821; Actuals 4: 7028; Actuals 1: 11792; Actuals 2: 10537; Actuals 3: 10678; Actuals 4: 12259; Actuals 1: 10692; Actuals 2: 11030; Actuals 3: 13534; Actuals 4: 11846 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.4.c.iii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.b.4.c.iii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.4.c.iii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.b.4.c.iii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | other | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 1; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.2.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.2.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.2.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.2.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | other | Actuals 1: 5; Actuals 2: 4; Actuals 3: 10; Actuals 4: 17; Actuals 1: 5; Actuals 2: 11; Actuals 3: 4; Actuals 4: 2; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.2.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Drone | Actuals 1: 3; Actuals 2: 9; Actuals 3: 19; Actuals 4: 22; Actuals 1: 8; Actuals 2: 16; Actuals 3: 7; Actuals 4: 0; Actuals 1: 6; Actuals 2: 4; Actuals 3: 1; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.2.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.2.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.2.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | other | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.2.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.2.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.2.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.2.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | other | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 1; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.2.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.2.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.2.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.2.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | other | Actuals 1: 113; Actuals 2: 214; Actuals 3: 204; Actuals 4: 226; Actuals 1: 225; Actuals 2: 605; Actuals 3: 234; Actuals 4: 77; Actuals 1: 183; Actuals 2: 225; Actuals 3: 121; Actuals 4: 88 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.2.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Drone | Actuals 1: 132; Actuals 2: 288; Actuals 3: 373; Actuals 4: 339; Actuals 1: 127; Actuals 2: 176; Actuals 3: 273; Actuals 4: 299; Actuals 1: 128; Actuals 2: 95; Actuals 3: 46; Actuals 4: 48 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.2.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.2.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.2.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | other | Actuals 1: 934; Actuals 2: 564; Actuals 3: 401; Actuals 4: 622; Actuals 1: 457; Actuals 2: 1015; Actuals 3: 309; Actuals 4: 46; Actuals 1: 238; Actuals 2: 226; Actuals 3: 138; Actuals 4: 80 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.2.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.2.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.2.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.2.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | other | Actuals 1: 57; Actuals 2: 161; Actuals 3: 50; Actuals 4: 35; Actuals 1: 86; Actuals 2: 30; Actuals 3: 20; Actuals 4: 19; Actuals 1: 2; Actuals 2: 9; Actuals 3: 15; Actuals 4: 4 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.2.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.2.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.2.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.2.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | other | Actuals 1: 68; Actuals 2: 140; Actuals 3: 141; Actuals 4: 90; Actuals 1: 199; Actuals 2: 158; Actuals 3: 54; Actuals 4: 23; Actuals 1: 53; Actuals 2: 45; Actuals 3: 88; Actuals 4: 87 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.2.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Drone | Actuals 1: 1; Actuals 2: 0; Actuals 3: 0; Actuals 4: 11; Actuals 1: 5; Actuals 2: 31; Actuals 3: 109; Actuals 4: 18; Actuals 1: 22; Actuals 2: 5; Actuals 3: 15; Actuals 4: 14 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.2.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.2.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.2.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | other | Actuals 1: 31; Actuals 2: 23; Actuals 3: 484; Actuals 4: 13; Actuals 1: 230; Actuals 2: 60; Actuals 3: 4; Actuals 4: 4; Actuals 1: 26; Actuals 2: 34; Actuals 3: 26; Actuals 4: 41 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.2.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.2.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.2.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.2.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | other | Actuals 1: 1; Actuals 2: 2; Actuals 3: 9; Actuals 4: 0; Actuals 1: 1; Actuals 2: 6; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.3.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.3.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.3.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.3.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | other | Actuals 1: 6; Actuals 2: 2; Actuals 3: 6; Actuals 4: 8; Actuals 1: 6; Actuals 2: 6; Actuals 3: 16; Actuals 4: 2; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.3.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Drone | Actuals 1: 4; Actuals 2: 6; Actuals 3: 15; Actuals 4: 10; Actuals 1: 9; Actuals 2: 22; Actuals 3: 11; Actuals 4: 1; Actuals 1: 2; Actuals 2: 4; Actuals 3: 1; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.3.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.3.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.3.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | other | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 1; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.3.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.3.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Aerial | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.3.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | LiDAR | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.3.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | other | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.3.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.3.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.3.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.3.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | other | Actuals 1: 54; Actuals 2: 178; Actuals 3: 445; Actuals 4: 342; Actuals 1: 169; Actuals 2: 333; Actuals 3: 171; Actuals 4: 39; Actuals 1: 154; Actuals 2: 96; Actuals 3: 121; Actuals 4: 107 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.3.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Drone | Actuals 1: 200; Actuals 2: 484; Actuals 3: 202; Actuals 4: 265; Actuals 1: 87; Actuals 2: 147; Actuals 3: 164; Actuals 4: 130; Actuals 1: 62; Actuals 2: 101; Actuals 3: 77; Actuals 4: 101 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.3.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.3.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.3.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | other | Actuals 1: 326; Actuals 2: 269; Actuals 3: 1418; Actuals 4: 756; Actuals 1: 217; Actuals 2: 622; Actuals 3: 165; Actuals 4: 146; Actuals 1: 209; Actuals 2: 189; Actuals 3: 188; Actuals 4: 122 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.3.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.3.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.3.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.3.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | other | Actuals 1: 47; Actuals 2: 22; Actuals 3: 11; Actuals 4: 15; Actuals 1: 6; Actuals 2: 7; Actuals 3: 7; Actuals 4: 10; Actuals 1: 3; Actuals 2: 0; Actuals 3: 4; Actuals 4: 6 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.3.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.3.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.3.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.3.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | other | Actuals 1: 56; Actuals 2: 116; Actuals 3: 93; Actuals 4: 63; Actuals 1: 81; Actuals 2: 77; Actuals 3: 43; Actuals 4: 28; Actuals 1: 44; Actuals 2: 54; Actuals 3: 94; Actuals 4: 75 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.3.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 3; Actuals 4: 6; Actuals 1: 2; Actuals 2: 13; Actuals 3: 64; Actuals 4: 14; Actuals 1: 15; Actuals 2: 16; Actuals 3: 32; Actuals 4: 12 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.3.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.3.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.3.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | other | Actuals 1: 12; Actuals 2: 51; Actuals 3: 15; Actuals 4: 27; Actuals 1: 42; Actuals 2: 64; Actuals 3: 4; Actuals 4: 7; Actuals 1: 23; Actuals 2: 49; Actuals 3: 43; Actuals 4: 48 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.3.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.3.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.3.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.3.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | other | Actuals 1: 6; Actuals 2: 0; Actuals 3: 0; Actuals 4: 3; Actuals 1: 2; Actuals 2: 7; Actuals 3: 0; Actuals 4: 1; Actuals 1: 1; Actuals 2: 0; Actuals 3: 1; Actuals 4: 1 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.4.a.i | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.4.a.i | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.4.a.i | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.4.a.i | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | other | Actuals 1: 39; Actuals 2: 26; Actuals 3: 48; Actuals 4: 35; Actuals 1: 38; Actuals 2: 49; Actuals 3: 28; Actuals 4: 10; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.4.a.ii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Drone | Actuals 1: 1; Actuals 2: 2; Actuals 3: 3; Actuals 4: 7; Actuals 1: 1; Actuals 2: 0; Actuals 3: 1; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.4.a.ii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.4.a.ii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.4.a.ii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | other | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.4.a.iii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.4.a.iii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.4.a.iii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.4.a.iii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | other | Actuals 1: 0; Actuals 2: 0; Actuals 3: 1; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 1; Actuals 1: 1; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.4.b.i | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.4.b.i | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.4.b.i | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.4.b.i | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | other | Actuals 1: 981; Actuals 2: 839; Actuals 3: 738; Actuals 4: 825; Actuals 1: 1083; Actuals 2: 933; Actuals 3: 674; Actuals 4: 527; Actuals 1: 711; Actuals 2: 715; Actuals 3: 733; Actuals 4: 668 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.4.b.ii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Drone | Actuals 1: 60; Actuals 2: 39; Actuals 3: 52; Actuals 4: 32; Actuals 1: 25; Actuals 2: 12; Actuals 3: 68; Actuals 4: 124; Actuals 1: 40; Actuals 2: 14; Actuals 3: 19; Actuals 4: 13 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.4.b.ii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.4.b.ii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.4.b.ii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | other | Actuals 1: 124; Actuals 2: 52; Actuals 3: 57; Actuals 4: 81; Actuals 1: 145; Actuals 2: 17; Actuals 3: 14; Actuals 4: 35; Actuals 1: 144; Actuals 2: 121; Actuals 3: 90; Actuals 4: 70 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.4.b.iii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.4.b.iii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.4.b.iii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.4.b.iii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | other | Actuals 1: 157; Actuals 2: 134; Actuals 3: 158; Actuals 4: 156; Actuals 1: 119; Actuals 2: 96; Actuals 3: 129; Actuals 4: 182; Actuals 1: 125; Actuals 2: 80; Actuals 3: 100; Actuals 4: 75 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.4.c.i | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.4.c.i | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.4.c.i | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.4.c.i | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | other | Actuals 1: 732; Actuals 2: 657; Actuals 3: 525; Actuals 4: 636; Actuals 1: 428; Actuals 2: 410; Actuals 3: 380; Actuals 4: 397; Actuals 1: 554; Actuals 2: 445; Actuals 3: 605; Actuals 4: 801 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.4.c.ii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 1; Actuals 3: 9; Actuals 4: 23; Actuals 1: 0; Actuals 2: 0; Actuals 3: 2; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.4.c.ii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.4.c.ii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.4.c.ii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | other | Actuals 1: 22; Actuals 2: 4; Actuals 3: 55; Actuals 4: 5; Actuals 1: 15; Actuals 2: 3; Actuals 3: 0; Actuals 4: 1; Actuals 1: 14; Actuals 2: 0; Actuals 3: 3; Actuals 4: 3 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.4.c.iii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Drone | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
15. Grid condition fixes in response to inspection findings | 15.t.4.c.iii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.4.c.iii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | SCE does not track this inspection type by this inspection method
15. Grid condition fixes in response to inspection findings | 15.t.4.c.iii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | other | Actuals 1: 0; Actuals 2: 0; Actuals 3: 8; Actuals 4: 0; Actuals 1: 1; Actuals 2: 3; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of asset inspection findings which have been fixed
16. Vegetation clearance findings from inspection | 16.d.2.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Distribution | Routine | Drone | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.d.2.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Distribution | Routine | Aerial | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.d.2.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Distribution | Routine | LiDAR | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.d.2.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Distribution | Routine | other | Actuals 1: 9248; Actuals 2: 39131; Actuals 3: 26924; Actuals 4: 24625; Actuals 1: 24354; Actuals 2: 31060; Actuals 3: 24192; Actuals 4: 17741; Actuals 1: 22774; Actuals 2: 28638; Actuals 3: 25547; Actuals 4: 18417 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
16. Vegetation clearance findings from inspection | 16.d.2.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Distribution | Non-Routine | Drone | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.d.2.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Distribution | Non-Routine | Aerial | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.d.2.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Distribution | Non-Routine | LiDAR | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.d.2.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Distribution | Non-Routine | other | Actuals 1: 6189; Actuals 2: 5941; Actuals 3: 5106; Actuals 4: 6619; Actuals 1: 3067; Actuals 2: 10994; Actuals 3: 12823; Actuals 4: 5474; Actuals 1: 3438; Actuals 2: 2613; Actuals 3: 985; Actuals 4: 591 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non0routine inspection.
16. Vegetation clearance findings from inspection | 16.d.2.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Distribution | Non-Routine | Drone | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.d.2.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Distribution | Non-Routine | Aerial | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.d.2.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Distribution | Non-Routine | LiDAR | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.d.2.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Distribution | Non-Routine | other | Actuals 1: 3; Actuals 2: 0; Actuals 3: 0; Actuals 4: 1; Actuals 1: 3; Actuals 2: 4; Actuals 3: 18; Actuals 4: 7; Actuals 1: 7; Actuals 2: 14; Actuals 3: 5; Actuals 4: 6 |  |  |  | # of trees found to be non0compliant with GO 95, Rule 35, and PRC 4293 at the time of non0routine inspection.
16. Vegetation clearance findings from inspection | 16.d.2.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Distribution | Routine | Drone | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.d.2.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Distribution | Routine | Aerial | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.d.2.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Distribution | Routine | LiDAR | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.d.2.b.ii | Number of trees inspected where at least some vegetation was found in non0compliant condition | N/A | N/A | HFTD Tier 2 | Distribution | Routine | other | Actuals 1: 341; Actuals 2: 1571; Actuals 3: 1996; Actuals 4: 2674; Actuals 1: 1552; Actuals 2: 1334; Actuals 3: 1160; Actuals 4: 1070; Actuals 1: 993; Actuals 2: 1127; Actuals 3: 1690; Actuals 4: 1136 |  |  |  | # of trees found to be non0compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
16. Vegetation clearance findings from inspection | 16.d.3.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Distribution | Routine | Drone | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.d.3.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Distribution | Routine | Aerial | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.d.3.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Distribution | Routine | LiDAR | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.d.3.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Distribution | Routine | other | Actuals 1: 23821; Actuals 2: 65574; Actuals 3: 77730; Actuals 4: 39735; Actuals 1: 50893; Actuals 2: 72294; Actuals 3: 64902; Actuals 4: 32110; Actuals 1: 56396; Actuals 2: 70743; Actuals 3: 64082; Actuals 4: 36052 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
16. Vegetation clearance findings from inspection | 16.d.3.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Distribution | Non-Routine | Drone | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.d.3.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Distribution | Non-Routine | Aerial | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.d.3.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Distribution | Non-Routine | LiDAR | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.d.3.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Distribution | Non-Routine | other | Actuals 1: 22806; Actuals 2: 19630; Actuals 3: 18832; Actuals 4: 18990; Actuals 1: 10157; Actuals 2: 40778; Actuals 3: 31813; Actuals 4: 16428; Actuals 1: 10021; Actuals 2: 9470; Actuals 3: 2493; Actuals 4: 1883 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non0routine inspection.
16. Vegetation clearance findings from inspection | 16.d.3.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Distribution | Non-Routine | Drone | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.d.3.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Distribution | Non-Routine | Aerial | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.d.3.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Distribution | Non-Routine | LiDAR | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.d.3.b.i | Number of trees inspected where at least some vegetation was found in non0compliant condition | N/A | N/A | HFTD Tier 3 | Distribution | Non-Routine | other | Actuals 1: 7; Actuals 2: 5; Actuals 3: 1; Actuals 4: 14; Actuals 1: 9; Actuals 2: 11; Actuals 3: 9; Actuals 4: 18; Actuals 1: 7; Actuals 2: 11; Actuals 3: 18; Actuals 4: 16 |  |  |  | # of trees found to be non0compliant with GO 95, Rule 35, and PRC 4293 at the time of non0routine inspection.
16. Vegetation clearance findings from inspection | 16.d.3.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Distribution | Routine | Drone | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.d.3.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Distribution | Routine | Aerial | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.d.3.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Distribution | Routine | LiDAR | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.d.3.b.ii | Number of trees inspected where at least some vegetation was found in non0compliant condition | N/A | N/A | HFTD Tier 3 | Distribution | Routine | other | Actuals 1: 766; Actuals 2: 4937; Actuals 3: 5441; Actuals 4: 2657; Actuals 1: 3141; Actuals 2: 3210; Actuals 3: 2810; Actuals 4: 1659; Actuals 1: 2271; Actuals 2: 2507; Actuals 3: 3539; Actuals 4: 2546 |  |  |  | # of trees found to be non0compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
16. Vegetation clearance findings from inspection | 16.d.4.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Distribution | Routine | Drone | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.d.4.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Distribution | Routine | Aerial | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.d.4.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Distribution | Routine | LiDAR | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.d.4.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Distribution | Routine | other | Actuals 1: 40816; Actuals 2: 72267; Actuals 3: 102371; Actuals 4: 118389; Actuals 1: 109839; Actuals 2: 85727; Actuals 3: 98760; Actuals 4: 109585; Actuals 1: 105204; Actuals 2: 92748; Actuals 3: 97861; Actuals 4: 85980 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
16. Vegetation clearance findings from inspection | 16.d.4.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Distribution | Non-Routine | Drone | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.d.4.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Distribution | Non-Routine | Aerial | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.d.4.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Distribution | Non-Routine | LiDAR | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.d.4.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Distribution | Non-Routine | other | Actuals 1: 2635; Actuals 2: 2601; Actuals 3: 2885; Actuals 4: 3000; Actuals 1: 1433; Actuals 2: 5776; Actuals 3: 5531; Actuals 4: 5037; Actuals 1: 2496; Actuals 2: 4313; Actuals 3: 3831; Actuals 4: 3717 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection.
16. Vegetation clearance findings from inspection | 16.d.4.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Distribution | Non-Routine | Drone | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.d.4.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Distribution | Non-Routine | Aerial | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.d.4.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Distribution | Non-Routine | LiDAR | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.d.4.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Distribution | Non-Routine | other | Actuals 1: 5; Actuals 2: 5; Actuals 3: 4; Actuals 4: 24; Actuals 1: 19; Actuals 2: 27; Actuals 3: 8; Actuals 4: 12; Actuals 1: 6; Actuals 2: 3; Actuals 3: 5; Actuals 4: 11 |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection.
16. Vegetation clearance findings from inspection | 16.d.4.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Distribution | Routine | Drone | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.d.4.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Distribution | Routine | Aerial | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.d.4.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Distribution | Routine | LiDAR | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.d.4.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Distribution | Routine | other | Actuals 1: 2153; Actuals 2: 4921; Actuals 3: 9962; Actuals 4: 11208; Actuals 1: 7379; Actuals 2: 3777; Actuals 3: 21; Actuals 4: 3; Actuals 1: 277; Actuals 2: 9; Actuals 3: 202; Actuals 4: 38 |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
16. Vegetation clearance findings from inspection | 16.t.2.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Transmission | Routine | Drone | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.t.2.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Transmission | Routine | Aerial | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.t.2.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Transmission | Routine | LiDAR | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.t.2.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Transmission | Routine | other | Actuals 1: 2495; Actuals 2: 12011; Actuals 3: 20185; Actuals 4: 2069; Actuals 1: 5727; Actuals 2: 10931; Actuals 3: 3841; Actuals 4: 3436; Actuals 1: 936; Actuals 2: 6766; Actuals 3: 1246; Actuals 4: 1854 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
16. Vegetation clearance findings from inspection | 16.t.2.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Transmission | Non-Routine | Drone | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.t.2.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Transmission | Non-Routine | Aerial | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.t.2.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Transmission | Non-Routine | LiDAR | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.t.2.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Transmission | Non-Routine | other | Actuals 1: 96; Actuals 2: 125; Actuals 3: 27; Actuals 4: 12; Actuals 1: 7; Actuals 2: 103; Actuals 3: 126; Actuals 4: 47; Actuals 1: 14; Actuals 2: 7; Actuals 3: 2; Actuals 4: 4 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non0routine inspection.
16. Vegetation clearance findings from inspection | 16.t.2.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Transmission | Non-Routine | Drone | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.t.2.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Transmission | Non-Routine | Aerial | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.t.2.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Transmission | Non-Routine | LiDAR | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.t.2.b.i | Number of trees inspected where at least some vegetation was found in non0compliant condition | N/A | N/A | HFTD Tier 2 | Transmission | Non-Routine | other | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of trees found to be non0compliant with GO 95, Rule 35, and PRC 4293 at the time of non0routine inspection.
16. Vegetation clearance findings from inspection | 16.t.2.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Transmission | Routine | Drone | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.t.2.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Transmission | Routine | Aerial | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.t.2.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Transmission | Routine | LiDAR | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.t.2.b.ii | Number of trees inspected where at least some vegetation was found in non0compliant condition | N/A | N/A | HFTD Tier 2 | Transmission | Routine | other | Actuals 1: 4; Actuals 2: 1634; Actuals 3: 51; Actuals 4: 58; Actuals 1: 54; Actuals 2: 18; Actuals 3: 18; Actuals 4: 187; Actuals 1: 59; Actuals 2: 214; Actuals 3: 136; Actuals 4: 12 |  |  |  | # of trees found to be non0compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
16. Vegetation clearance findings from inspection | 16.t.3.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Transmission | Routine | Drone | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.t.3.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Transmission | Routine | Aerial | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.t.3.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Transmission | Routine | LiDAR | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.t.3.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Transmission | Routine | other | Actuals 1: 2644; Actuals 2: 13146; Actuals 3: 55134; Actuals 4: 3521; Actuals 1: 5137; Actuals 2: 2634; Actuals 3: 3434; Actuals 4: 2846; Actuals 1: 2666; Actuals 2: 4944; Actuals 3: 583; Actuals 4: 728 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
16. Vegetation clearance findings from inspection | 16.t.3.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Transmission | Non-Routine | Drone | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.t.3.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Transmission | Non-Routine | Aerial | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.t.3.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Transmission | Non-Routine | LiDAR | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.t.3.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Transmission | Non-Routine | other | Actuals 1: 103; Actuals 2: 183; Actuals 3: 8; Actuals 4: 20; Actuals 1: 16; Actuals 2: 117; Actuals 3: 42; Actuals 4: 59; Actuals 1: 9; Actuals 2: 17; Actuals 3: 5; Actuals 4: 11 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non0routine inspection.
16. Vegetation clearance findings from inspection | 16.t.3.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Transmission | Non-Routine | Drone | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.t.3.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Transmission | Non-Routine | Aerial | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.t.3.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Transmission | Non-Routine | LiDAR | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.t.3.b.i | Number of trees inspected where at least some vegetation was found in non0compliant condition | N/A | N/A | HFTD Tier 3 | Transmission | Non-Routine | other | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of trees found to be non0compliant with GO 95, Rule 35, and PRC 4293 at the time of non0routine inspection.
16. Vegetation clearance findings from inspection | 16.t.3.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Transmission | Routine | Drone | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.t.3.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Transmission | Routine | Aerial | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.t.3.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Transmission | Routine | LiDAR | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.t.3.b.ii | Number of trees inspected where at least some vegetation was found in non0compliant condition | N/A | N/A | HFTD Tier 3 | Transmission | Routine | other | Actuals 1: 74; Actuals 2: 70; Actuals 3: 51; Actuals 4: 275; Actuals 1: 186; Actuals 2: 29; Actuals 3: 61; Actuals 4: 66; Actuals 1: 260; Actuals 2: 114; Actuals 3: 8; Actuals 4: 1 |  |  |  | # of trees found to be non0compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
16. Vegetation clearance findings from inspection | 16.t.4.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Transmission | Routine | Drone | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.t.4.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Transmission | Routine | Aerial | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.t.4.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Transmission | Routine | LiDAR | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.t.4.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Transmission | Routine | other | Actuals 1: 4171; Actuals 2: 7806; Actuals 3: 6451; Actuals 4: 4747; Actuals 1: 6007; Actuals 2: 4316; Actuals 3: 4941; Actuals 4: 2158; Actuals 1: 1879; Actuals 2: 5212; Actuals 3: 3201; Actuals 4: 2157 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
16. Vegetation clearance findings from inspection | 16.t.4.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Transmission | Non-Routine | Drone | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.t.4.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Transmission | Non-Routine | Aerial | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.t.4.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Transmission | Non-Routine | LiDAR | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.t.4.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Transmission | Non-Routine | other | Actuals 1: 51; Actuals 2: 31; Actuals 3: 40; Actuals 4: 20; Actuals 1: 36; Actuals 2: 53; Actuals 3: 212; Actuals 4: 34; Actuals 1: 116; Actuals 2: 325; Actuals 3: 57; Actuals 4: 75 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection.
16. Vegetation clearance findings from inspection | 16.t.4.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Transmission | Non-Routine | Drone | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.t.4.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Transmission | Non-Routine | Aerial | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.t.4.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Transmission | Non-Routine | LiDAR | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.t.4.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Transmission | Non-Routine | other | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 2; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0 |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection.
16. Vegetation clearance findings from inspection | 16.t.4.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Transmission | Routine | Drone | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.t.4.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Transmission | Routine | Aerial | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.t.4.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Transmission | Routine | LiDAR | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | SCE does not track Veg inspections using Drone, Aerial, or LiDAR.
16. Vegetation clearance findings from inspection | 16.t.4.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Transmission | Routine | other | Actuals 1: 57; Actuals 2: 273; Actuals 3: 164; Actuals 4: 76; Actuals 1: 70; Actuals 2: 31; Actuals 3: 2 |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
17. Community outreach metrics | 17.a. | % of customers notified of evacuation in evacuation zone of a utility-ignited wildfire | N/A | N/A | N/A | N/A | N/A | N/A | [27 empty] | Percentage of customers notified of evacuation | SCE has no jurisdiction over evacuation orders. SCE diligently requested and followed up with local governments and law enforcement, and was only able to obtain information from one county. Even then, the information provided included high-level estimations of evacuation counts estimated by the local government and law enforcement entity for a limited amount of fires. Because of this, SCE is unable to obtain the requested data, analyze it, and report on evacuation related requirements in this table. SCE anticipates this to be a recurring challenge going forward. | SCE does not track this metric.

## Table 3
Utility | Southern California Edison
Table No. | 3
Date Modified | 2023-02-01
[5 empty] | Actual | [7 empty] | Note: These columns are placeholders for future QR submissions. | [7 empty] | Projected
Table 3: List and description of additional metrics |  |  |  |  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric | Definition | Purpose | Assumptions made to connect metric to purpose | Third-party validation (if any) | 2022 | 2022 | 2022 | 2022 | 2023 | 2023 | 2023 | 2023 | 2024 | 2024 | 2024 | 2024 | 2025 | 2025 | 2025 | 2025 | 2023 | 2024 | 2025 | Unit(s) | Comments | Blank Meaning
1. Number of CPUC reportable ignitions in HFRA | Count of the number of CPUC reportable ignitions in HFRA | To measure changes in rate of ignitions between years | Factors outside of SCE's control (e.g., wind, live fuel moisture) have a significant effect on CPUC reportable ignition counts in HFRA. | Annual submission of CPUC reportable ignition totals to CPUC | Actual 1: 8; Actual 2: 16; Actual 3: 12; Actual 4: 4 | 38.9808 | 37.844 | 37.0722
2. Number of wire downs in HFRA | Count of the number of wire downs in HFRA | To measure changes in rate of fault events which are a pre-cursor both ignition and safety events | Number of wire down incidents in HFRA based on cause. These metrics may help to provide insight on controllable and uncontrollable risks or help plan future activities to focus on a particular type of fault or outage that may be of wildfire risk. | Deep-dive audits of select portions of utility grid | Actual 1: 92; Actual 2: 65; Actual 3: 76; Actual 4: 83 | 360.5342 | 360.1761 | 360.5014
3. Number of outages in HFRA | Count of the number of outages in HFRA | To measure changes in rate of wire down events which are a pre-cursor both ignition and safety events | Number of faults in HFRA based on cause. These metrics may help to provide insight on controllable and uncontrollable risks or help plan future activities to focus on a particular type of fault or outage that may be of wildfire risk. | Deep-dive audits of select portions of utility grid | Actual 1: 460; Actual 2: 680; Actual 3: 739; Actual 4: 525 | 2017.7963 | 1945.887 | 1892.4631
4. # of asset management ignition risk-related work orders that are past due (excluding GO95 exceptions) | Count of the total past due T&D ignition risk work orders, excluding GO95 exceptions | To meaure the past due asset-related work orders that have ignition risk and are not subject to GO95 exceptions | This metric will help track past due work order that are related to wildfire risk mitigation and that are largely within the utility's control for addressing. |  | Actual 1: 4029; Actual 2: 3723; Actual 3: 4351; Actual 4: 4688 | 4198 | 4198 | 4198
5. Number of Tree-Caused Circuit Interruptions (TCCIs) in HFRA | Count of TCCIs in HFRA | To measure trends in how vegetation is causing risk events when contacting overhead circuitry in HFRA | Vegetation that comes into contact with energized circuits can cause a circuit interruption (e.g., fault), however there may be cases with vegetation comes into contact with SCE infrastructure and no fault occurs. |  | Actual 1: 17; Actual 2: 11; Actual 3: 8; Actual 4: 24 | 57 | 54.15 | 51.4425 |  | The number of TCCIs exclude anything that was human caused, no cause/not tree related, and uncategorized. There are also 11 pending review TCCIs that is included in the Q4 (Depending on the result of review Q4 number might change).Projections are an estimate only and actual performance is dependent on weather and other factors.
6. Number of trees inspected where at least some vegetation was found in a non-compliant condition in HFRA | Count of instances in HFRA where vegetation found in non-compliant condition through Routine Line Clearing programs | To meaure the extent to which vegetation exists in non-compliant condition | Routine Line Clearing activities will identify instances in which vegetation exists in a non-compliant condition |  | Actual 1: 3583; Actual 2: 3962; Actual 3: 5373; Actual 4: 3695 | 15782.35 | 14993.2325 | 14243.5709 |  | Projections are an estimate only and actual performance is dependent on weather and other factors.
7. Frequency of PSPS events (total) | Count of PSPS events in which de-energization has occurred | To measure trends in how many de-energization events occur each year | Metric does not account for the normalization of weather, fuel conditions, etc., year over year. Actual performance in each year will be driven by weather and fuel conditions experienced in those years and may vary from prior year and future year projected figures. | CPUC compliance reporting (e.g., PSPS Post-Event Reports, Post Season Reports) | Actual 1: 0; Actual 2: 0; Actual 3: 1; Actual 4: 2 | 6 | 6 | 6 |  | SCE uses a 2020-2022 PSPS event average to forecast 2023-2025 events. SCE does not forecast a reduction in events from the 2020-2022 average as overall circuit scope reduction may not reduce event count
8. Scope of PSPS events (total) | Count of circuit de-energized | To meaure trends in how may circuits are de-energized due to PSPS events | Metric does not account for the normalization of weather, fuel conditions, etc., year over year. Actual performance in each year will be driven by weather and fuel conditions experienced in those years and may vary from prior year and future year projected figures. | CPUC compliance reporting (e.g., PSPS Post-Event Reports, Post Season Reports) | Actual 1: 0; Actual 2: 0; Actual 3: 2; Actual 4: 11 | 225 | 212 | 199 |  | Forecast reductions are derived from applying SCE's 2023 reduction forecast to 2020-2022 averages across each future year.
9. Duration of PSPS (total) | Customer hours de-energized due to PSPS | To measure trends in the amount of customer hours de-energized due to PSPS | Metric does not account for the normalization of weather, fuel conditions, etc., year over year. Actual performance in each year will be driven by weather and fuel conditions experienced in those years and may vary from prior year and future year projected figures. | CPUC compliance reporting (e.g., PSPS Post-Event Reports, Post Season Reports) | Actual 1: 0; Actual 2: 0; Actual 3: 5273; Actual 4: 134925 | 2516572 | 2290080 | 2083972 |  | Forecast reductions are derived from applying SCE's 2023 reduction forecast to 2020-2022 averages across each future year.
10. # of customers impacted by PSPS | Count of customers de-enrgized due to PSPS | To measure trends in the number of customers de-energized due to PSPS | Metric does not account for the normalization of weather, fuel conditions, etc., year over year. Actual performance in each year will be driven by weather and fuel conditions experienced in those years and may vary from prior year and future year projected figures. | CPUC compliance reporting (e.g., PSPS Post-Event Reports, Post Season Reports) | Actual 1: 0; Actual 2: 0; Actual 3: 209; Actual 4: 15568 | 126361 | 107408 | 91297 |  | Forecast reductions are derived from applying SCE's 2023 reduction forecast to 2020-2022 averages across each future year.
11a. Customer recall of SCE wildfire and preparedness communications - System Wide | The percentage of surveyed customers across SCE's service area who responded that they recalled communications from SCE about the threat of wildfire and how they can prepare for them. | To help measure the effectiveness of its community outreach and engagement activities by measuring customer awareness of SCE’s wildfire messaging and customer wildfire and PSPS programs and services. | Results can be impacted by volume of PSPS events experienced per year, level of marketing and outreach to customers, severity of fire season, and other factors. | In-Language Wildfire Mitigation / PSPS Communications Effectiveness Survey | Actual 1: 0; Actual 2: 0; Actual 3: 46; Actual 4: 48 | 48 | 48 | 48 |  | The survey that generates these results is performed twice annually, once once toward the start of Q3 and once toward the end of Q4. Therefore, figures are not provided for Q1 or Q2.
11b. Customer recall of SCE wildfire and preparedness communications - HFRA only | The percentage of surveyed customers across SCE's HFRA who responded that they recalled communications from SCE about the threat of wildfire and how they can prepare for them. | To help measure the effectiveness of its community outreach and engagement activities by measuring customer awareness of SCE’s wildfire messaging and customer wildfire and PSPS programs and services. | Results can be impacted by volume of PSPS events experienced per year, level of marketing and outreach to customers, severity of fire season, and other factors. | In-Language Wildfire Mitigation / PSPS Communications Effectiveness Survey | Actual 1: 0; Actual 2: 0; Actual 3: 52; Actual 4: 56 | 56 | 56 | 56 |  | The survey that generates these results is performed twice annually, once once toward the start of Q3 and once toward the end of Q4. Therefore, figures are not provided for Q1 or Q2.

## Table 4
Utility | Southern California Edison
Table No. | 4
Date Modified | 2023-02-01
Note: These columns are placeholders for future QR submissions.
Table 4: Weather patterns |  |  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Metric name | 2022 | 2022 | 2022 | 2022 | 2023 | 2023 | 2023 | 2023 | 2024 | 2024 | 2024 | 2024 | 2025 | 2025 | 2025 | 2025 | Unit(s) | Comments | Blank Meaning
1. Red flag warning only overhead circuit mile days | 1.a. | Red Flag Warning Only overhead circuit mile days - HFTD tier 2 | 1: 0; 2: 515; 3: 2354; 4: 22403 | Sum of overhead circuit miles of utility grid subject to red flag warning each day within a given time period, calculated as the number of overhead circuit miles that were under an RFW multiplied by the number of days those circuit miles were under said RFW. For example, if 100 overhead circuit miles were under an RFW for 1 day, and 10 of those miles were under RFW for an additional day, then the total RFW OH circuit mile days would be 110.
1. Red flag warning only overhead circuit mile days | 1.b. | Red Flag Warning Only overhead circuit mile days - HFTD tier 3 | 1: 0; 2: 74; 3: 10607; 4: 84896 | Red flag warning overhead circuit mile days, see above for definition
1. Red flag warning only overhead circuit mile days | 1.c. | Red Flag Warning Only overhead circuit mile days - non-HFTD | 1: 0; 2: 8004; 3: 88; 4: 36015 | Red flag warning overhead circuit mile days, see above for definition
2. Wind condition overhead circuit mile days | 2.a. | High Wind Warning Only overhead circuit mile days - HFTD tier 2 | 1: 12842; 2: 4598; 3: 630; 4: 6944 | Sum of overhead circuit miles of utility grid subject to high wind warnings (HWW, as defined by the National Weather Service) each day within a given time period, calculated as the number of overhead circuit miles that were under an HWW multiplied by the number of days those miles were under said HWW. For example, if 100 overhead circuit miles were under an HWW for 1 day, and 10 of those miles were under HWW for an additional day, then the total HWW OH circuit mile days would be 110.
2. Wind condition overhead circuit mile days | 2.b. | High Wind Warning Only overhead circuit mile days - HFTD tier 3 | 1: 43734; 2: 11753; 3: 571; 4: 24772 | High wind warning overhead circuit mile days, see above for definition
2. Wind condition overhead circuit mile days | 2.c. | High Wind Warning Only overhead circuit mile days - non-HFTD | 1: 24529; 2: 13161; 3: 2017; 4: 22641 | High wind warning overhead circuit mile days, see above for definition
3. Wind condition and Red flag warning overhead circuit mile days | 3.a. | High Wind Warning and Red Flag Warning overhead circuit mile days - HFTD tier 2 | 1: 0; 2: 223; 3: 0; 4: 1932 | Sum of overhead circuit miles of utility grid subject to concurrent red flag warning and a high wind warning each day within a given time period, calculated as the number of overhead circuit miles that were under an RFW and HWW multiplied by the number of days those circuit miles were under said RFW and HWW. For example, if 100 overhead circuit miles were under an RFW and HWW for 1 day, and 10 of those miles were under RFW and HWW for an additional day, then the total RFW and HWW OH circuit mile days would be 110.
3. Wind condition and Red flag warning overhead circuit mile days | 3.b. | High Wind Warning and Red Flag Warning overhead circuit mile days - HFTD tier 3 | 1: 0; 2: 0; 3: 0; 4: 16434 | High wind warning and red flag warning overhead circuit mile days, see above for definition
3. Wind condition and Red flag warning overhead circuit mile days | 3.c. | High Wind Warning and Red Flag Warning overhead circuit mile days - non-HFTD | 1: 0; 2: 3384; 3: 0; 4: 2321 | High wind warning and red flag warning overhead circuit mile days, see above for definition
4. Fire potential index overhead circuit mile days | 4.a. | Fire potential index circuit mile days - HFTD tier 2 | 1: 135; 2: 3338; 3: 37187; 4: 6284 | Sum of overhead circuit miles of utility grid subject to high fire potential index (FPI, as defined by the utility in its WMP) each day within a given time period, calculated as the number of overhead circuit miles that were under a high FPI multiplied by the number of days those miles were under said FPI. For example, if 100 overhead circuit miles were under a high FPI for 1 day, and 10 of those miles were under a high FPI for an additional day, then the total FPI OH circuit mile days would be 110.
4. Fire potential index overhead circuit mile days | 4.b. | Fire potential index circuit mile days - HFTD tier 3 | 1: 46; 2: 533; 3: 14217; 4: 6533 | Fire potential index overhead circuit mile days, see above for definition
4. Fire potential index overhead circuit mile days | 4.c. | Fire potential index circuit mile days - non-HFTD | 1: 33; 2: 512; 3: 5547; 4: 1592 | Fire potential index overhead circuit mile days, see above for definition
5. Other | 5.a. | Other relevant weather pattern metrics tracked (add additional rows as needed) | [18 empty] | Not available.

## Table 5
Utility | Southern California Edison | Notes:
Table No. | 5 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.
Date Modified | 2023-02-01 | Data from 2015 - 2021 should be actual numbers. 2022 and 2023 should be projected. In future submissions update projected numbers with actuals
[7 empty] | Actual number of risk events | [15 empty] | Projected risk events
Table 5: Risk event drivers | [6 empty] | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4
Risk event category | Metric type | # | Risk event driver | Line Type | HFTD Tier | Are risk events tracked for ignition driver? (yes / no) | 2022 | 2022 | 2022 | 2022 | 2023 | 2023 | 2023 | 2023 | 2024 | 2024 | 2024 | 2024 | 2025 | 2025 | 2025 | 2025 | 2023 | 2024 | 2025 | Unit(s) | Comments | Blank Meaning
Wire down event | 1. Fire | 1.a.d.0 | Fire | Distribution | Non-HFTD | No | Actual number of risk events Q1: 4; Actual number of risk events Q2: 13; Actual number of risk events Q3: 17; Actual number of risk events Q4: 6 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 1. Fire | 1.a.d.2 | Fire | Distribution | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 1. Fire | 1.a.d.3 | Fire | Distribution | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 1. Fire | 1.a.t.0 | Fire | Transmission | Non-HFTD | No | Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 1. Fire | 1.a.t.2 | Fire | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 1. Fire | 1.a.t.3 | Fire | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.a.d.0 | Animal contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 6; Actual number of risk events Q2: 6; Actual number of risk events Q3: 7; Actual number of risk events Q4: 5 | 33.1943 | 33.1641 | 33.229 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.a.d.2 | Animal contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 2.9293 | 2.9266 | 2.9324 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.a.d.3 | Animal contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.a.t.0 | Animal contact | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.a.t.2 | Animal contact | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.a.t.3 | Animal contact | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.b.d.0 | Balloon contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 30; Actual number of risk events Q2: 38; Actual number of risk events Q3: 14; Actual number of risk events Q4: 11 | 93.2346 | 93.1164 | 93.4526 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.b.d.2 | Balloon contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 4.7327 | 4.7267 | 4.7438 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.b.d.3 | Balloon contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 1.7935 | 1.7912 | 1.7977 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.b.t.0 | Balloon contact | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.21959 | 0.21959 | 0.21959 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.b.t.2 | Balloon contact | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.b.t.3 | Balloon contact | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.c.d.0 | Land vehicle contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 63; Actual number of risk events Q2: 94; Actual number of risk events Q3: 88; Actual number of risk events Q4: 72 | 298.0424 | 297.8564 | 298.3986 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.c.d.2 | Land vehicle contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 2; Actual number of risk events Q2: 8; Actual number of risk events Q3: 10; Actual number of risk events Q4: 7 | 27.4274 | 27.4102 | 27.4601 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.c.d.3 | Land vehicle contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 8; Actual number of risk events Q2: 11; Actual number of risk events Q3: 12; Actual number of risk events Q4: 4 | 35.1717 | 35.1498 | 35.2138 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.c.t.0 | Land vehicle contact | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 1.3785 | 1.3785 | 1.3785 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.c.t.2 | Land vehicle contact | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.004892 | 0.004892 | 0.004892 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.c.t.3 | Land vehicle contact | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.d.d.0 | Aircraft vehicle contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.d.d.2 | Aircraft vehicle contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.d.d.3 | Aircraft vehicle contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.d.t.0 | Aircraft vehicle contact | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.d.t.2 | Aircraft vehicle contact | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.d.t.3 | Aircraft vehicle contact | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.e.d.0 | 3rd party contact | Distribution | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.e.d.2 | 3rd party contact | Distribution | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.e.d.3 | 3rd party contact | Distribution | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.e.t.0 | 3rd party contact | Transmission | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.e.t.2 | 3rd party contact | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.e.t.3 | 3rd party contact | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.f.d.0 | Other contact from object | Distribution | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 5; Actual number of risk events Q3: 2; Actual number of risk events Q4: 5 | 13.1247 | 13.1081 | 13.1285 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.f.d.2 | Other contact from object | Distribution | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0 | 0.25385 | 0.25353 | 0.25393 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.f.d.3 | Other contact from object | Distribution | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 2; Actual number of risk events Q4: 0 | 0.61146 | 0.61069 | 0.61164 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.f.t.0 | Other contact from object | Transmission | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.009067 | 0.009067 | 0.009067 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.f.t.2 | Other contact from object | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.f.t.3 | Other contact from object | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.g.d.0 | Unknown | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 203.4891 | 203.4891 | 203.4891 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.g.d.2 | Unknown | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 8.4702 | 8.4702 | 8.4702 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.g.d.3 | Unknown | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 10.121 | 10.121 | 10.121 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.g.t.0 | Unknown | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 1.0919 | 1.0919 | 1.0919 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.g.t.2 | Unknown | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.g.t.3 | Unknown | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 3. Vegetation contact | 3.a.d.0 | Vegetation contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 46; Actual number of risk events Q2: 35; Actual number of risk events Q3: 45; Actual number of risk events Q4: 44 | 230.8538 | 230.6673 | 231.1153 | # risk events (excluding ignitions) | Note: A portion of this data includes "Unknown" HFTD.
Wire down event | 3. Vegetation contact | 3.a.d.2 | Vegetation contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 9; Actual number of risk events Q2: 6; Actual number of risk events Q3: 3; Actual number of risk events Q4: 14 | 42.7625 | 42.7279 | 42.8109 | # risk events (excluding ignitions)
Wire down event | 3. Vegetation contact | 3.a.d.3 | Vegetation contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 41; Actual number of risk events Q2: 11; Actual number of risk events Q3: 21; Actual number of risk events Q4: 28 | 93.8653 | 93.7894 | 93.9716 | # risk events (excluding ignitions)
Wire down event | 3. Vegetation contact | 3.a.t.0 | Vegetation contact | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.011826 | 0.011826 | 0.011826 | # risk events (excluding ignitions)
Wire down event | 3. Vegetation contact | 3.a.t.2 | Vegetation contact | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.004929 | 0.004929 | 0.004929 | # risk events (excluding ignitions)
Wire down event | 3. Vegetation contact | 3.a.t.3 | Vegetation contact | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.a.d.0 | Anchor/guy | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0 | 1.9894 | 1.9894 | 1.9894 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.a.d.2 | Anchor/guy | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1 | 0.21123 | 0.21123 | 0.21123 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.a.d.3 | Anchor/guy | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.a.t.0 | Anchor/guy | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.a.t.2 | Anchor/guy | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.a.t.3 | Anchor/guy | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.b.d.0 | Capacitor bank | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.b.d.2 | Capacitor bank | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.b.d.3 | Capacitor bank | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.b.t.0 | Capacitor bank | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.b.t.2 | Capacitor bank | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.b.t.3 | Capacitor bank | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.c.d.0 | Conductor | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 15; Actual number of risk events Q2: 26; Actual number of risk events Q3: 41; Actual number of risk events Q4: 17 | 47.3282 | 47.3282 | 47.3282 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.c.d.2 | Conductor | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 2; Actual number of risk events Q3: 3; Actual number of risk events Q4: 0 | 7.8078 | 7.8078 | 7.8078 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.c.d.3 | Conductor | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 2; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 2 | 8.1921 | 8.1921 | 8.1921 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.c.t.0 | Conductor | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.59807 | 0.59807 | 0.59807 | # risk events (excluding ignitions) | Note: A portion of this data includes "Unknown" HFTD.
Wire down event | 4. Equipment / facility failure or damage | 4.c.t.2 | Conductor | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.3615 | 0.3615 | 0.3615 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.c.t.3 | Conductor | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.63983 | 0.63983 | 0.63983 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.d.d.0 | Connector device | Distribution | Non-HFTD | No | Actual number of risk events Q1: 18; Actual number of risk events Q2: 8; Actual number of risk events Q3: 20; Actual number of risk events Q4: 14 | 71.3036 | 71.1655 | 71.1518 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.d.d.2 | Connector device | Distribution | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0 | 3.8474 | 3.84 | 3.8392 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.d.d.3 | Connector device | Distribution | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 5; Actual number of risk events Q4: 1 | 7.1697 | 7.1558 | 7.1544 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.d.t.0 | Connector device | Transmission | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.d.t.2 | Connector device | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.d.t.3 | Connector device | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.005528 | 0.005528 | 0.005528 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.e.d.0 | Crossarm | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 7; Actual number of risk events Q2: 5; Actual number of risk events Q3: 8; Actual number of risk events Q4: 9 | 26.3099 | 26.2704 | 26.2163 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.e.d.2 | Crossarm | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 1.6634 | 1.6609 | 1.6575 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.e.d.3 | Crossarm | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 1.82 | 1.8172 | 1.8135 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.e.t.0 | Crossarm | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.e.t.2 | Crossarm | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.005528 | 0.005528 | 0.005528 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.e.t.3 | Crossarm | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.f.d.0 | Fuse | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0 | 1.835 | 1.835 | 1.835 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.f.d.2 | Fuse | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.f.d.3 | Fuse | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.f.t.0 | Fuse | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.f.t.2 | Fuse | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.f.t.3 | Fuse | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.g.d.0 | Cutout | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.g.d.2 | Cutout | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.g.d.3 | Cutout | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.g.t.0 | Cutout | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.g.t.2 | Cutout | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.g.t.3 | Cutout | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.h.d.0 | Insulator and bushing | Distribution | Non-HFTD | No | Actual number of risk events Q1: 1; Actual number of risk events Q2: 2; Actual number of risk events Q3: 3; Actual number of risk events Q4: 1 | 5.4403 | 5.4403 | 5.4403 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.h.d.2 | Insulator and bushing | Distribution | HFTD Tier 2 | No | Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.41446 | 0.41446 | 0.41446 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.h.d.3 | Insulator and bushing | Distribution | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0 | 0.41446 | 0.41446 | 0.41446 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.h.t.0 | Insulator and bushing | Transmission | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.29933 | 0.29933 | 0.29933 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.h.t.2 | Insulator and bushing | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.021642 | 0.021642 | 0.021642 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.h.t.3 | Insulator and bushing | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.021642 | 0.021642 | 0.021642 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.i.d.0 | Lightning arrester | Distribution | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1 | 1.0001 | 0.99809 | 0.98932 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.i.d.2 | Lightning arrester | Distribution | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.i.d.3 | Lightning arrester | Distribution | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.i.t.0 | Lightning arrester | Transmission | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.i.t.2 | Lightning arrester | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.i.t.3 | Lightning arrester | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.j.d.0 | Pole | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 9; Actual number of risk events Q2: 21; Actual number of risk events Q3: 26; Actual number of risk events Q4: 4 | 71.9197 | 71.9197 | 71.9197 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.j.d.2 | Pole | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 3; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 3.0774 | 3.0774 | 3.0774 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.j.d.3 | Pole | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 2; Actual number of risk events Q3: 2; Actual number of risk events Q4: 0 | 8.3283 | 8.3283 | 8.3283 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.j.t.0 | Pole | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.22789 | 0.22789 | 0.22789 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.j.t.2 | Pole | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.j.t.3 | Pole | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.k.d.0 | Recloser | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.k.d.2 | Recloser | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.k.d.3 | Recloser | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.k.t.0 | Recloser | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.k.t.2 | Recloser | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.k.t.3 | Recloser | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.l.d.0 | Relay | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.l.d.2 | Relay | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.l.d.3 | Relay | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.l.t.0 | Relay | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.l.t.2 | Relay | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.l.t.3 | Relay | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.m.d.0 | Sectionalizer | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.m.d.2 | Sectionalizer | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.m.d.3 | Sectionalizer | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.m.t.0 | Sectionalizer | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.m.t.2 | Sectionalizer | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.m.t.3 | Sectionalizer | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.n.d.0 | Splice | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 3; Actual number of risk events Q2: 1; Actual number of risk events Q3: 5; Actual number of risk events Q4: 2 | 17.9058 | 17.8716 | 17.8706 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.n.d.2 | Splice | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.89311 | 0.89141 | 0.89136 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.n.d.3 | Splice | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 2; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 3.5556 | 3.5488 | 3.5486 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.n.t.0 | Splice | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 1.2968 | 1.2968 | 1.2968 | # risk events (excluding ignitions) | Note: A portion of this data includes "Unknown" HFTD.
Wire down event | 4. Equipment / facility failure or damage | 4.n.t.2 | Splice | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.060113 | 0.060113 | 0.060113 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.n.t.3 | Splice | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.010509 | 0.010509 | 0.010509 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.o.d.0 | Switch | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.o.d.2 | Switch | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.o.d.3 | Switch | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.o.t.0 | Switch | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.o.t.2 | Switch | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.o.t.3 | Switch | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.p.d.0 | Tap | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 3; Actual number of risk events Q3: 2; Actual number of risk events Q4: 1 | 6.2068 | 6.1947 | 6.1934 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.p.d.2 | Tap | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1 | 0.5577 | 0.55662 | 0.5565 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.p.d.3 | Tap | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.010215 | 0.010195 | 0.010193 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.p.t.0 | Tap | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.p.t.2 | Tap | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.p.t.3 | Tap | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.q.d.0 | Tie wire | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.q.d.2 | Tie wire | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.q.d.3 | Tie wire | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.q.t.0 | Tie wire | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.q.t.2 | Tie wire | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.q.t.3 | Tie wire | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.r.d.0 | Transformer | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.r.d.2 | Transformer | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.r.d.3 | Transformer | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.r.t.0 | Transformer | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.r.t.2 | Transformer | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.r.t.3 | Transformer | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.s.d.0 | Voltage regulator/booster | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.s.d.2 | Voltage regulator/booster | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.s.d.3 | Voltage regulator/booster | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.s.t.0 | Voltage regulator/booster | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.s.t.2 | Voltage regulator/booster | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.s.t.3 | Voltage regulator/booster | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.t.d.0 | Unknown | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.t.d.2 | Unknown | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.t.d.3 | Unknown | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.t.t.0 | Unknown | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.t.t.2 | Unknown | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.t.t.3 | Unknown | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.u.d.0 | Other | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 47; Actual number of risk events Q2: 65; Actual number of risk events Q3: 65; Actual number of risk events Q4: 44 | 198.1203 | 197.7388 | 197.2466 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.u.d.2 | Other | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 2; Actual number of risk events Q2: 5; Actual number of risk events Q3: 2; Actual number of risk events Q4: 1 | 12.1234 | 12.1 | 12.0699 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.u.d.3 | Other | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 8; Actual number of risk events Q2: 3; Actual number of risk events Q3: 1; Actual number of risk events Q4: 5 | 12.9985 | 12.9734 | 12.9412 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.u.t.0 | Other | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.72344 | 0.72344 | 0.72344 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.u.t.2 | Other | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.u.t.3 | Other | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0 | 0.25818 | 0.25818 | 0.25818 | # risk events (excluding ignitions)
Wire down event | 5. Wire-to-wire contact | 5.a.d.0 | Wire-to-wire contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 1.2189 | 1.2189 | 1.2189 | # risk events (excluding ignitions)
Wire down event | 5. Wire-to-wire contact | 5.a.d.2 | Wire-to-wire contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.049608 | 0.049608 | 0.049608 | # risk events (excluding ignitions)
Wire down event | 5. Wire-to-wire contact | 5.a.d.3 | Wire-to-wire contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.018569 | 0.018569 | 0.018569 | # risk events (excluding ignitions)
Wire down event | 5. Wire-to-wire contact | 5.a.t.0 | Wire-to-wire contact | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 5. Wire-to-wire contact | 5.a.t.2 | Wire-to-wire contact | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 5. Wire-to-wire contact | 5.a.t.3 | Wire-to-wire contact | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 6. Contamination | 6.a.d.0 | Contamination | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 6. Contamination | 6.a.d.2 | Contamination | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 6. Contamination | 6.a.d.3 | Contamination | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 6. Contamination | 6.a.t.0 | Contamination | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 6. Contamination | 6.a.t.2 | Contamination | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 6. Contamination | 6.a.t.3 | Contamination | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 7. Vandalism/theft | 7.a.d.0 | Vandalism/theft | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 4; Actual number of risk events Q2: 1; Actual number of risk events Q3: 2; Actual number of risk events Q4: 4 | 12.8785 | 12.8785 | 12.8785 | # risk events (excluding ignitions)
Wire down event | 7. Vandalism/theft | 7.a.d.2 | Vandalism/theft | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 7. Vandalism/theft | 7.a.d.3 | Vandalism/theft | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.000168 | 0.000168 | 0.000168 | # risk events (excluding ignitions)
Wire down event | 7. Vandalism/theft | 7.a.t.0 | Vandalism/theft | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 7. Vandalism/theft | 7.a.t.2 | Vandalism/theft | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 9.29e-05 | 9.29e-05 | 9.29e-05 | # risk events (excluding ignitions)
Wire down event | 7. Vandalism/theft | 7.a.t.3 | Vandalism/theft | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 8. Lightning | 8.a.d.0 | Lightning | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 16; Actual number of risk events Q3: 3; Actual number of risk events Q4: 4 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 8. Lightning | 8.a.d.2 | Lightning | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 8. Lightning | 8.a.d.3 | Lightning | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 3; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 8. Lightning | 8.a.t.0 | Lightning | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 8. Lightning | 8.a.t.2 | Lightning | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 8. Lightning | 8.a.t.3 | Lightning | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 9. Unknown | 9.a.d.0 | Unknown | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 15; Actual number of risk events Q2: 32; Actual number of risk events Q3: 43; Actual number of risk events Q4: 44 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 9. Unknown | 9.a.d.2 | Unknown | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 2; Actual number of risk events Q3: 3; Actual number of risk events Q4: 3 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 9. Unknown | 9.a.d.3 | Unknown | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 2; Actual number of risk events Q3: 2; Actual number of risk events Q4: 4 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 9. Unknown | 9.a.t.0 | Unknown | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 9. Unknown | 9.a.t.2 | Unknown | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 9. Unknown | 9.a.t.3 | Unknown | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 10. Other | 10.a.d.0 | All Other | Distribution | Non-HFTD | No | Actual number of risk events Q1: 35; Actual number of risk events Q2: 43; Actual number of risk events Q3: 39; Actual number of risk events Q4: 38 | 145.4754 | 145.1931 | 145.1622 | # risk events (excluding ignitions)
Wire down event | 10. Other | 10.a.d.2 | All Other | Distribution | HFTD Tier 2 | No | Actual number of risk events Q1: 2; Actual number of risk events Q2: 4; Actual number of risk events Q3: 2; Actual number of risk events Q4: 5 | 22.7137 | 22.6696 | 22.6648 | # risk events (excluding ignitions)
Wire down event | 10. Other | 10.a.d.3 | All Other | Distribution | HFTD Tier 3 | No | Actual number of risk events Q1: 9; Actual number of risk events Q2: 1; Actual number of risk events Q3: 3; Actual number of risk events Q4: 6 | 35.0802 | 35.0122 | 35.0047 | # risk events (excluding ignitions)
Wire down event | 10. Other | 10.a.t.0 | All Other | Transmission | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.11019 | 0.11019 | 0.11019 | # risk events (excluding ignitions)
Wire down event | 10. Other | 10.a.t.2 | All Other | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 10. Other | 10.a.t.3 | All Other | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.054035 | 0.054035 | 0.054035 | # risk events (excluding ignitions)
Unplanned Outage | 11. Dig-in | 11.a.d.0 | Dig-in | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 15; Actual number of risk events Q2: 18; Actual number of risk events Q3: 14; Actual number of risk events Q4: 10 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 11. Dig-in | 11.a.d.2 | Dig-in | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 2; Actual number of risk events Q2: 2; Actual number of risk events Q3: 1; Actual number of risk events Q4: 2 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 11. Dig-in | 11.a.d.3 | Dig-in | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 1; Actual number of risk events Q3: 1; Actual number of risk events Q4: 2 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 11. Dig-in | 11.a.t.0 | Dig-in | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 11. Dig-in | 11.a.t.2 | Dig-in | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 11. Dig-in | 11.a.t.3 | Dig-in | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 12. Fire | 12.a.d.0 | Fire | Distribution | Non-HFTD | No | Actual number of risk events Q1: 14; Actual number of risk events Q2: 28; Actual number of risk events Q3: 35; Actual number of risk events Q4: 21 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 12. Fire | 12.a.d.2 | Fire | Distribution | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 2; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 12. Fire | 12.a.d.3 | Fire | Distribution | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 12. Fire | 12.a.t.0 | Fire | Transmission | Non-HFTD | No | Actual number of risk events Q1: 4; Actual number of risk events Q2: 2; Actual number of risk events Q3: 3; Actual number of risk events Q4: 1 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 12. Fire | 12.a.t.2 | Fire | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 12. Fire | 12.a.t.3 | Fire | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.a.d.0 | Animal contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 64; Actual number of risk events Q2: 166; Actual number of risk events Q3: 141; Actual number of risk events Q4: 94 | 503.6743 | 500.2201 | 494.9232 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.a.d.2 | Animal contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 2; Actual number of risk events Q2: 12; Actual number of risk events Q3: 12; Actual number of risk events Q4: 4 | 47.6435 | 45.568 | 44.7865 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.a.d.3 | Animal contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 12; Actual number of risk events Q2: 26; Actual number of risk events Q3: 14; Actual number of risk events Q4: 11 | 66.2166 | 63.1707 | 60.6245 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.a.t.0 | Animal contact | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 7; Actual number of risk events Q2: 6; Actual number of risk events Q3: 4; Actual number of risk events Q4: 1 | 16.3727 | 16.3727 | 16.3727 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.a.t.2 | Animal contact | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 2; Actual number of risk events Q3: 1; Actual number of risk events Q4: 1 | 3.797 | 3.7 | 3.6059 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.a.t.3 | Animal contact | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 3; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1 | 5.0501 | 4.9636 | 4.8776 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.b.d.0 | Balloon contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 209; Actual number of risk events Q2: 272; Actual number of risk events Q3: 171; Actual number of risk events Q4: 88 | 846.6854 | 845.7848 | 843.3977 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.b.d.2 | Balloon contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 2; Actual number of risk events Q2: 9; Actual number of risk events Q3: 4; Actual number of risk events Q4: 3 | 28.0227 | 27.8133 | 27.722 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.b.d.3 | Balloon contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 5; Actual number of risk events Q2: 7; Actual number of risk events Q3: 3; Actual number of risk events Q4: 4 | 25.147 | 24.5507 | 24.8185 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.b.t.0 | Balloon contact | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 2; Actual number of risk events Q2: 10; Actual number of risk events Q3: 3; Actual number of risk events Q4: 2 | 30.0683 | 30.0683 | 30.0683 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.b.t.2 | Balloon contact | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 2.0966 | 2.0966 | 2.0966 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.b.t.3 | Balloon contact | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0 | 1.4891 | 1.4891 | 1.4891 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.c.d.0 | Land vehicle contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 117; Actual number of risk events Q2: 123; Actual number of risk events Q3: 122; Actual number of risk events Q4: 96 | 454.2456 | 453.8739 | 453.2061 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.c.d.2 | Land vehicle contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 3; Actual number of risk events Q2: 10; Actual number of risk events Q3: 13; Actual number of risk events Q4: 5 | 29.9326 | 29.8952 | 30.025 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.c.d.3 | Land vehicle contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 20; Actual number of risk events Q2: 13; Actual number of risk events Q3: 18; Actual number of risk events Q4: 8 | 57.612 | 58.2721 | 58.5831 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.c.t.0 | Land vehicle contact | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 9; Actual number of risk events Q2: 3; Actual number of risk events Q3: 7; Actual number of risk events Q4: 2 | 20.7565 | 20.5326 | 20.5269 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.c.t.2 | Land vehicle contact | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.c.t.3 | Land vehicle contact | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 1 | 1.7452 | 1.7446 | 1.7444 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.d.d.0 | Aircraft vehicle contact | Distribution | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.d.d.2 | Aircraft vehicle contact | Distribution | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.d.d.3 | Aircraft vehicle contact | Distribution | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.d.t.0 | Aircraft vehicle contact | Transmission | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.d.t.2 | Aircraft vehicle contact | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.d.t.3 | Aircraft vehicle contact | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.e.d.0 | 3rd party contact | Distribution | Non-HFTD | No | Actual number of risk events Q1: 7; Actual number of risk events Q2: 11; Actual number of risk events Q3: 6; Actual number of risk events Q4: 6 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.e.d.2 | 3rd party contact | Distribution | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 2; Actual number of risk events Q3: 2; Actual number of risk events Q4: 1 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.e.d.3 | 3rd party contact | Distribution | HFTD Tier 3 | No | Actual number of risk events Q1: 2; Actual number of risk events Q2: 0; Actual number of risk events Q3: 3; Actual number of risk events Q4: 2 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.e.t.0 | 3rd party contact | Transmission | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.e.t.2 | 3rd party contact | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.e.t.3 | 3rd party contact | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.f.d.0 | Other | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 21; Actual number of risk events Q2: 31; Actual number of risk events Q3: 22; Actual number of risk events Q4: 14 | 98.3413 | 98.0462 | 97.7264 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.f.d.2 | Other | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 1; Actual number of risk events Q3: 2; Actual number of risk events Q4: 2 | 8.398 | 7.9068 | 7.4871 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.f.d.3 | Other | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 3; Actual number of risk events Q2: 1; Actual number of risk events Q3: 3; Actual number of risk events Q4: 2 | 12.5712 | 11.6501 | 10.9305 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.f.t.0 | Other | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 5; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1 | 5.9494 | 5.9035 | 5.9014 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.f.t.2 | Other | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.f.t.3 | Other | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.g.d.0 | Unknown | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.g.d.2 | Unknown | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.g.d.3 | Unknown | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.g.t.0 | Unknown | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.g.t.2 | Unknown | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.g.t.3 | Unknown | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 14. Vegetation contact | 14.a.d.0 | Vegetation contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 72; Actual number of risk events Q2: 18; Actual number of risk events Q3: 32; Actual number of risk events Q4: 57 | 175.1937 | 175.1017 | 174.807 | # risk events (excluding ignitions)
Unplanned Outage | 14. Vegetation contact | 14.a.d.2 | Vegetation contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 8; Actual number of risk events Q2: 4; Actual number of risk events Q3: 3; Actual number of risk events Q4: 11 | 44.7531 | 42.5444 | 41.3097 | # risk events (excluding ignitions)
Unplanned Outage | 14. Vegetation contact | 14.a.d.3 | Vegetation contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 10; Actual number of risk events Q2: 6; Actual number of risk events Q3: 5; Actual number of risk events Q4: 14 | 77.1636 | 72.5996 | 70.6338 | # risk events (excluding ignitions)
Unplanned Outage | 14. Vegetation contact | 14.a.t.0 | Vegetation contact | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.24437 | 0.24437 | 0.24437 | # risk events (excluding ignitions)
Unplanned Outage | 14. Vegetation contact | 14.a.t.2 | Vegetation contact | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1 | 1.4299 | 1.4299 | 1.4299 | # risk events (excluding ignitions)
Unplanned Outage | 14. Vegetation contact | 14.a.t.3 | Vegetation contact | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 1.6928 | 1.6816 | 1.667 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.a.d.0 | Anchor/guy | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 2; Actual number of risk events Q2: 3; Actual number of risk events Q3: 2; Actual number of risk events Q4: 0 | 10.4996 | 10.4996 | 10.4996 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.a.d.2 | Anchor/guy | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.74983 | 0.74983 | 0.74983 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.a.d.3 | Anchor/guy | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 1 | 1.4998 | 1.4998 | 1.4998 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.a.t.0 | Anchor/guy | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.a.t.2 | Anchor/guy | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.a.t.3 | Anchor/guy | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.b.d.0 | Capacitor bank | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 5; Actual number of risk events Q2: 10; Actual number of risk events Q3: 15; Actual number of risk events Q4: 8 | 32.7752 | 32.7734 | 32.7692 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.b.d.2 | Capacitor bank | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0 | 1.3104 | 1.3104 | 1.3104 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.b.d.3 | Capacitor bank | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 2; Actual number of risk events Q2: 1; Actual number of risk events Q3: 3; Actual number of risk events Q4: 0 | 3.5662 | 3.3692 | 3.2127 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.b.t.0 | Capacitor bank | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 3.6189 | 3.6189 | 3.6189 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.b.t.2 | Capacitor bank | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 1.1237 | 1.1237 | 1.1237 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.b.t.3 | Capacitor bank | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.74884 | 0.74884 | 0.74884 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.c.d.0 | Conductor | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 194; Actual number of risk events Q2: 131; Actual number of risk events Q3: 174; Actual number of risk events Q4: 124 | 609.5489 | 607.9625 | 605.8275 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.c.d.2 | Conductor | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 8; Actual number of risk events Q2: 12; Actual number of risk events Q3: 13; Actual number of risk events Q4: 6 | 63.0708 | 59.9076 | 58.071 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.c.d.3 | Conductor | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 40; Actual number of risk events Q2: 14; Actual number of risk events Q3: 13; Actual number of risk events Q4: 23 | 100.2712 | 95.4653 | 92.8042 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.c.t.0 | Conductor | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 3; Actual number of risk events Q2: 8; Actual number of risk events Q3: 6; Actual number of risk events Q4: 7 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.c.t.2 | Conductor | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.c.t.3 | Conductor | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.d.d.0 | Connection device | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 150; Actual number of risk events Q2: 153; Actual number of risk events Q3: 124; Actual number of risk events Q4: 137 | 479.8438 | 478.6123 | 476.8374 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.d.d.2 | Connection device | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 12; Actual number of risk events Q2: 16; Actual number of risk events Q3: 9; Actual number of risk events Q4: 16 | 47.2426 | 46.4404 | 46.403 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.d.d.3 | Connection device | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 13; Actual number of risk events Q2: 18; Actual number of risk events Q3: 13; Actual number of risk events Q4: 24 | 53.255 | 52.1093 | 52.372 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.d.t.0 | Connection device | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 2; Actual number of risk events Q2: 3; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1 | 5.0308 | 5.0308 | 5.0308 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.d.t.2 | Connection device | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.054882 | 0.054882 | 0.054882 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.d.t.3 | Connection device | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.e.d.0 | Crossarm | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 37; Actual number of risk events Q2: 25; Actual number of risk events Q3: 30; Actual number of risk events Q4: 32 | 191.0492 | 190.2666 | 189.9551 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.e.d.2 | Crossarm | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 4; Actual number of risk events Q3: 1; Actual number of risk events Q4: 2 | 3.1558 | 3.1558 | 3.1558 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.e.d.3 | Crossarm | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 2; Actual number of risk events Q4: 2 | 6.2556 | 5.6763 | 5.0475 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.e.t.0 | Crossarm | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 2; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 5.603 | 5.603 | 5.603 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.e.t.2 | Crossarm | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.50594 | 0.50594 | 0.50594 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.e.t.3 | Crossarm | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.00594 | 0.00594 | 0.00594 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.f.d.0 | Fuse | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 128; Actual number of risk events Q2: 186; Actual number of risk events Q3: 232; Actual number of risk events Q4: 148 | 694.2424 | 693.0039 | 691.9622 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.f.d.2 | Fuse | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 18; Actual number of risk events Q2: 24; Actual number of risk events Q3: 47; Actual number of risk events Q4: 18 | 73.8677 | 64.8978 | 57.8073 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.f.d.3 | Fuse | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 25; Actual number of risk events Q2: 30; Actual number of risk events Q3: 48; Actual number of risk events Q4: 38 | 132.6352 | 119.381 | 110.0412 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.f.t.0 | Fuse | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.f.t.2 | Fuse | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.f.t.3 | Fuse | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.g.d.0 | Cutout | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.g.d.2 | Cutout | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.g.d.3 | Cutout | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.g.t.0 | Cutout | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.g.t.2 | Cutout | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.g.t.3 | Cutout | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.h.d.0 | Insulator and bushing | Distribution | Non-HFTD | No | Actual number of risk events Q1: 13; Actual number of risk events Q2: 10; Actual number of risk events Q3: 21; Actual number of risk events Q4: 28 | 70.7605 | 70.6428 | 70.3956 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.h.d.2 | Insulator and bushing | Distribution | HFTD Tier 2 | No | Actual number of risk events Q1: 4; Actual number of risk events Q2: 1; Actual number of risk events Q3: 1; Actual number of risk events Q4: 2 | 9.61 | 8.9257 | 8.6172 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.h.d.3 | Insulator and bushing | Distribution | HFTD Tier 3 | No | Actual number of risk events Q1: 2; Actual number of risk events Q2: 0; Actual number of risk events Q3: 4; Actual number of risk events Q4: 9 | 12.1877 | 11.2031 | 10.7052 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.h.t.0 | Insulator and bushing | Transmission | Non-HFTD | No | Actual number of risk events Q1: 1; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.h.t.2 | Insulator and bushing | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 1; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.h.t.3 | Insulator and bushing | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.i.d.0 | Lightning arrestor | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 6; Actual number of risk events Q2: 13; Actual number of risk events Q3: 10; Actual number of risk events Q4: 6 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.i.d.2 | Lightning arrestor | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 4; Actual number of risk events Q3: 1; Actual number of risk events Q4: 1 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.i.d.3 | Lightning arrestor | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 2; Actual number of risk events Q2: 2; Actual number of risk events Q3: 0; Actual number of risk events Q4: 3 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.i.t.0 | Lightning arrestor | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.i.t.2 | Lightning arrestor | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.i.t.3 | Lightning arrestor | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.j.d.0 | Pole | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 20; Actual number of risk events Q2: 14; Actual number of risk events Q3: 46; Actual number of risk events Q4: 10 | 91.0497 | 90.8809 | 90.6537 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.j.d.2 | Pole | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 8; Actual number of risk events Q3: 3; Actual number of risk events Q4: 3 | 18.9319 | 18.285 | 17.8869 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.j.d.3 | Pole | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 8; Actual number of risk events Q2: 2; Actual number of risk events Q3: 4; Actual number of risk events Q4: 1 | 7.8277 | 7.4667 | 7.1641 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.j.t.0 | Pole | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 7; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.j.t.2 | Pole | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 2; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.j.t.3 | Pole | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.k.d.0 | Recloser | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.k.d.2 | Recloser | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.k.d.3 | Recloser | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.k.t.0 | Recloser | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.k.t.2 | Recloser | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.k.t.3 | Recloser | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.l.d.0 | Relay | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.l.d.2 | Relay | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.l.d.3 | Relay | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.l.t.0 | Relay | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.l.t.2 | Relay | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.l.t.3 | Relay | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.m.d.0 | Sectionalizer | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.m.d.2 | Sectionalizer | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.m.d.3 | Sectionalizer | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.m.t.0 | Sectionalizer | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.m.t.2 | Sectionalizer | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.m.t.3 | Sectionalizer | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.n.d.0 | Splice | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.n.d.2 | Splice | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.n.d.3 | Splice | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.n.t.0 | Splice | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.n.t.2 | Splice | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.n.t.3 | Splice | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.o.d.0 | Switch | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 9; Actual number of risk events Q2: 16; Actual number of risk events Q3: 31; Actual number of risk events Q4: 17 | 73.4724 | 73.4386 | 73.3722 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.o.d.2 | Switch | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 2; Actual number of risk events Q3: 4; Actual number of risk events Q4: 1 | 5.3846 | 5.3846 | 5.3846 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.o.d.3 | Switch | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 2; Actual number of risk events Q3: 5; Actual number of risk events Q4: 1 | 9.1563 | 8.644 | 7.8294 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.o.t.0 | Switch | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.o.t.2 | Switch | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.o.t.3 | Switch | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.p.d.0 | Tap | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.p.d.2 | Tap | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.p.d.3 | Tap | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.p.t.0 | Tap | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.p.t.2 | Tap | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.p.t.3 | Tap | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.q.d.0 | Tie wire | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.q.d.2 | Tie wire | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.q.d.3 | Tie wire | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.q.t.0 | Tie wire | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.q.t.2 | Tie wire | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.q.t.3 | Tie wire | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.r.d.0 | Transformer | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 232; Actual number of risk events Q2: 424; Actual number of risk events Q3: 732; Actual number of risk events Q4: 225 | 1663.397 | 1656.344 | 1647.444 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.r.d.2 | Transformer | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 41; Actual number of risk events Q2: 65; Actual number of risk events Q3: 65; Actual number of risk events Q4: 31 | 230.2307 | 222.1104 | 216.2654 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.r.d.3 | Transformer | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 39; Actual number of risk events Q2: 86; Actual number of risk events Q3: 109; Actual number of risk events Q4: 55 | 310.7854 | 300.5502 | 286.8855 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.r.t.0 | Transformer | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.r.t.2 | Transformer | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.r.t.3 | Transformer | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.s.d.0 | Voltage regulator/booster | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 3; Actual number of risk events Q4: 0 | 2.7141 | 2.7141 | 2.7141 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.s.d.2 | Voltage regulator/booster | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.085579 | 0.085579 | 0.085579 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.s.d.3 | Voltage regulator/booster | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0 | 0.085579 | 0.085579 | 0.085579 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.s.t.0 | Voltage regulator/booster | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.s.t.2 | Voltage regulator/booster | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.s.t.3 | Voltage regulator/booster | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.t.d.0 | Unknown | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.t.d.2 | Unknown | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.t.d.3 | Unknown | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.t.t.0 | Unknown | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.t.t.2 | Unknown | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.t.t.3 | Unknown | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.u.d.0 | Other | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 19; Actual number of risk events Q2: 26; Actual number of risk events Q3: 22; Actual number of risk events Q4: 25 | 94.2507 | 94.0322 | 93.7566 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.u.d.2 | Other | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 3; Actual number of risk events Q2: 3; Actual number of risk events Q3: 0; Actual number of risk events Q4: 5 | 7.3774 | 7.3462 | 7.3413 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.u.d.3 | Other | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 2; Actual number of risk events Q2: 4; Actual number of risk events Q3: 4; Actual number of risk events Q4: 10 | 13.1469 | 12.958 | 12.8081 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.u.t.0 | Other | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 4; Actual number of risk events Q3: 1; Actual number of risk events Q4: 1 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.u.t.2 | Other | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.u.t.3 | Other | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 16. Wire-to-wire contact | 16.a.d.0 | Wire-to-wire contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 4; Actual number of risk events Q2: 3; Actual number of risk events Q3: 2; Actual number of risk events Q4: 3 | 27.3482 | 27.3317 | 27.2836 | # risk events (excluding ignitions)
Unplanned Outage | 16. Wire-to-wire contact | 16.a.d.2 | Wire-to-wire contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 1.5292 | 1.5955 | 1.5723 | # risk events (excluding ignitions)
Unplanned Outage | 16. Wire-to-wire contact | 16.a.d.3 | Wire-to-wire contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.017658 | 0.017347 | 0.017541 | # risk events (excluding ignitions)
Unplanned Outage | 16. Wire-to-wire contact | 16.a.t.0 | Wire-to-wire contact | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 16. Wire-to-wire contact | 16.a.t.2 | Wire-to-wire contact | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 16. Wire-to-wire contact | 16.a.t.3 | Wire-to-wire contact | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 17. Contamination | 17.a.d.0 | Contamination | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 2; Actual number of risk events Q4: 0 | 9.1084 | 9.0949 | 9.0765 | # risk events (excluding ignitions)
Unplanned Outage | 17. Contamination | 17.a.d.2 | Contamination | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.022772 | 0.022669 | 0.022604 | # risk events (excluding ignitions)
Unplanned Outage | 17. Contamination | 17.a.d.3 | Contamination | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.017862 | 0.017862 | 0.017862 | # risk events (excluding ignitions)
Unplanned Outage | 17. Contamination | 17.a.t.0 | Contamination | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 3; Actual number of risk events Q2: 3; Actual number of risk events Q3: 4; Actual number of risk events Q4: 2 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 17. Contamination | 17.a.t.2 | Contamination | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 17. Contamination | 17.a.t.3 | Contamination | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 18. Vandalism/theft | 18.a.d.0 | Vandalism/theft | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 3; Actual number of risk events Q2: 5; Actual number of risk events Q3: 1; Actual number of risk events Q4: 4 | 10.2317 | 10.2239 | 10.2175 | # risk events (excluding ignitions)
Unplanned Outage | 18. Vandalism/theft | 18.a.d.2 | Vandalism/theft | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 1.2681 | 1.2658 | 1.2594 | # risk events (excluding ignitions)
Unplanned Outage | 18. Vandalism/theft | 18.a.d.3 | Vandalism/theft | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.074446 | 0.074383 | 0.074295 | # risk events (excluding ignitions)
Unplanned Outage | 18. Vandalism/theft | 18.a.t.0 | Vandalism/theft | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.000861 | 0.000861 | 0.000861 | # risk events (excluding ignitions)
Unplanned Outage | 18. Vandalism/theft | 18.a.t.2 | Vandalism/theft | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 18. Vandalism/theft | 18.a.t.3 | Vandalism/theft | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 6.87e-05 | 6.87e-05 | 6.87e-05 | # risk events (excluding ignitions)
Unplanned Outage | 19. Lightning | 19.a.d.0 | Lightning | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 5; Actual number of risk events Q2: 322; Actual number of risk events Q3: 28; Actual number of risk events Q4: 40 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 19. Lightning | 19.a.d.2 | Lightning | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 19; Actual number of risk events Q3: 3; Actual number of risk events Q4: 3 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 19. Lightning | 19.a.d.3 | Lightning | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 2; Actual number of risk events Q2: 25; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 19. Lightning | 19.a.t.0 | Lightning | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 3; Actual number of risk events Q2: 25; Actual number of risk events Q3: 2; Actual number of risk events Q4: 4 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 19. Lightning | 19.a.t.2 | Lightning | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 2; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 19. Lightning | 19.a.t.3 | Lightning | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 3; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 20. Government agency request | 20.a.d.0 | Government agency request | Distribution | Non-HFTD | No | Actual number of risk events Q1: 1; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 2 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 20. Government agency request | 20.a.d.2 | Government agency request | Distribution | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 20. Government agency request | 20.a.d.3 | Government agency request | Distribution | HFTD Tier 3 | No | Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 20. Government agency request | 20.a.t.0 | Government agency request | Transmission | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 2; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 20. Government agency request | 20.a.t.2 | Government agency request | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 20. Government agency request | 20.a.t.3 | Government agency request | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 21. Customer request | 21.a.d.0 | Customer request | Distribution | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 21. Customer request | 21.a.d.2 | Customer request | Distribution | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 21. Customer request | 21.a.d.3 | Customer request | Distribution | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 21. Customer request | 21.a.t.0 | Customer request | Transmission | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 21. Customer request | 21.a.t.2 | Customer request | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 21. Customer request | 21.a.t.3 | Customer request | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 22. Emergency repairs | 22.a.d.0 | Emergency repairs | Distribution | Non-HFTD | No | Actual number of risk events Q1: 1171; Actual number of risk events Q2: 1245; Actual number of risk events Q3: 1410; Actual number of risk events Q4: 1007 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 22. Emergency repairs | 22.a.d.2 | Emergency repairs | Distribution | HFTD Tier 2 | No | Actual number of risk events Q1: 258; Actual number of risk events Q2: 172; Actual number of risk events Q3: 167; Actual number of risk events Q4: 134 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 22. Emergency repairs | 22.a.d.3 | Emergency repairs | Distribution | HFTD Tier 3 | No | Actual number of risk events Q1: 275; Actual number of risk events Q2: 257; Actual number of risk events Q3: 313; Actual number of risk events Q4: 180 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 22. Emergency repairs | 22.a.t.0 | Emergency repairs | Transmission | Non-HFTD | No | Actual number of risk events Q1: 41; Actual number of risk events Q2: 53; Actual number of risk events Q3: 24; Actual number of risk events Q4: 17 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 22. Emergency repairs | 22.a.t.2 | Emergency repairs | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 22. Emergency repairs | 22.a.t.3 | Emergency repairs | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 23. Unknown | 23.a.d.0 | Unknown | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 385; Actual number of risk events Q2: 464; Actual number of risk events Q3: 383; Actual number of risk events Q4: 304 | 1537.316 | 1533.696 | 1530.453 | # risk events (excluding ignitions)
Unplanned Outage | 23. Unknown | 23.a.d.2 | Unknown | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 26; Actual number of risk events Q2: 55; Actual number of risk events Q3: 50; Actual number of risk events Q4: 45 | 215.744 | 212.1381 | 209.4628 | # risk events (excluding ignitions)
Unplanned Outage | 23. Unknown | 23.a.d.3 | Unknown | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 43; Actual number of risk events Q2: 48; Actual number of risk events Q3: 56; Actual number of risk events Q4: 57 | 270.2319 | 270.2319 | 270.2319 | # risk events (excluding ignitions)
Unplanned Outage | 23. Unknown | 23.a.t.0 | Unknown | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 37; Actual number of risk events Q2: 82; Actual number of risk events Q3: 39; Actual number of risk events Q4: 32 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 23. Unknown | 23.a.t.2 | Unknown | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 4 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 23. Unknown | 23.a.t.3 | Unknown | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 2; Actual number of risk events Q4: 1 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 24. Other | 24.a.d.0 | All Other | Distribution | Non-HFTD | No | Actual number of risk events Q1: 311; Actual number of risk events Q2: 459; Actual number of risk events Q3: 680; Actual number of risk events Q4: 300 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 24. Other | 24.a.d.2 | All Other | Distribution | HFTD Tier 2 | No | Actual number of risk events Q1: 31; Actual number of risk events Q2: 34; Actual number of risk events Q3: 64; Actual number of risk events Q4: 37 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 24. Other | 24.a.d.3 | All Other | Distribution | HFTD Tier 3 | No | Actual number of risk events Q1: 52; Actual number of risk events Q2: 69; Actual number of risk events Q3: 117; Actual number of risk events Q4: 45 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 24. Other | 24.a.t.0 | All Other | Transmission | Non-HFTD | No | Actual number of risk events Q1: 40; Actual number of risk events Q2: 53; Actual number of risk events Q3: 46; Actual number of risk events Q4: 41 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 24. Other | 24.a.t.2 | All Other | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 8; Actual number of risk events Q3: 2; Actual number of risk events Q4: 1 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 24. Other | 24.a.t.3 | All Other | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 9; Actual number of risk events Q2: 8; Actual number of risk events Q3: 4; Actual number of risk events Q4: 2 | 0 | 0 | 0 | # risk events (excluding ignitions)

## Table 6
Utility | Southern California Edison | Notes:
Table No. | 6 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.
Date Modified | 2023-02-01 | Data from 2015 - 2021 should be actual numbers. 2022 and 2023 should be projected. In future submissions update projected numbers with actuals
[6 empty] | Actual number of ignitions | [15 empty] | Projected ignitions
Table 6: Ignition drivers | [5 empty] | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4
Metric type | # | Ignition driver | Line Type | HFTD Tier | Are ignitions tracked for ignition driver? (yes / no) | 2022 | 2022 | 2022 | 2022 | 2023 | 2023 | 2023 | 2023 | 2024 | 2024 | 2024 | 2024 | 2025 | 2025 | 2025 | 2025 | 2023 | 2024 | 2025 | Unit(s) | Comments | Blank Meaning
1. Dig-in | 1.a.d.0 | Dig-in | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
1. Dig-in | 1.a.d.2 | Dig-in | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
1. Dig-in | 1.a.d.3 | Dig-in | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
1. Dig-in | 1.a.t.0 | Dig-in | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
1. Dig-in | 1.a.t.2 | Dig-in | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
1. Dig-in | 1.a.t.3 | Dig-in | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
2. Contact from object | 2.a.d.0 | Animal contact | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 1; Actual number of ignitions Q2: 5; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 0 | 6.1334 | 6.0963 | 6.0412 | # ignitions
2. Contact from object | 2.a.d.2 | Animal contact | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 1.4453 | 1.3762 | 1.3416 | # ignitions
2. Contact from object | 2.a.d.3 | Animal contact | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 1; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 0 | 2.5912 | 2.4647 | 2.3354 | # ignitions
2. Contact from object | 2.a.t.0 | Animal contact | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 2; Actual number of ignitions Q4: 0 | 1.6319 | 1.6319 | 1.6319 | # ignitions
2. Contact from object | 2.a.t.2 | Animal contact | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.95998 | 0.93667 | 0.91507 | # ignitions
2. Contact from object | 2.a.t.3 | Animal contact | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 0 | 1.6532 | 1.6276 | 1.6031 | # ignitions
2. Contact from object | 2.b.d.0 | Balloon contact | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 7; Actual number of ignitions Q2: 3; Actual number of ignitions Q3: 3; Actual number of ignitions Q4: 0 | 13.5921 | 13.5782 | 13.5388 | # ignitions
2. Contact from object | 2.b.d.2 | Balloon contact | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 1.1781 | 1.1709 | 1.1657 | # ignitions
2. Contact from object | 2.b.d.3 | Balloon contact | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 1.9844 | 1.9163 | 1.9288 | # ignitions
2. Contact from object | 2.b.t.0 | Balloon contact | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.44221 | 0.44221 | 0.44221 | # ignitions
2. Contact from object | 2.b.t.2 | Balloon contact | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.11841 | 0.11841 | 0.11841 | # ignitions
2. Contact from object | 2.b.t.3 | Balloon contact | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.11841 | 0.11841 | 0.11841 | # ignitions
2. Contact from object | 2.c.d.0 | Land vehicle contact | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 2; Actual number of ignitions Q2: 3; Actual number of ignitions Q3: 3; Actual number of ignitions Q4: 1 | 7.2537 | 7.2485 | 7.2394 | # ignitions
2. Contact from object | 2.c.d.2 | Land vehicle contact | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.8391 | 0.8349 | 0.83998 | # ignitions
2. Contact from object | 2.c.d.3 | Land vehicle contact | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 1; Actual number of ignitions Q2: 2; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 2.7065 | 2.7332 | 2.7478 | # ignitions
2. Contact from object | 2.c.t.0 | Land vehicle contact | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 0 | 0.34583 | 0.34471 | 0.34471 | # ignitions
2. Contact from object | 2.c.t.2 | Land vehicle contact | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
2. Contact from object | 2.c.t.3 | Land vehicle contact | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.19866 | 0.19856 | 0.19853 | # ignitions
2. Contact from object | 2.d.d.0 | Aircraft vehicle contact | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
2. Contact from object | 2.d.d.2 | Aircraft vehicle contact | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
2. Contact from object | 2.d.d.3 | Aircraft vehicle contact | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
2. Contact from object | 2.d.t.0 | Aircraft vehicle contact | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
2. Contact from object | 2.d.t.2 | Aircraft vehicle contact | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
2. Contact from object | 2.d.t.3 | Aircraft vehicle contact | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
2. Contact from object | 2.e.d.0 | 3rd party facility | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
2. Contact from object | 2.e.d.2 | 3rd party facility | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
2. Contact from object | 2.e.d.3 | 3rd party facility | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
2. Contact from object | 2.e.t.0 | 3rd party facility | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
2. Contact from object | 2.e.t.2 | 3rd party facility | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
2. Contact from object | 2.e.t.3 | 3rd party facility | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
2. Contact from object | 2.f.d.0 | Unknown | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
2. Contact from object | 2.f.d.2 | Unknown | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
2. Contact from object | 2.f.d.3 | Unknown | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
2. Contact from object | 2.f.t.0 | Unknown | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
2. Contact from object | 2.f.t.2 | Unknown | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
2. Contact from object | 2.f.t.3 | Unknown | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
2. Contact from object | 2.g.d.0 | Other | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 2.4647 | 2.4544 | 2.4429 | # ignitions
2. Contact from object | 2.g.d.2 | Other | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.35327 | 0.32633 | 0.30104 | # ignitions
2. Contact from object | 2.g.d.3 | Other | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.54001 | 0.48792 | 0.44428 | # ignitions
2. Contact from object | 2.g.t.0 | Other | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.072848 | 0.072089 | 0.072089 | # ignitions
2. Contact from object | 2.g.t.2 | Other | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.07259 | 0.071543 | 0.070688 | # ignitions
2. Contact from object | 2.g.t.3 | Other | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.146 | 0.14473 | 0.14353 | # ignitions
3. Vegetation contact | 3.a.d.0 | Vegetation contact | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 1; Actual number of ignitions Q2: 3; Actual number of ignitions Q3: 2; Actual number of ignitions Q4: 1 | 8.19 | 8.1856 | 8.1707 | # ignitions
3. Vegetation contact | 3.a.d.2 | Vegetation contact | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 3; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 1 | 2.8666 | 2.749 | 2.6777 | # ignitions
3. Vegetation contact | 3.a.d.3 | Vegetation contact | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 1; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 1 | 2.9958 | 2.8223 | 2.7431 | # ignitions
3. Vegetation contact | 3.a.t.0 | Vegetation contact | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.035829 | 0.035829 | 0.035829 | # ignitions
3. Vegetation contact | 3.a.t.2 | Vegetation contact | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
3. Vegetation contact | 3.a.t.3 | Vegetation contact | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.035698 | 0.035363 | 0.035023 | # ignitions
4. Equipment / facility failure or damage | 4.a.d.0 | Anchor/guy | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.a.d.2 | Anchor/guy | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.a.d.3 | Anchor/guy | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.a.t.0 | Anchor/guy | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.a.t.2 | Anchor/guy | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.a.t.3 | Anchor/guy | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.b.d.0 | Capacitor bank | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 2; Actual number of ignitions Q4: 0 | 0.97497 | 0.97493 | 0.97485 | # ignitions
4. Equipment / facility failure or damage | 4.b.d.2 | Capacitor bank | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.b.d.3 | Capacitor bank | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.016904 | 0.015816 | 0.014216 | # ignitions
4. Equipment / facility failure or damage | 4.b.t.0 | Capacitor bank | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.062326 | 0.062326 | 0.062326 | # ignitions
4. Equipment / facility failure or damage | 4.b.t.2 | Capacitor bank | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.b.t.3 | Capacitor bank | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.c.d.0 | Conductor | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 2; Actual number of ignitions Q2: 8; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 1 | 12.2891 | 12.2587 | 12.2094 | # ignitions
4. Equipment / facility failure or damage | 4.c.d.2 | Conductor | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 1.2978 | 1.2301 | 1.1827 | # ignitions
4. Equipment / facility failure or damage | 4.c.d.3 | Conductor | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 1; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 3; Actual number of ignitions Q4: 1 | 4.4531 | 4.2812 | 4.1524 | # ignitions
4. Equipment / facility failure or damage | 4.c.t.0 | Conductor | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.c.t.2 | Conductor | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.c.t.3 | Conductor | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 0 | 0.28116 | 0.28116 | 0.28116 | # ignitions
4. Equipment / facility failure or damage | 4.d.d.0 | Connection device | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 2; Actual number of ignitions Q4: 0 | 4.0671 | 4.0567 | 4.041 | # ignitions
4. Equipment / facility failure or damage | 4.d.d.2 | Connection device | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.70331 | 0.68869 | 0.67858 | # ignitions
4. Equipment / facility failure or damage | 4.d.d.3 | Connection device | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 1 | 1.8469 | 1.8195 | 1.817 | # ignitions
4. Equipment / facility failure or damage | 4.d.t.0 | Connection device | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.031163 | 0.031163 | 0.031163 | # ignitions
4. Equipment / facility failure or damage | 4.d.t.2 | Connection device | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.d.t.3 | Connection device | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.e.d.0 | Crossarm | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.27276 | 0.27114 | 0.27035 | # ignitions
4. Equipment / facility failure or damage | 4.e.d.2 | Crossarm | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.e.d.3 | Crossarm | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.043915 | 0.036314 | 0.028716 | # ignitions
4. Equipment / facility failure or damage | 4.e.t.0 | Crossarm | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.031163 | 0.031163 | 0.031163 | # ignitions
4. Equipment / facility failure or damage | 4.e.t.2 | Crossarm | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.e.t.3 | Crossarm | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.f.d.0 | Fuse | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.74168 | 0.73996 | 0.73838 | # ignitions
4. Equipment / facility failure or damage | 4.f.d.2 | Fuse | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 0 | 0.29353 | 0.28706 | 0.27901 | # ignitions
4. Equipment / facility failure or damage | 4.f.d.3 | Fuse | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.022632 | 0.019882 | 0.016783 | # ignitions
4. Equipment / facility failure or damage | 4.f.t.0 | Fuse | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.f.t.2 | Fuse | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.f.t.3 | Fuse | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.g.d.0 | Cutout | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.g.d.2 | Cutout | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.g.d.3 | Cutout | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.g.t.0 | Cutout | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.g.t.2 | Cutout | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.g.t.3 | Cutout | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.h.d.0 | Insulator and brushing | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 1; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 1.0351 | 1.0327 | 1.0285 | # ignitions
4. Equipment / facility failure or damage | 4.h.d.2 | Insulator and brushing | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.39521 | 0.36612 | 0.34412 | # ignitions
4. Equipment / facility failure or damage | 4.h.d.3 | Insulator and brushing | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.38851 | 0.35562 | 0.32862 | # ignitions
4. Equipment / facility failure or damage | 4.h.t.0 | Insulator and brushing | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.29155 | 0.29155 | 0.29155 | # ignitions
4. Equipment / facility failure or damage | 4.h.t.2 | Insulator and brushing | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.h.t.3 | Insulator and brushing | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.29155 | 0.29155 | 0.29155 | # ignitions
4. Equipment / facility failure or damage | 4.i.d.0 | Lightning arrestor | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 0 | 1.381 | 1.3771 | 1.3724 | # ignitions
4. Equipment / facility failure or damage | 4.i.d.2 | Lightning arrestor | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.i.d.3 | Lightning arrestor | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.i.t.0 | Lightning arrestor | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.031163 | 0.031163 | 0.031163 | # ignitions
4. Equipment / facility failure or damage | 4.i.t.2 | Lightning arrestor | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.i.t.3 | Lightning arrestor | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.j.d.0 | Pole | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 1.0336 | 1.0317 | 1.029 | # ignitions
4. Equipment / facility failure or damage | 4.j.d.2 | Pole | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.022796 | 0.021857 | 0.020874 | # ignitions
4. Equipment / facility failure or damage | 4.j.d.3 | Pole | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.023125 | 0.021815 | 0.020222 | # ignitions
4. Equipment / facility failure or damage | 4.j.t.0 | Pole | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.j.t.2 | Pole | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.j.t.3 | Pole | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.k.d.0 | Recloser | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.k.d.2 | Recloser | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.k.d.3 | Recloser | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.k.t.0 | Recloser | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.k.t.2 | Recloser | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.k.t.3 | Recloser | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.l.d.0 | Relay | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.l.d.2 | Relay | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.l.d.3 | Relay | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.l.t.0 | Relay | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.l.t.2 | Relay | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.l.t.3 | Relay | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.m.d.0 | Sectionalizer | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.m.d.2 | Sectionalizer | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.m.d.3 | Sectionalizer | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.m.t.0 | Sectionalizer | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.m.t.2 | Sectionalizer | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.m.t.3 | Sectionalizer | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.n.d.0 | Splice | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 1; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.n.d.2 | Splice | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.n.d.3 | Splice | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.n.t.0 | Splice | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.n.t.2 | Splice | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.n.t.3 | Splice | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.o.d.0 | Switch | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 0 | 1.1693 | 1.1687 | 1.1676 | # ignitions
4. Equipment / facility failure or damage | 4.o.d.2 | Switch | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.o.d.3 | Switch | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 3; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.78235 | 0.78072 | 0.77287 | # ignitions
4. Equipment / facility failure or damage | 4.o.t.0 | Switch | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.o.t.2 | Switch | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.o.t.3 | Switch | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.p.d.0 | Tap | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.p.d.2 | Tap | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.p.d.3 | Tap | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.p.t.0 | Tap | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.p.t.2 | Tap | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.p.t.3 | Tap | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.q.d.0 | Tie wire | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.q.d.2 | Tie wire | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.q.d.3 | Tie wire | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.q.t.0 | Tie wire | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.q.t.2 | Tie wire | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.q.t.3 | Tie wire | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.r.d.0 | Transformer | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 1; Actual number of ignitions Q2: 2; Actual number of ignitions Q3: 2; Actual number of ignitions Q4: 3 | 11.1972 | 11.1459 | 11.0774 | # ignitions
4. Equipment / facility failure or damage | 4.r.d.2 | Transformer | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.58827 | 0.57257 | 0.5581 | # ignitions
4. Equipment / facility failure or damage | 4.r.d.3 | Transformer | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 0 | 1.0075 | 0.97448 | 0.92343 | # ignitions
4. Equipment / facility failure or damage | 4.r.t.0 | Transformer | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.r.t.2 | Transformer | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.r.t.3 | Transformer | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.s.d.0 | Voltage regulator/booster | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.s.d.2 | Voltage regulator/booster | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.s.d.3 | Voltage regulator/booster | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.s.t.0 | Voltage regulator/booster | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.s.t.2 | Voltage regulator/booster | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.s.t.3 | Voltage regulator/booster | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.t.d.0 | Unknown | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.t.d.2 | Unknown | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.t.d.3 | Unknown | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.t.t.0 | Unknown | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.t.t.2 | Unknown | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.t.t.3 | Unknown | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.u.d.0 | Other | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 1; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 0 | 3.6934 | 3.6846 | 3.6726 | # ignitions
4. Equipment / facility failure or damage | 4.u.d.2 | Other | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 1.1384 | 1.1282 | 1.1211 | # ignitions
4. Equipment / facility failure or damage | 4.u.d.3 | Other | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 0 | 1.2185 | 1.2017 | 1.1836 | # ignitions
4. Equipment / facility failure or damage | 4.u.t.0 | Other | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.39943 | 0.39943 | 0.39943 | # ignitions
4. Equipment / facility failure or damage | 4.u.t.2 | Other | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.u.t.3 | Other | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.074131 | 0.072555 | 0.070692 | # ignitions
5. Wire-to-wire contact | 5.a.d.0 | Wire-to-wire contact | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 1; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 2.267 | 2.2654 | 2.2604 | # ignitions
5. Wire-to-wire contact | 5.a.d.2 | Wire-to-wire contact | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.02363 | 0.023286 | 0.022276 | # ignitions
5. Wire-to-wire contact | 5.a.d.3 | Wire-to-wire contact | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 1; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.70582 | 0.69416 | 0.70047 | # ignitions
5. Wire-to-wire contact | 5.a.t.0 | Wire-to-wire contact | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
5. Wire-to-wire contact | 5.a.t.2 | Wire-to-wire contact | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
5. Wire-to-wire contact | 5.a.t.3 | Wire-to-wire contact | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
6. Contamination | 6.a.d.0 | Contamination | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.18824 | 0.18788 | 0.18736 | # ignitions
6. Contamination | 6.a.d.2 | Contamination | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.071003 | 0.07062 | 0.070322 | # ignitions
6. Contamination | 6.a.d.3 | Contamination | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
6. Contamination | 6.a.t.0 | Contamination | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.25816 | 0.25816 | 0.25816 | # ignitions
6. Contamination | 6.a.t.2 | Contamination | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
6. Contamination | 6.a.t.3 | Contamination | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.0081629 | 0.0081629 | 0.0081629 | # ignitions
7. Protective device operation | 7.a.d.0 | Protective device operation | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
7. Protective device operation | 7.a.d.2 | Protective device operation | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
7. Protective device operation | 7.a.d.3 | Protective device operation | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
7. Protective device operation | 7.a.t.0 | Protective device operation | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
7. Protective device operation | 7.a.t.2 | Protective device operation | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
7. Protective device operation | 7.a.t.3 | Protective device operation | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
8. Vandalism/theft | 8.a.d.0 | Vandalism/theft | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 1; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 1 | 3.5538 | 3.5512 | 3.5491 | # ignitions
8. Vandalism/theft | 8.a.d.2 | Vandalism/theft | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.0084123 | 0.008401 | 0.0083802 | # ignitions
8. Vandalism/theft | 8.a.d.3 | Vandalism/theft | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.35618 | 0.35561 | 0.35453 | # ignitions
8. Vandalism/theft | 8.a.t.0 | Vandalism/theft | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.0081629 | 0.0081629 | 0.0081629 | # ignitions
8. Vandalism/theft | 8.a.t.2 | Vandalism/theft | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
8. Vandalism/theft | 8.a.t.3 | Vandalism/theft | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
9. Lightning | 9.a.d.0 | Lightning | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
9. Lightning | 9.a.d.2 | Lightning | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
9. Lightning | 9.a.d.3 | Lightning | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
9. Lightning | 9.a.t.0 | Lightning | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
9. Lightning | 9.a.t.2 | Lightning | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
9. Lightning | 9.a.t.3 | Lightning | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
10. Unknown | 10.a.d.0 | Unknown | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 1 | 2.5339 | 2.5273 | 2.518 | # ignitions
10. Unknown | 10.a.d.2 | Unknown | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 0 | 0.75926 | 0.74806 | 0.73863 | # ignitions
10. Unknown | 10.a.d.3 | Unknown | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
10. Unknown | 10.a.t.0 | Unknown | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.068688 | 0.068688 | 0.068688 | # ignitions
10. Unknown | 10.a.t.2 | Unknown | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.37462 | 0.37462 | 0.37462 | # ignitions
10. Unknown | 10.a.t.3 | Unknown | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
11. Other | 11.a.d.0 | Other | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 2; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.5265 | 0.5265 | 0.5265 | # ignitions
11. Other | 11.a.d.2 | Other | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.6775 | 0.6775 | 0.6775 | # ignitions
11. Other | 11.a.d.3 | Other | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.30347 | 0.30347 | 0.30347 | # ignitions
11. Other | 11.a.t.0 | Other | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.0081629 | 0.0081629 | 0.0081629 | # ignitions
11. Other | 11.a.t.2 | Other | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
11. Other | 11.a.t.3 | Other | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions

## Table 7
Utility | Southern California Edison
Table No. | 7
Date Modified | 2023-02-01
[6 empty] | Actual | [15 empty] | Projected
Table 7: State of service territory and utility equipment | [5 empty] | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4
Metric type | # | Line Type | HFTD Tier | Area Type | WUI Status | 2022 | 2022 | 2022 | 2022 | 2023 | 2023 | 2023 | 2023 | 2024 | 2024 | 2024 | 2024 | 2025 | 2025 | 2025 | 2025 | 2023 | 2024 | 2025 | Unit(s) | Comments | Blank Meaning
1. Overhead circuit miles | 1.d.0.a.i | Distribution | Non-HFTD | Urban | WUI | Actual Q1: 3603; Actual Q2: 3601; Actual Q3: 3565; Actual Q4: 3552 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
1. Overhead circuit miles | 1.d.0.a.ii | Distribution | Non-HFTD | Urban | Non-WUI | Actual Q1: 13283; Actual Q2: 13280; Actual Q3: 13082; Actual Q4: 12996 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
1. Overhead circuit miles | 1.d.0.b.i | Distribution | Non-HFTD | Rural | WUI | Actual Q1: 2849; Actual Q2: 2851; Actual Q3: 2842; Actual Q4: 2843 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
1. Overhead circuit miles | 1.d.0.b.ii | Distribution | Non-HFTD | Rural | Non-WUI | Actual Q1: 6512; Actual Q2: 6511; Actual Q3: 6473; Actual Q4: 6464 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
1. Overhead circuit miles | 1.d.0.c.i | Distribution | Non-HFTD | Highly rural | WUI | Actual Q1: 474; Actual Q2: 474; Actual Q3: 473; Actual Q4: 473 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
1. Overhead circuit miles | 1.d.0.c.ii | Distribution | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 2328; Actual Q2: 2328; Actual Q3: 2328; Actual Q4: 2331 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
1. Overhead circuit miles | 1.d.2.a.i | Distribution | HFTD Tier 2 | Urban | WUI | Actual Q1: 598; Actual Q2: 597; Actual Q3: 592; Actual Q4: 589 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
1. Overhead circuit miles | 1.d.2.a.ii | Distribution | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: 424; Actual Q2: 423; Actual Q3: 412; Actual Q4: 406 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
1. Overhead circuit miles | 1.d.2.b.i | Distribution | HFTD Tier 2 | Rural | WUI | Actual Q1: 1071; Actual Q2: 1069; Actual Q3: 1061; Actual Q4: 1059 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
1. Overhead circuit miles | 1.d.2.b.ii | Distribution | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: 840; Actual Q2: 840; Actual Q3: 829; Actual Q4: 828 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
1. Overhead circuit miles | 1.d.2.c.i | Distribution | HFTD Tier 2 | Highly rural | WUI | Actual Q1: 223; Actual Q2: 223; Actual Q3: 223; Actual Q4: 222 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
1. Overhead circuit miles | 1.d.2.c.ii | Distribution | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 805; Actual Q2: 807; Actual Q3: 803; Actual Q4: 802 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
1. Overhead circuit miles | 1.d.3.a.i | Distribution | HFTD Tier 3 | Urban | WUI | Actual Q1: 764; Actual Q2: 763; Actual Q3: 761; Actual Q4: 760 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
1. Overhead circuit miles | 1.d.3.a.ii | Distribution | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: 169; Actual Q2: 169; Actual Q3: 169; Actual Q4: 168 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
1. Overhead circuit miles | 1.d.3.b.i | Distribution | HFTD Tier 3 | Rural | WUI | Actual Q1: 2619; Actual Q2: 2617; Actual Q3: 2611; Actual Q4: 2609 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
1. Overhead circuit miles | 1.d.3.b.ii | Distribution | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 1609; Actual Q2: 1610; Actual Q3: 1607; Actual Q4: 1600 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
1. Overhead circuit miles | 1.d.3.c.i | Distribution | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 148; Actual Q2: 148; Actual Q3: 148; Actual Q4: 148 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
1. Overhead circuit miles | 1.d.3.c.ii | Distribution | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 359; Actual Q2: 358; Actual Q3: 358; Actual Q4: 358 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
1. Overhead circuit miles | 1.t.0.a.i | Transmission | Non-HFTD | Urban | WUI | Actual Q1: 512; Actual Q2: 509; Actual Q3: 509; Actual Q4: 509 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
1. Overhead circuit miles | 1.t.0.a.ii | Transmission | Non-HFTD | Urban | Non-WUI | Actual Q1: 2779; Actual Q2: 2779; Actual Q3: 2770; Actual Q4: 2770 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
1. Overhead circuit miles | 1.t.0.b.i | Transmission | Non-HFTD | Rural | WUI | Actual Q1: 274; Actual Q2: 275; Actual Q3: 275; Actual Q4: 276 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
1. Overhead circuit miles | 1.t.0.b.ii | Transmission | Non-HFTD | Rural | Non-WUI | Actual Q1: 2361; Actual Q2: 2370; Actual Q3: 2372; Actual Q4: 2377 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
1. Overhead circuit miles | 1.t.0.c.i | Transmission | Non-HFTD | Highly rural | WUI | Actual Q1: 38; Actual Q2: 38; Actual Q3: 38; Actual Q4: 38 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
1. Overhead circuit miles | 1.t.0.c.ii | Transmission | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 2048; Actual Q2: 2048; Actual Q3: 2040; Actual Q4: 2040 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
1. Overhead circuit miles | 1.t.2.a.i | Transmission | HFTD Tier 2 | Urban | WUI | Actual Q1: 191; Actual Q2: 194; Actual Q3: 195; Actual Q4: 195 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
1. Overhead circuit miles | 1.t.2.a.ii | Transmission | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: 213; Actual Q2: 216; Actual Q3: 217; Actual Q4: 217 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
1. Overhead circuit miles | 1.t.2.b.i | Transmission | HFTD Tier 2 | Rural | WUI | Actual Q1: 251; Actual Q2: 253; Actual Q3: 253; Actual Q4: 253 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
1. Overhead circuit miles | 1.t.2.b.ii | Transmission | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: 719; Actual Q2: 724; Actual Q3: 724; Actual Q4: 723 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
1. Overhead circuit miles | 1.t.2.c.i | Transmission | HFTD Tier 2 | Highly rural | WUI | Actual Q1: 33; Actual Q2: 33; Actual Q3: 32; Actual Q4: 32 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
1. Overhead circuit miles | 1.t.2.c.ii | Transmission | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 554; Actual Q2: 554; Actual Q3: 555; Actual Q4: 553 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
1. Overhead circuit miles | 1.t.3.a.i | Transmission | HFTD Tier 3 | Urban | WUI | Actual Q1: 234; Actual Q2: 235; Actual Q3: 235; Actual Q4: 236 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
1. Overhead circuit miles | 1.t.3.a.ii | Transmission | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: 200; Actual Q2: 201; Actual Q3: 201; Actual Q4: 202 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
1. Overhead circuit miles | 1.t.3.b.i | Transmission | HFTD Tier 3 | Rural | WUI | Actual Q1: 415; Actual Q2: 419; Actual Q3: 420; Actual Q4: 420 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
1. Overhead circuit miles | 1.t.3.b.ii | Transmission | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 1260; Actual Q2: 1267; Actual Q3: 1267; Actual Q4: 1267 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
1. Overhead circuit miles | 1.t.3.c.i | Transmission | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 22; Actual Q2: 22; Actual Q3: 22; Actual Q4: 22 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
1. Overhead circuit miles | 1.t.3.c.ii | Transmission | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 243; Actual Q2: 250; Actual Q3: 250; Actual Q4: 250 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
2. Underground circuit miles | 2.d.0.a.i | Distribution | Non-HFTD | Urban | WUI | Actual Q1: 6438; Actual Q2: 6441; Actual Q3: 6444; Actual Q4: 6451 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
2. Underground circuit miles | 2.d.0.a.ii | Distribution | Non-HFTD | Urban | Non-WUI | Actual Q1: 13311; Actual Q2: 13320; Actual Q3: 13338; Actual Q4: 13353 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
2. Underground circuit miles | 2.d.0.b.i | Distribution | Non-HFTD | Rural | WUI | Actual Q1: 1676; Actual Q2: 1678; Actual Q3: 1681; Actual Q4: 1684 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
2. Underground circuit miles | 2.d.0.b.ii | Distribution | Non-HFTD | Rural | Non-WUI | Actual Q1: 2259; Actual Q2: 2269; Actual Q3: 2279; Actual Q4: 2287 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
2. Underground circuit miles | 2.d.0.c.i | Distribution | Non-HFTD | Highly rural | WUI | Actual Q1: 58; Actual Q2: 58; Actual Q3: 58; Actual Q4: 58 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
2. Underground circuit miles | 2.d.0.c.ii | Distribution | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 253; Actual Q2: 253; Actual Q3: 253; Actual Q4: 254 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
2. Underground circuit miles | 2.d.2.a.i | Distribution | HFTD Tier 2 | Urban | WUI | Actual Q1: 1140; Actual Q2: 1140; Actual Q3: 1141; Actual Q4: 1143 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
2. Underground circuit miles | 2.d.2.a.ii | Distribution | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: 631; Actual Q2: 632; Actual Q3: 633; Actual Q4: 635 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
2. Underground circuit miles | 2.d.2.b.i | Distribution | HFTD Tier 2 | Rural | WUI | Actual Q1: 730; Actual Q2: 730; Actual Q3: 734; Actual Q4: 736 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
2. Underground circuit miles | 2.d.2.b.ii | Distribution | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: 292; Actual Q2: 293; Actual Q3: 296; Actual Q4: 297 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
2. Underground circuit miles | 2.d.2.c.i | Distribution | HFTD Tier 2 | Highly rural | WUI | Actual Q1: 37; Actual Q2: 37; Actual Q3: 37; Actual Q4: 37 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
2. Underground circuit miles | 2.d.2.c.ii | Distribution | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 109; Actual Q2: 109; Actual Q3: 109; Actual Q4: 109 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
2. Underground circuit miles | 2.d.3.a.i | Distribution | HFTD Tier 3 | Urban | WUI | Actual Q1: 1881; Actual Q2: 1882; Actual Q3: 1883; Actual Q4: 1885 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
2. Underground circuit miles | 2.d.3.a.ii | Distribution | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: 277; Actual Q2: 278; Actual Q3: 278; Actual Q4: 280 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
2. Underground circuit miles | 2.d.3.b.i | Distribution | HFTD Tier 3 | Rural | WUI | Actual Q1: 1577; Actual Q2: 1581; Actual Q3: 1584; Actual Q4: 1591 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
2. Underground circuit miles | 2.d.3.b.ii | Distribution | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 420; Actual Q2: 423; Actual Q3: 426; Actual Q4: 427 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
2. Underground circuit miles | 2.d.3.c.i | Distribution | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 14; Actual Q2: 14; Actual Q3: 14; Actual Q4: 14 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
2. Underground circuit miles | 2.d.3.c.ii | Distribution | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 60; Actual Q2: 61; Actual Q3: 61; Actual Q4: 61 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
2. Underground circuit miles | 2.t.0.a.i | Transmission | Non-HFTD | Urban | WUI | Actual Q1: 15; Actual Q2: 15; Actual Q3: 15; Actual Q4: 15 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
2. Underground circuit miles | 2.t.0.a.ii | Transmission | Non-HFTD | Urban | Non-WUI | Actual Q1: 208; Actual Q2: 207; Actual Q3: 211; Actual Q4: 211 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
2. Underground circuit miles | 2.t.0.b.i | Transmission | Non-HFTD | Rural | WUI | [19 empty] | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades | bar: Actual Q1 to Actual Q4
2. Underground circuit miles | 2.t.0.b.ii | Transmission | Non-HFTD | Rural | Non-WUI | Actual Q1: 36; Actual Q2: 36; Actual Q3: 35; Actual Q4: 35 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
2. Underground circuit miles | 2.t.0.c.i | Transmission | Non-HFTD | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
2. Underground circuit miles | 2.t.0.c.ii | Transmission | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 18; Actual Q2: 19; Actual Q3: 19; Actual Q4: 19 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
2. Underground circuit miles | 2.t.2.a.i | Transmission | HFTD Tier 2 | Urban | WUI | Actual Q1: 5; Actual Q2: 5; Actual Q3: 5; Actual Q4: 5 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
2. Underground circuit miles | 2.t.2.a.ii | Transmission | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: 7; Actual Q2: 7; Actual Q3: 7; Actual Q4: 7 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
2. Underground circuit miles | 2.t.2.b.i | Transmission | HFTD Tier 2 | Rural | WUI | Actual Q1: 2; Actual Q2: 2; Actual Q3: 2; Actual Q4: 2 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
2. Underground circuit miles | 2.t.2.b.ii | Transmission | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: 6; Actual Q2: 6; Actual Q3: 6; Actual Q4: 6 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
2. Underground circuit miles | 2.t.2.c.i | Transmission | HFTD Tier 2 | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
2. Underground circuit miles | 2.t.2.c.ii | Transmission | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
2. Underground circuit miles | 2.t.3.a.i | Transmission | HFTD Tier 3 | Urban | WUI | Actual Q1: 12; Actual Q2: 12; Actual Q3: 11; Actual Q4: 12 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
2. Underground circuit miles | 2.t.3.a.ii | Transmission | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: 9; Actual Q2: 9; Actual Q3: 9; Actual Q4: 9 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
2. Underground circuit miles | 2.t.3.b.i | Transmission | HFTD Tier 3 | Rural | WUI | Actual Q1: 9; Actual Q2: 9; Actual Q3: 9; Actual Q4: 9 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
2. Underground circuit miles | 2.t.3.b.ii | Transmission | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 9; Actual Q2: 8; Actual Q3: 8; Actual Q4: 8 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
2. Underground circuit miles | 2.t.3.c.i | Transmission | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
2. Underground circuit miles | 2.t.3.c.ii | Transmission | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 |  |  |  | Circuit miles | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
3. Critical facilities | 3.0.a.i | N/A | Non-HFTD | Urban | WUI | Actual Q1: 8337; Actual Q2: 8337; Actual Q3: 8337; Actual Q4: 8337 |  |  |  | Number of critical facilities | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
3. Critical facilities | 3.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | Actual Q1: 34949; Actual Q2: 34949; Actual Q3: 34949; Actual Q4: 34949 |  |  |  | Number of critical facilities | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
3. Critical facilities | 3.0.b.i | N/A | Non-HFTD | Rural | WUI | Actual Q1: 2494; Actual Q2: 2494; Actual Q3: 2494; Actual Q4: 2494 |  |  |  | Number of critical facilities | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
3. Critical facilities | 3.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | Actual Q1: 4920; Actual Q2: 4920; Actual Q3: 4920; Actual Q4: 4920 |  |  |  | Number of critical facilities | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
3. Critical facilities | 3.0.c.i | N/A | Non-HFTD | Highly rural | WUI | Actual Q1: 195; Actual Q2: 195; Actual Q3: 195; Actual Q4: 195 |  |  |  | Number of critical facilities | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
3. Critical facilities | 3.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 907; Actual Q2: 907; Actual Q3: 907; Actual Q4: 907 |  |  |  | Number of critical facilities | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
3. Critical facilities | 3.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | Actual Q1: 1284; Actual Q2: 1284; Actual Q3: 1284; Actual Q4: 1284 |  |  |  | Number of critical facilities | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
3. Critical facilities | 3.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: 1075; Actual Q2: 1075; Actual Q3: 1075; Actual Q4: 1075 |  |  |  | Number of critical facilities | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
3. Critical facilities | 3.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | Actual Q1: 1036; Actual Q2: 1036; Actual Q3: 1036; Actual Q4: 1036 |  |  |  | Number of critical facilities | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
3. Critical facilities | 3.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: 656; Actual Q2: 656; Actual Q3: 656; Actual Q4: 656 |  |  |  | Number of critical facilities | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
3. Critical facilities | 3.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | Actual Q1: 150; Actual Q2: 150; Actual Q3: 150; Actual Q4: 150 |  |  |  | Number of critical facilities | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
3. Critical facilities | 3.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 371; Actual Q2: 371; Actual Q3: 371; Actual Q4: 371 |  |  |  | Number of critical facilities | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
3. Critical facilities | 3.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | Actual Q1: 2794; Actual Q2: 2794; Actual Q3: 2794; Actual Q4: 2794 |  |  |  | Number of critical facilities | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
3. Critical facilities | 3.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: 810; Actual Q2: 810; Actual Q3: 810; Actual Q4: 810 |  |  |  | Number of critical facilities | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
3. Critical facilities | 3.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | Actual Q1: 3002; Actual Q2: 3002; Actual Q3: 3002; Actual Q4: 3002 |  |  |  | Number of critical facilities | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
3. Critical facilities | 3.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 1349; Actual Q2: 1349; Actual Q3: 1349; Actual Q4: 1349 |  |  |  | Number of critical facilities | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
3. Critical facilities | 3.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 164; Actual Q2: 164; Actual Q3: 164; Actual Q4: 164 |  |  |  | Number of critical facilities | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
3. Critical facilities | 3.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 225; Actual Q2: 225; Actual Q3: 225; Actual Q4: 225 |  |  |  | Number of critical facilities | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
4. Residential customers | 4.0.a.i | N/A | Non-HFTD | Urban | WUI | Actual Q1: 845308; Actual Q2: 845308; Actual Q3: 845308; Actual Q4: 845308 |  |  |  | Number of residential customers | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
4. Residential customers | 4.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | Actual Q1: 2660413; Actual Q2: 2660413; Actual Q3: 2660413; Actual Q4: 2660413 |  |  |  | Number of residential customers | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
4. Residential customers | 4.0.b.i | N/A | Non-HFTD | Rural | WUI | Actual Q1: 170607; Actual Q2: 170607; Actual Q3: 170607; Actual Q4: 170607 |  |  |  | Number of residential customers | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
4. Residential customers | 4.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | Actual Q1: 84981; Actual Q2: 84981; Actual Q3: 84981; Actual Q4: 84981 |  |  |  | Number of residential customers | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
4. Residential customers | 4.0.c.i | N/A | Non-HFTD | Highly rural | WUI | Actual Q1: 8441; Actual Q2: 8441; Actual Q3: 8441; Actual Q4: 8441 |  |  |  | Number of residential customers | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
4. Residential customers | 4.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 3747; Actual Q2: 3747; Actual Q3: 3747; Actual Q4: 3747 |  |  |  | Number of residential customers | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
4. Residential customers | 4.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | Actual Q1: 107185; Actual Q2: 107185; Actual Q3: 107185; Actual Q4: 107185 |  |  |  | Number of residential customers | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
4. Residential customers | 4.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: 51117; Actual Q2: 51117; Actual Q3: 51117; Actual Q4: 51117 |  |  |  | Number of residential customers | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
4. Residential customers | 4.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | Actual Q1: 67095; Actual Q2: 67095; Actual Q3: 67095; Actual Q4: 67095 |  |  |  | Number of residential customers | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
4. Residential customers | 4.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: 9331; Actual Q2: 9331; Actual Q3: 9331; Actual Q4: 9331 |  |  |  | Number of residential customers | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
4. Residential customers | 4.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | Actual Q1: 5270; Actual Q2: 5270; Actual Q3: 5270; Actual Q4: 5270 |  |  |  | Number of residential customers | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
4. Residential customers | 4.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 2353; Actual Q2: 2353; Actual Q3: 2353; Actual Q4: 2353 |  |  |  | Number of residential customers | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
4. Residential customers | 4.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | Actual Q1: 225712; Actual Q2: 225712; Actual Q3: 225712; Actual Q4: 225712 |  |  |  | Number of residential customers | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
4. Residential customers | 4.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: 7586; Actual Q2: 7586; Actual Q3: 7586; Actual Q4: 7586 |  |  |  | Number of residential customers | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
4. Residential customers | 4.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | Actual Q1: 143222; Actual Q2: 143222; Actual Q3: 143222; Actual Q4: 143222 |  |  |  | Number of residential customers | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
4. Residential customers | 4.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 8436; Actual Q2: 8436; Actual Q3: 8436; Actual Q4: 8436 |  |  |  | Number of residential customers | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
4. Residential customers | 4.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 5955; Actual Q2: 5955; Actual Q3: 5955; Actual Q4: 5955 |  |  |  | Number of residential customers | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
4. Residential customers | 4.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 838; Actual Q2: 838; Actual Q3: 838; Actual Q4: 838 |  |  |  | Number of residential customers | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
5. Commercial customers | 5.0.a.i | N/A | Non-HFTD | Urban | WUI | Actual Q1: 66760; Actual Q2: 66760; Actual Q3: 66760; Actual Q4: 66760 |  |  |  | Number of commercial customers | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
5. Commercial customers | 5.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | Actual Q1: 398376; Actual Q2: 398376; Actual Q3: 398376; Actual Q4: 398376 |  |  |  | Number of commercial customers | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
5. Commercial customers | 5.0.b.i | N/A | Non-HFTD | Rural | WUI | Actual Q1: 14345; Actual Q2: 14345; Actual Q3: 14345; Actual Q4: 14345 |  |  |  | Number of commercial customers | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
5. Commercial customers | 5.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | Actual Q1: 45861; Actual Q2: 45861; Actual Q3: 45861; Actual Q4: 45861 |  |  |  | Number of commercial customers | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
5. Commercial customers | 5.0.c.i | N/A | Non-HFTD | Highly rural | WUI | Actual Q1: 809; Actual Q2: 809; Actual Q3: 809; Actual Q4: 809 |  |  |  | Number of commercial customers | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
5. Commercial customers | 5.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 2438; Actual Q2: 2438; Actual Q3: 2438; Actual Q4: 2438 |  |  |  | Number of commercial customers | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
5. Commercial customers | 5.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | Actual Q1: 6974; Actual Q2: 6974; Actual Q3: 6974; Actual Q4: 6974 |  |  |  | Number of commercial customers | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
5. Commercial customers | 5.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: 5929; Actual Q2: 5929; Actual Q3: 5929; Actual Q4: 5929 |  |  |  | Number of commercial customers | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
5. Commercial customers | 5.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | Actual Q1: 4667; Actual Q2: 4667; Actual Q3: 4667; Actual Q4: 4667 |  |  |  | Number of commercial customers | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
5. Commercial customers | 5.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: 2399; Actual Q2: 2399; Actual Q3: 2399; Actual Q4: 2399 |  |  |  | Number of commercial customers | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
5. Commercial customers | 5.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | Actual Q1: 581; Actual Q2: 581; Actual Q3: 581; Actual Q4: 581 |  |  |  | Number of commercial customers | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
5. Commercial customers | 5.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 1029; Actual Q2: 1029; Actual Q3: 1029; Actual Q4: 1029 |  |  |  | Number of commercial customers | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
5. Commercial customers | 5.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | Actual Q1: 20823; Actual Q2: 20823; Actual Q3: 20823; Actual Q4: 20823 |  |  |  | Number of commercial customers | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
5. Commercial customers | 5.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: 8464; Actual Q2: 8464; Actual Q3: 8464; Actual Q4: 8464 |  |  |  | Number of commercial customers | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
5. Commercial customers | 5.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | Actual Q1: 12968; Actual Q2: 12968; Actual Q3: 12968; Actual Q4: 12968 |  |  |  | Number of commercial customers | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
5. Commercial customers | 5.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 6472; Actual Q2: 6472; Actual Q3: 6472; Actual Q4: 6472 |  |  |  | Number of commercial customers | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
5. Commercial customers | 5.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 571; Actual Q2: 571; Actual Q3: 571; Actual Q4: 571 |  |  |  | Number of commercial customers | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
5. Commercial customers | 5.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 553; Actual Q2: 553; Actual Q3: 553; Actual Q4: 553 |  |  |  | Number of commercial customers | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
6. AFN customers | 6.0.a.i | N/A | Non-HFTD | Urban | WUI | Actual Q1: 299920; Actual Q2: 299920; Actual Q3: 299920; Actual Q4: 299920 |  |  |  | Number of customers belonging to access and functional needs populations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
6. AFN customers | 6.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | Actual Q1: 1034683; Actual Q2: 1034683; Actual Q3: 1034683; Actual Q4: 1034683 |  |  |  | Number of customers belonging to access and functional needs populations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
6. AFN customers | 6.0.b.i | N/A | Non-HFTD | Rural | WUI | Actual Q1: 60847; Actual Q2: 60847; Actual Q3: 60847; Actual Q4: 60847 |  |  |  | Number of customers belonging to access and functional needs populations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
6. AFN customers | 6.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | Actual Q1: 34044; Actual Q2: 34044; Actual Q3: 34044; Actual Q4: 34044 |  |  |  | Number of customers belonging to access and functional needs populations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
6. AFN customers | 6.0.c.i | N/A | Non-HFTD | Highly rural | WUI | Actual Q1: 2768; Actual Q2: 2768; Actual Q3: 2768; Actual Q4: 2768 |  |  |  | Number of customers belonging to access and functional needs populations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
6. AFN customers | 6.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 1083; Actual Q2: 1083; Actual Q3: 1083; Actual Q4: 1083 |  |  |  | Number of customers belonging to access and functional needs populations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
6. AFN customers | 6.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | Actual Q1: 25441; Actual Q2: 25441; Actual Q3: 25441; Actual Q4: 25441 |  |  |  | Number of customers belonging to access and functional needs populations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
6. AFN customers | 6.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: 9042; Actual Q2: 9042; Actual Q3: 9042; Actual Q4: 9042 |  |  |  | Number of customers belonging to access and functional needs populations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
6. AFN customers | 6.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | Actual Q1: 17107; Actual Q2: 17107; Actual Q3: 17107; Actual Q4: 17107 |  |  |  | Number of customers belonging to access and functional needs populations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
6. AFN customers | 6.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: 1892; Actual Q2: 1892; Actual Q3: 1892; Actual Q4: 1892 |  |  |  | Number of customers belonging to access and functional needs populations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
6. AFN customers | 6.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | Actual Q1: 917; Actual Q2: 917; Actual Q3: 917; Actual Q4: 917 |  |  |  | Number of customers belonging to access and functional needs populations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
6. AFN customers | 6.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 539; Actual Q2: 539; Actual Q3: 539; Actual Q4: 539 |  |  |  | Number of customers belonging to access and functional needs populations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
6. AFN customers | 6.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | Actual Q1: 45392; Actual Q2: 45392; Actual Q3: 45392; Actual Q4: 45392 |  |  |  | Number of customers belonging to access and functional needs populations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
6. AFN customers | 6.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: 1520; Actual Q2: 1520; Actual Q3: 1520; Actual Q4: 1520 |  |  |  | Number of customers belonging to access and functional needs populations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
6. AFN customers | 6.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | Actual Q1: 27152; Actual Q2: 27152; Actual Q3: 27152; Actual Q4: 27152 |  |  |  | Number of customers belonging to access and functional needs populations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
6. AFN customers | 6.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 1673; Actual Q2: 1673; Actual Q3: 1673; Actual Q4: 1673 |  |  |  | Number of customers belonging to access and functional needs populations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
6. AFN customers | 6.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 1703; Actual Q2: 1703; Actual Q3: 1703; Actual Q4: 1703 |  |  |  | Number of customers belonging to access and functional needs populations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
6. AFN customers | 6.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 214; Actual Q2: 214; Actual Q3: 214; Actual Q4: 214 |  |  |  | Number of customers belonging to access and functional needs populations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
7. Substations | 7.0.a.i | N/A | Non-HFTD | Urban | WUI | Actual Q1: 64; Actual Q2: 64; Actual Q3: 65; Actual Q4: 63 |  |  |  | Number of substations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
7. Substations | 7.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | Actual Q1: 358; Actual Q2: 358; Actual Q3: 398; Actual Q4: 374 |  |  |  | Number of substations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
7. Substations | 7.0.b.i | N/A | Non-HFTD | Rural | WUI | Actual Q1: 20; Actual Q2: 20; Actual Q3: 25; Actual Q4: 21 |  |  |  | Number of substations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
7. Substations | 7.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | Actual Q1: 169; Actual Q2: 169; Actual Q3: 209; Actual Q4: 218 |  |  |  | Number of substations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
7. Substations | 7.0.c.i | N/A | Non-HFTD | Highly rural | WUI | Actual Q1: 6; Actual Q2: 6; Actual Q3: 9; Actual Q4: 6 |  |  |  | Number of substations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
7. Substations | 7.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 81; Actual Q2: 81; Actual Q3: 100; Actual Q4: 103 |  |  |  | Number of substations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
7. Substations | 7.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | Actual Q1: 12; Actual Q2: 12; Actual Q3: 14; Actual Q4: 12 |  |  |  | Number of substations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
7. Substations | 7.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: 13; Actual Q2: 13; Actual Q3: 13; Actual Q4: 13 |  |  |  | Number of substations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
7. Substations | 7.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | Actual Q1: 10; Actual Q2: 10; Actual Q3: 15; Actual Q4: 10 |  |  |  | Number of substations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
7. Substations | 7.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: 32; Actual Q2: 32; Actual Q3: 38; Actual Q4: 37 |  |  |  | Number of substations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
7. Substations | 7.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | Actual Q1: 7; Actual Q2: 7; Actual Q3: 5; Actual Q4: 5 |  |  |  | Number of substations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
7. Substations | 7.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 36; Actual Q2: 36; Actual Q3: 32; Actual Q4: 29 |  |  |  | Number of substations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
7. Substations | 7.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | Actual Q1: 15; Actual Q2: 15; Actual Q3: 18; Actual Q4: 15 |  |  |  | Number of substations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
7. Substations | 7.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: 8; Actual Q2: 8; Actual Q3: 8; Actual Q4: 8 |  |  |  | Number of substations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
7. Substations | 7.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | Actual Q1: 23; Actual Q2: 23; Actual Q3: 48; Actual Q4: 23 |  |  |  | Number of substations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
7. Substations | 7.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 42; Actual Q2: 42; Actual Q3: 51; Actual Q4: 38 |  |  |  | Number of substations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
7. Substations | 7.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 1; Actual Q2: 1; Actual Q3: 2; Actual Q4: 1 |  |  |  | Number of substations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
7. Substations | 7.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 6; Actual Q2: 6; Actual Q3: 6; Actual Q4: 5 |  |  |  | Number of substations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
8. Weather stations | 8.0.a.i | N/A | Non-HFTD | Urban | WUI | Actual Q1: 36; Actual Q2: 50; Actual Q3: 27; Actual Q4: 11 |  |  |  | Number of weather stations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
8. Weather stations | 8.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | Actual Q1: 49; Actual Q2: 78; Actual Q3: 45; Actual Q4: 14 |  |  |  | Number of weather stations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
8. Weather stations | 8.0.b.i | N/A | Non-HFTD | Rural | WUI | Actual Q1: 48; Actual Q2: 52; Actual Q3: 27; Actual Q4: 22 |  |  |  | Number of weather stations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
8. Weather stations | 8.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | Actual Q1: 36; Actual Q2: 46; Actual Q3: 26; Actual Q4: 15 |  |  |  | Number of weather stations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
8. Weather stations | 8.0.c.i | N/A | Non-HFTD | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 |  |  |  | Number of weather stations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
8. Weather stations | 8.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 25; Actual Q2: 32; Actual Q3: 17; Actual Q4: 9 |  |  |  | Number of weather stations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
8. Weather stations | 8.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | Actual Q1: 217; Actual Q2: 228; Actual Q3: 114; Actual Q4: 111 |  |  |  | Number of weather stations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
8. Weather stations | 8.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: 167; Actual Q2: 174; Actual Q3: 90; Actual Q4: 88 |  |  |  | Number of weather stations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
8. Weather stations | 8.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | Actual Q1: 251; Actual Q2: 256; Actual Q3: 129; Actual Q4: 129 |  |  |  | Number of weather stations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
8. Weather stations | 8.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: 304; Actual Q2: 330; Actual Q3: 169; Actual Q4: 168 |  |  |  | Number of weather stations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
8. Weather stations | 8.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | Actual Q1: 43; Actual Q2: 46; Actual Q3: 24; Actual Q4: 23 |  |  |  | Number of weather stations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
8. Weather stations | 8.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 191; Actual Q2: 206; Actual Q3: 121; Actual Q4: 120 |  |  |  | Number of weather stations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
8. Weather stations | 8.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | Actual Q1: 252; Actual Q2: 256; Actual Q3: 129; Actual Q4: 128 |  |  |  | Number of weather stations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
8. Weather stations | 8.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: 98; Actual Q2: 106; Actual Q3: 57; Actual Q4: 52 |  |  |  | Number of weather stations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
8. Weather stations | 8.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | Actual Q1: 646; Actual Q2: 688; Actual Q3: 346; Actual Q4: 339 |  |  |  | Number of weather stations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
8. Weather stations | 8.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 637; Actual Q2: 676; Actual Q3: 344; Actual Q4: 342 |  |  |  | Number of weather stations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
8. Weather stations | 8.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 26; Actual Q2: 26; Actual Q3: 13; Actual Q4: 13 |  |  |  | Number of weather stations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades
8. Weather stations | 8.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 125; Actual Q2: 132; Actual Q3: 66; Actual Q4: 63 |  |  |  | Number of weather stations | It is important to note that GIS models are updated frequently to reflect changes within SCE’s service area and for data clean‐up. SCE does not have the ability to analyze and calculate information in previous years since the GIS data is dynamic and cannot be pulled retroactively. Accordingly, while SCE has provided data on a quarterly basis starting with 2022, SCE is still conducting quality control review of all the data and will correct any errors once its review is complete. | SCE does not track projections for these metrics, please see tables 8 and 9 for future additions/removals and upgrades

## Table 8
Utility | Southern California Edison |  |  |  |  | Notes:
Table No. | 8 |  |  |  |  | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV. Report net additions using positive numbers and net removals and undergrounding using negative numbers for circuit miles and numbers of substations. Only report changes expected within the target year.
Date Modified | 2023-02-01
[6 empty] | Actual | [15 empty] | Projected
Table 8: Location of utility equipment additions or removal | [5 empty] | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4
Metric type | # | Line Type | HFTD Tier | Area Type | WUI Status | 2022 | 2022 | 2022 | 2022 | 2023 | 2023 | 2023 | 2023 | 2024 | 2024 | 2024 | 2024 | 2025 | 2025 | 2025 | 2025 | 2023 | 2024 | 2025 | Unit(s) | Comments | Blank Meaning
1. Planned net addition (or removal) - overhead circuit miles | 1.d.0.a.i | Distribution | Non-HFTD | Urban | WUI | Actual Q4: 0 | 0 | 0 |  | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.d.0.a.ii | Distribution | Non-HFTD | Urban | Non-WUI | Actual Q4: 0 | 0 | 0.04 |  | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.d.0.b.i | Distribution | Non-HFTD | Rural | WUI | Actual Q4: 0 | 0 | 0.17 |  | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.d.0.b.ii | Distribution | Non-HFTD | Rural | Non-WUI | Actual Q4: 0 | 0 | 0 |  | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.d.0.c.i | Distribution | Non-HFTD | Highly rural | WUI | Actual Q4: 0 | 0 | 0 |  | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.d.0.c.ii | Distribution | Non-HFTD | Highly rural | Non-WUI | Actual Q4: 0 | 0 | 0 |  | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.d.2.a.i | Distribution | HFTD Tier 2 | Urban | WUI | Actual Q4: 0 | 0.01 | 1.15 |  | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.d.2.a.ii | Distribution | HFTD Tier 2 | Urban | Non-WUI | Actual Q4: 0 | 0 | 0.15 |  | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.d.2.b.i | Distribution | HFTD Tier 2 | Rural | WUI | Actual Q4: 0.31 | 0.06 | 2.05 |  | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.d.2.b.ii | Distribution | HFTD Tier 2 | Rural | Non-WUI | Actual Q4: 0 | 0 | 3.01 |  | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.d.2.c.i | Distribution | HFTD Tier 2 | Highly rural | WUI | Actual Q4: 0 | 0 | 0 |  | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.d.2.c.ii | Distribution | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q4: 0 | 0 | 0 |  | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.d.3.a.i | Distribution | HFTD Tier 3 | Urban | WUI | Actual Q4: 0.07 | 0.05 | 0.28 |  | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.d.3.a.ii | Distribution | HFTD Tier 3 | Urban | Non-WUI | Actual Q4: 0.02 | 0 | 0 |  | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.d.3.b.i | Distribution | HFTD Tier 3 | Rural | WUI | Actual Q4: 0.15 | 0.66 | 16.45 |  | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.d.3.b.ii | Distribution | HFTD Tier 3 | Rural | Non-WUI | Actual Q4: 2.14 | 0 | 2.69 |  | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.d.3.c.i | Distribution | HFTD Tier 3 | Highly rural | WUI | Actual Q4: 0 | 0 | 0 |  | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.d.3.c.ii | Distribution | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q4: 0 | 0 | 0 |  | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.t.0.a.i | Transmission | Non-HFTD | Urban | WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.t.0.a.ii | Transmission | Non-HFTD | Urban | Non-WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.t.0.b.i | Transmission | Non-HFTD | Rural | WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.t.0.b.ii | Transmission | Non-HFTD | Rural | Non-WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.t.0.c.i | Transmission | Non-HFTD | Highly rural | WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.t.0.c.ii | Transmission | Non-HFTD | Highly rural | Non-WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.t.2.a.i | Transmission | HFTD Tier 2 | Urban | WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.t.2.a.ii | Transmission | HFTD Tier 2 | Urban | Non-WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.t.2.b.i | Transmission | HFTD Tier 2 | Rural | WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.t.2.b.ii | Transmission | HFTD Tier 2 | Rural | Non-WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.t.2.c.i | Transmission | HFTD Tier 2 | Highly rural | WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.t.2.c.ii | Transmission | HFTD Tier 2 | Highly rural | Non-WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.t.3.a.i | Transmission | HFTD Tier 3 | Urban | WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.t.3.a.ii | Transmission | HFTD Tier 3 | Urban | Non-WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.t.3.b.i | Transmission | HFTD Tier 3 | Rural | WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.t.3.b.ii | Transmission | HFTD Tier 3 | Rural | Non-WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.t.3.c.i | Transmission | HFTD Tier 3 | Highly rural | WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.t.3.c.ii | Transmission | HFTD Tier 3 | Highly rural | Non-WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
2. Planned net addition (or removal) - underground circuit miles | 2.d.0.a.i | Distribution | Non-HFTD | Urban | WUI | Actual Q4: 0 | 0 | 0 |  | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.d.0.a.ii | Distribution | Non-HFTD | Urban | Non-WUI | Actual Q4: 0 | 0 | 0 |  | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.d.0.b.i | Distribution | Non-HFTD | Rural | WUI | Actual Q4: 0.03 | 0 | 0.04 |  | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
New Track Development | 2.d.0.b.ii | Distribution | Non-HFTD | Rural | Non-WUI | Actual Q4: 0 | 0 | 0 |  | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.d.0.c.i | Distribution | Non-HFTD | Highly rural | WUI | Actual Q4: 0 | 0 | 0 |  | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.d.0.c.ii | Distribution | Non-HFTD | Highly rural | Non-WUI | Actual Q4: 0 | 0 | 0 |  | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.d.2.a.i | Distribution | HFTD Tier 2 | Urban | WUI | Actual Q4: 0.14 | 0.79 | 3.3 |  | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.d.2.a.ii | Distribution | HFTD Tier 2 | Urban | Non-WUI | Actual Q4: 0 | 0 | 0.23 |  | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.d.2.b.i | Distribution | HFTD Tier 2 | Rural | WUI | Actual Q4: 1.11 | 0.37 | 4.81 |  | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.d.2.b.ii | Distribution | HFTD Tier 2 | Rural | Non-WUI | Actual Q4: 4.18 | 0 | 13.74 |  | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.d.2.c.i | Distribution | HFTD Tier 2 | Highly rural | WUI | Actual Q4: 0 | 0 | 0 |  | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.d.2.c.ii | Distribution | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q4: 0 | 0 | 0 |  | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.d.3.a.i | Distribution | HFTD Tier 3 | Urban | WUI | Actual Q4: 0.74 | 0.09 | 7.36 |  | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.d.3.a.ii | Distribution | HFTD Tier 3 | Urban | Non-WUI | Actual Q4: 0 | 0.13 | 0.09 |  | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.d.3.b.i | Distribution | HFTD Tier 3 | Rural | WUI | Actual Q4: 1.84 | 7.27 | 70.68 |  | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.d.3.b.ii | Distribution | HFTD Tier 3 | Rural | Non-WUI | Actual Q4: 8.74 | 2.05 | 22.86 |  | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.d.3.c.i | Distribution | HFTD Tier 3 | Highly rural | WUI | Actual Q4: 0 | 0 | 0 |  | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.d.3.c.ii | Distribution | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q4: 0 | 0 | 0 |  | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.t.0.a.i | Transmission | Non-HFTD | Urban | WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.t.0.a.ii | Transmission | Non-HFTD | Urban | Non-WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.t.0.b.i | Transmission | Non-HFTD | Rural | WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.t.0.b.ii | Transmission | Non-HFTD | Rural | Non-WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.t.0.c.i | Transmission | Non-HFTD | Highly rural | WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.t.0.c.ii | Transmission | Non-HFTD | Highly rural | Non-WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.t.2.a.i | Transmission | HFTD Tier 2 | Urban | WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.t.2.a.ii | Transmission | HFTD Tier 2 | Urban | Non-WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.t.2.b.i | Transmission | HFTD Tier 2 | Rural | WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.t.2.b.ii | Transmission | HFTD Tier 2 | Rural | Non-WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.t.2.c.i | Transmission | HFTD Tier 2 | Highly rural | WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.t.2.c.ii | Transmission | HFTD Tier 2 | Highly rural | Non-WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.t.3.a.i | Transmission | HFTD Tier 3 | Urban | WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.t.3.a.ii | Transmission | HFTD Tier 3 | Urban | Non-WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.t.3.b.i | Transmission | HFTD Tier 3 | Rural | WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.t.3.b.ii | Transmission | HFTD Tier 3 | Rural | Non-WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.t.3.c.i | Transmission | HFTD Tier 3 | Highly rural | WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.t.3.c.ii | Transmission | HFTD Tier 3 | Highly rural | Non-WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
3. Planned net addition (or removal) - Substations | 3.0.a.i | N/A | Non-HFTD | Urban | WUI | Actual Q4: 0 | 0 | -1 | 0 | Number of substations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 3.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | [16 empty] | -3 | 0 | -4 | Number of substations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability. | bar: Actual Q4
| 3.0.b.i | N/A | Non-HFTD | Rural | WUI | Actual Q4: 0 | 0 | 0 | 0 | Number of substations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 3.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | Actual Q4: 0 | 0 | 0 | 0 | Number of substations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 3.0.c.i | N/A | Non-HFTD | Highly rural | WUI | Actual Q4: 0 | 0 | 0 | 0 | Number of substations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 3.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | Actual Q4: 0 | 0 | 0 | 0 | Number of substations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 3.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | Actual Q4: 0 | 0 | 0 | 0 | Number of substations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 3.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | Actual Q4: 0 | 0 | 0 | 0 | Number of substations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 3.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | Actual Q4: 0 | 0 | 0 | 0 | Number of substations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 3.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | Actual Q4: 0 | 0 | 0 | 0 | Number of substations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 3.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | Actual Q4: 0 | 0 | 0 | 0 | Number of substations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 3.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q4: 0 | 0 | 0 | 0 | Number of substations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 3.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | Actual Q4: 0 | 0 | 0 | 0 | Number of substations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 3.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | Actual Q4: 0 | 0 | 0 | 0 | Number of substations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 3.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | Actual Q4: 0 | 0 | 0 | 0 | Number of substations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 3.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | Actual Q4: 0 | 0 | 0 | 0 | Number of substations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 3.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | Actual Q4: 0 | 0 | 0 | 0 | Number of substations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 3.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q4: 0 | 0 | 0 | 0 | Number of substations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
4. Planned net addition (or removal) - Weather stations | 4.0.a.i | N/A | Non-HFTD | Urban | WUI | Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 |  |  | 0 | Number of weather stations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 4.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 |  |  | 0 | Number of weather stations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 4.0.b.i | N/A | Non-HFTD | Rural | WUI | Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 |  |  | 0 | Number of weather stations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 4.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | Actual Q2: 0; Actual Q3: 0; Actual Q4: 1 |  |  | 0 | Number of weather stations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 4.0.c.i | N/A | Non-HFTD | Highly rural | WUI | Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 |  |  | 0 | Number of weather stations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 4.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 |  |  | 0 | Number of weather stations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 4.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | Actual Q2: 8; Actual Q3: 1; Actual Q4: 1 |  |  | 11 | Number of weather stations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 4.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | Actual Q2: 3; Actual Q3: 2; Actual Q4: 1 |  |  | 8 | Number of weather stations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 4.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | Actual Q2: 8; Actual Q3: 0; Actual Q4: 1 |  |  | 6 | Number of weather stations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 4.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | Actual Q2: 13; Actual Q3: 4; Actual Q4: 7 |  |  | 25 | Number of weather stations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 4.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | Actual Q2: 1; Actual Q3: 1; Actual Q4: 0 |  |  | 2 | Number of weather stations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 4.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q2: 18; Actual Q3: 8; Actual Q4: 4 |  |  | 22 | Number of weather stations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 4.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | Actual Q2: 6; Actual Q3: 0; Actual Q4: 1 |  |  | 9 | Number of weather stations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 4.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | Actual Q2: 2; Actual Q3: 1; Actual Q4: 1 |  |  | 1 | Number of weather stations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 4.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | Actual Q2: 27; Actual Q3: 1; Actual Q4: 1 |  |  | 16 | Number of weather stations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 4.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | Actual Q2: 26; Actual Q3: 3; Actual Q4: 5 |  |  | 62 | Number of weather stations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 4.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | Actual Q2: 1; Actual Q3: 0; Actual Q4: 0 |  |  | 0 | Number of weather stations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 4.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q2: 2; Actual Q3: 0; Actual Q4: 1 |  |  | 7 | Number of weather stations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.

## Table 9
Utility | Southern California Edison
Table No. | 9
Date Modified | 2023-02-01
[6 empty] | Actual | [15 empty] | Projected
Table 9: Location of utility infrastructure upgrades | [5 empty] | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4
Metric type | # | Line Type | HFTD Tier | Area Type | WUI Status | 2022 | 2022 | 2022 | 2022 | 2023 | 2023 | 2023 | 2023 | 2024 | 2024 | 2024 | 2024 | 2025 | 2025 | 2025 | 2025 | 2023 | 2024 | 2025 | Unit(s) | Comments | Blank Meaning
1. Number of overhead circuit miles planned for upgrade | 1.d.0.a.i | Distribution | Non-HFTD | Urban | WUI | Actual Q4: 0 | 2.6 | 19.08 | 1.92 | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.d.0.a.ii | Distribution | Non-HFTD | Urban | Non-WUI | Actual Q4: 2.38 | 1.2 | 78.65 | 87.22 | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.d.0.b.i | Distribution | Non-HFTD | Rural | WUI | Actual Q4: 0 | 0 | 3.99 | 0.35 | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.d.0.b.ii | Distribution | Non-HFTD | Rural | Non-WUI | Actual Q4: 0 | 0 | 5.34 | 0.04 | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.d.0.c.i | Distribution | Non-HFTD | Highly rural | WUI | Actual Q4: 0 | 0.12 | 0 | 0 | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.d.0.c.ii | Distribution | Non-HFTD | Highly rural | Non-WUI | Actual Q4: 0 | 2.93 | 0 | 0 | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.d.2.a.i | Distribution | HFTD Tier 2 | Urban | WUI | Actual Q4: 0 | 0.14 | 6.58 | 0.01 | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.d.2.a.ii | Distribution | HFTD Tier 2 | Urban | Non-WUI | Actual Q4: 0 | 0.09 | 0.25 | 3.25 | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.d.2.b.i | Distribution | HFTD Tier 2 | Rural | WUI | Actual Q4: 0 | 0 | 1.32 | 2.33 | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.d.2.b.ii | Distribution | HFTD Tier 2 | Rural | Non-WUI | Actual Q4: 0 | 0.68 | 0.1 | 0.24 | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.d.2.c.i | Distribution | HFTD Tier 2 | Highly rural | WUI | Actual Q4: 0 | 0 | 0 | 0 | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.d.2.c.ii | Distribution | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q4: 0 | 0 | 0 | 0 | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.d.3.a.i | Distribution | HFTD Tier 3 | Urban | WUI | Actual Q4: 0 | 0 | 0.31 | 0 | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.d.3.a.ii | Distribution | HFTD Tier 3 | Urban | Non-WUI | Actual Q4: 0 | 0 | 0 | 0 | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.d.3.b.i | Distribution | HFTD Tier 3 | Rural | WUI | Actual Q4: 0 | 0 | 4.47 | 0 | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.d.3.b.ii | Distribution | HFTD Tier 3 | Rural | Non-WUI | Actual Q4: 0 | 0 | 0 | 0 | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.d.3.c.i | Distribution | HFTD Tier 3 | Highly rural | WUI | Actual Q4: 0 | 0 | 0 | 0 | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.d.3.c.ii | Distribution | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q4: 0 | 0 | 0 | 0 | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.t.0.a.i | Transmission | Non-HFTD | Urban | WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.t.0.a.ii | Transmission | Non-HFTD | Urban | Non-WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.t.0.b.i | Transmission | Non-HFTD | Rural | WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.t.0.b.ii | Transmission | Non-HFTD | Rural | Non-WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.t.0.c.i | Transmission | Non-HFTD | Highly rural | WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.t.0.c.ii | Transmission | Non-HFTD | Highly rural | Non-WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.t.2.a.i | Transmission | HFTD Tier 2 | Urban | WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.t.2.a.ii | Transmission | HFTD Tier 2 | Urban | Non-WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.t.2.b.i | Transmission | HFTD Tier 2 | Rural | WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.t.2.b.ii | Transmission | HFTD Tier 2 | Rural | Non-WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.t.2.c.i | Transmission | HFTD Tier 2 | Highly rural | WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.t.2.c.ii | Transmission | HFTD Tier 2 | Highly rural | Non-WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.t.3.a.i | Transmission | HFTD Tier 3 | Urban | WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.t.3.a.ii | Transmission | HFTD Tier 3 | Urban | Non-WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.t.3.b.i | Transmission | HFTD Tier 3 | Rural | WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.t.3.b.ii | Transmission | HFTD Tier 3 | Rural | Non-WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.t.3.c.i | Transmission | HFTD Tier 3 | Highly rural | WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 1.t.3.c.ii | Transmission | HFTD Tier 3 | Highly rural | Non-WUI | [19 empty] | Circuit miles | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
2. Number of substations planned for upgrades | 2.0.a.i | N/A | Non-HFTD | Urban | WUI | Actual Q1: 1; Actual Q2: 9; Actual Q3: 1; Actual Q4: 6 | 12 | 14 | 7 | Number of substations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | Actual Q1: 1; Actual Q2: 17; Actual Q3: 1; Actual Q4: 17 | 48 | 34 | 23 | Number of substations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.0.b.i | N/A | Non-HFTD | Rural | WUI | Actual Q1: 0; Actual Q2: 2; Actual Q3: 0; Actual Q4: 0 | 3 | 1 | 1 | Number of substations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | Actual Q1: 0; Actual Q2: 4; Actual Q3: 1; Actual Q4: 3 | 13 | 6 | 6 | Number of substations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.0.c.i | N/A | Non-HFTD | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 1 | 1 | 0 | 0 | Number of substations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 0; Actual Q2: 2; Actual Q3: 0; Actual Q4: 0 | 4 | 5 | 0 | Number of substations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | Actual Q1: 0; Actual Q2: 2; Actual Q3: 0; Actual Q4: 0 | 1 | 1 | 0 | Number of substations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 1 | 0 | 0 | Number of substations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 2 | 1 | 0 | Number of substations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | Actual Q1: 0; Actual Q2: 2; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 5 | 0 | 0 | Number of substations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 4 | 3 | 2 | Number of substations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 1 | 0 | Number of substations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 1 | 0 | 2 | Number of substations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 2 | 3 | 2 | 0 | Number of substations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 2.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
3. Number of weather stations planned for (hardware) upgrades | 3.0.a.i | N/A | Non-HFTD | Urban | WUI | [19 empty] | Number of weather stations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 3.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | [19 empty] | Number of weather stations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 3.0.b.i | N/A | Non-HFTD | Rural | WUI | [19 empty] | Number of weather stations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 3.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | [19 empty] | Number of weather stations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 3.0.c.i | N/A | Non-HFTD | Highly rural | WUI | [19 empty] | Number of weather stations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 3.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | [19 empty] | Number of weather stations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 3.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | [19 empty] | Number of weather stations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 3.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | [19 empty] | Number of weather stations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 3.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | [19 empty] | Number of weather stations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 3.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | [19 empty] | Number of weather stations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 3.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | [19 empty] | Number of weather stations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 3.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | [19 empty] | Number of weather stations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 3.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | [19 empty] | Number of weather stations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 3.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | [19 empty] | Number of weather stations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 3.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | [19 empty] | Number of weather stations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 3.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | Actual Q2: 2 |  |  |  | Number of weather stations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 3.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | [19 empty] | Number of weather stations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.
| 3.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | [19 empty] | Number of weather stations | SCE provides equipment addition, removal and upgrade data where available. In some instances, the exact circuit and/or geospatial locational data and line lengths required are not available. This is due in part to detailed designs not yet completed for certain infrastructure projects. SCE is working internally to begin incorporating the geospatial data needed to provide these data points for future submissions. Furthermore, projections are subject to change due to operating constraints, changes in priority, and resource availability.

## Table 10
Utility | Southern California Edison
Table No. | 10
Date Modified | 2023-02-01
|  |  |  | Actual | [15 empty] | Projected
Table 10: Recent use of PSPS and other PSPS metrics |  |  |  | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Wind Warning Status | Metric name | 2022 | 2022 | 2022 | 2022 | 2023 | 2023 | 2023 | 2023 | 2024 | 2024 | 2024 | 2024 | 2025 | 2025 | 2025 | 2025 | 2023 | 2023 | 2023 | 2023 | 2024 | 2024 | 2024 | 2024 | 2025 | 2025 | 2025 | 2025 | Unit(s) | Comments | Blank Meaning
1. Recent use of PSPS and fast-trip | 1.a. | RFW only | Frequency of PSPS events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 1; Actual Q4: 0 | Number of instances where utility operating protocol requires de-energization of a circuit or portion thereof to reduce ignition probability, per year
| 1.a. | HWW only | Frequency of PSPS events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | Number of instances where utility operating protocol requires de-energization of a circuit or portion thereof to reduce ignition probability, per year
| 1.a. | HWW & RFW | Frequency of PSPS events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 2 | Number of instances where utility operating protocol requires de-energization of a circuit or portion thereof to reduce ignition probability, per year
| 1.a. | None | Frequency of PSPS events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Projected 1: 0; Projected 2: 0; Projected 3: 1; Projected 4: 5; Projected 1: 0; Projected 2: 0; Projected 3: 1; Projected 4: 5; Projected 1: 0; Projected 2: 0; Projected 3: 1; Projected 4: 5 | Number of instances where utility operating protocol requires de-energization of a circuit or portion thereof to reduce ignition probability, per year | SCE does not forecast a reduction in events from the 2020-2022 quarterly average as overall circuit scope reduction may not reduce event count. SCE does not forecast based on wind warning status.
| 1.b. | RFW only | Scope of PSPS events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 1; Actual Q4: 1 | Circuit-events, measured in number of events multiplied by number of circuits de-energized per year | SCE interprets this line item as de-energized circuit count. If one circuit is de-energized in subsequent events, the circuit count would be two.
| 1.b. | HWW only | Scope of PSPS events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | Circuit-events, measured in number of events multiplied by number of circuits de-energized per year | SCE interprets this line item as de-energized circuit count. If one circuit is de-energized in subsequent events, the circuit count would be two.
| 1.b. | HWW & RFW | Scope of PSPS events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 6 | Circuit-events, measured in number of events multiplied by number of circuits de-energized per year | SCE interprets this line item as de-energized circuit count. If one circuit is de-energized in subsequent events, the circuit count would be two.
| 1.b. | None | Scope of PSPS events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 1; Actual Q4: 4; Projected 1: 50; Projected 2: 0; Projected 3: 3; Projected 4: 172; Projected 1: 47; Projected 2: 0; Projected 3: 3; Projected 4: 162; Projected 1: 44; Projected 2: 0; Projected 3: 3; Projected 4: 152 | Circuit-events, measured in number of events multiplied by number of circuits de-energized per year | SCE interprets this line item as de-energized circuit count. If one circuit is de-energized in subsequent events, the circuit count would be two. Forecast reductions are derived from applying SCE's 2023 reduction forecast to 2020-2022 averages across each future year. SCE does not forecast based on wind warning status.
| 1.c. | RFW only | Duration of PSPS events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 2547; Actual Q4: 3325 | Customer hours per year
| 1.c. | HWW only | Duration of PSPS events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | Customer hours per year
| 1.c. | HWW & RFW | Duration of PSPS events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 66872 | Customer hours per year
| 1.c. | None | Duration of PSPS events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 2726; Actual Q4: 64728; Projected 1: 592702; Projected 2: 68; Projected 3: 2834; Projected 4: 1920968; Projected 1: 539359; Projected 2: 62; Projected 3: 2579; Projected 4: 1748080; Projected 1: 490816; Projected 2: 56; Projected 3: 2347; Projected 4: 1590753 | Customer hours per year | Forecast reductions are derived from applying SCE's 2023 reduction forecast to 2020-2022 averages across each future year. SCE does not forecast based on wind warning status.
| 1.d. | RFW only | Frequency of fast-trip events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 4 | Number of events | Fast curve (FC) events are outages where FC settings were enabled on HFRA circuits and not solely where outages were due to FC.
| 1.d. | HWW only | Frequency of fast-trip events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 10; Actual Q4: 17 | Number of events | Fast curve (FC) events are outages where FC settings were enabled on HFRA circuits and not solely where outages were due to FC.
| 1.d. | HWW & RFW | Frequency of fast-trip events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 6 | Number of events | Fast curve (FC) events are outages where FC settings were enabled on HFRA circuits and not solely where outages were due to FC.
| 1.d. | None | Frequency of fast-trip events (total) | Actual Q1: 4; Actual Q2: 273; Actual Q3: 379; Actual Q4: 130 | Number of events | Fast curve (FC) events are outages where FC settings were enabled HFRA circuits and not solely where outages were due to FC.
| 1.e | RFW only | Circuit mile days with fast-trip settings enabled (total) | Actual Q1: 0; Actual Q2: 462.68; Actual Q3: 36.34; Actual Q4: 194.9 | Circuit mile days
| 1.e | HWW only | Circuit mile days with fast-trip settings enabled (total) | Actual Q1: 0; Actual Q2: 12.5264; Actual Q3: 0; Actual Q4: 447.1312 | Circuit mile days
| 1.e | HWW & RFW | Circuit mile days with fast-trip settings enabled (total) | Actual Q1: 0; Actual Q2: 57.8032; Actual Q3: 0; Actual Q4: 20867.1564 | Circuit mile days
| 1.e | None | Circuit mile days with fast-trip settings enabled (total) | Actual Q1: 370442.6; Actual Q2: 6980491.075; Actual Q3: 12254678.52; Actual Q4: 6303994.996 | Circuit mile days
2. Customer hours of PSPS and other outages | 2.a. | N/A | Customer hours of planned outages including PSPS (total) | [28 empty] | Total customer hours of planned outages per year | SCE is currently unable to provide planned outage data metrics due to recent IT system implementation issues. SCE is actively investigating this issue and will provide the data when it is available. | Planned outage data is not currently available. Current estimate to restore Planned outage data is 2nd quarter 2023.
| 2.b. | N/A | Customer hours of unplanned outages, not including PSPS or fast-trip (total) | Actual Q1: 2931105; Actual Q2: 2064163; Actual Q3: 2564354; Actual Q4: 1837564 | Total customer hours of unplanned outages, not including PSPS or fast-trip, per year
| 2.c. | N/A | Customer hours of unplanned outages resulting from fast-trip | Actual Q1: 1190; Actual Q2: 734702; Actual Q3: 924951; Actual Q4: 356744 | Total customer hours of outages due to fast-trip per year | Fast curve (FC) events are outages where FC settings were enabled on HFRA circuits and not solely where outages were due to FC. Customer hours are customer hours of interruption (customers multiplied by their duration)
| 2.d. | N/A | System Average Interruption Duration Index (SAIDI) (including PSPS) | [28 empty] | SAIDI index value = sum of all interruptions in time period where each interruption is defined as sum(duration of interruption * # of customer interruptions) / Total number of customers served | SCE is currently unable to provide planned outage data metrics due to recent IT system implementation issues. SCE is actively investigating this issue and will provide the data when it is available. | SAIDI SAIFI required combined Planned/Unplanned outages. Planned outage data is not currently available. Current estimate to restore Planned outage data is 2nd quarter 2023.
| 2.e. | N/A | System Average Interruption Duration Index (SAIDI) (excluding PSPS) | [28 empty] | SAIDI index value = sum of all interruptions in time period where each interruption is defined as sum(duration of interruption * # of customer interruptions) / Total number of customers served | SCE is currently unable to provide planned outage data metrics due to recent IT system implementation issues. SCE is actively investigating this issue and will provide the data when it is available. | SAIDI SAIFI required combined Planned/Unplanned outages. Planned outage data is not currently available. Current estimate to restore Planned outage data is 2nd quarter 2023.
| 2.f. | N/A | System Average Interruption Frequency Index (SAIFI) (including PSPS) | [28 empty] | SAIFI index value = sum of all interruptions in time period where each interruption is defined as (total # of customer interruptions) / (total # of customers served) | SCE is currently unable to provide planned outage data metrics due to recent IT system implementation issues. SCE is actively investigating this issue and will provide the data when it is available. | SAIDI SAIFI required combined Planned/Unplanned outages. Planned outage data is not currently available. Current estimate to restore Planned outage data is 2nd quarter 2023.
| 2.g. | N/A | System Average Interruption Frequency Index (SAIFI) (excluding PSPS) | [28 empty] | SAIFI index value = sum of all interruptions in time period where each interruption is defined as (total # of customer interruptions) / (total # of customers served) | SCE is currently unable to provide planned outage data metrics due to recent IT system implementation issues. SCE is actively investigating this issue and will provide the data when it is available. | SAIDI SAIFI required combined Planned/Unplanned outages. Planned outage data is not currently available. Current estimate to restore Planned outage data is 2nd quarter 2023.
3. Critical infrastructure impacted by PSPS | 3.a. | N/A | Critical infrastructure impacted by PSPS | Actual Q1: 0; Actual Q2: 0; Actual Q3: 740.3; Actual Q4: 274 | Number of critical infrastructure (in accordance with D.19-05-042) locations impacted per hour multiplied by hours offline per year
4. Community outreach of PSPS metrics | 4.a. | N/A | # of customers impacted by PSPS | Actual Q1: 0; Actual Q2: 0; Actual Q3: 209; Actual Q4: 15568; Projected 1: 32966; Projected 2: 22; Projected 3: 138; Projected 4: 93235; Projected 1: 28021; Projected 2: 19; Projected 3: 118; Projected 4: 79250; Projected 1: 23818; Projected 2: 16; Projected 3: 100; Projected 4: 67363 | # of customers impacted by PSPS (if multiple PSPS events impact the same customer, count each event as a separate customer) | Forecast reductions are derived from applying SCE's 2023 reduction forecast to 2020-2022 averages across each future year. SCE does not forecast based on wind warning status.
| 4.b. | N/A | # of medical baseline customers impacted by PSPS | Actual Q1: 0; Actual Q2: 0; Actual Q3: 4; Actual Q4: 747 | # of customers impacted by PSPS (if multiple PSPS events impact the same customer, count each event as a separate customer)
| 4.c. | N/A | # of customers notified prior to initiation of PSPS event | Actual Q1: 0; Actual Q2: 0; Actual Q3: 187; Actual Q4: 57533 | # of customers notified of PSPS event prior to initiation (if multiple PSPS events impact the same customer, count each event in which customer was notified as a separate customer) | This number is the total number of customers in-scope for a potential PSPS de-energization.
| 4.d. | N/A | # of medical baseline customers notified prior to initiation of PSPS event | Actual Q1: 0; Actual Q2: 0; Actual Q3: 4; Actual Q4: 1993 | # of customers notified of PSPS event prior to initiation (if multiple PSPS events impact the same customer, count each event in which customer was notified as a separate customer) | This number is the total number of MBL customers in-scope for a potential PSPS de-energization.
| 4.e. | N/A | # of customers notified prior to a PSPS event impacting them | Actual Q1: 0; Actual Q2: 0; Actual Q3: 187; Actual Q4: 10997 | # of customers impacted customers who were notified prior to PSPS initiation (if multiple PSPS events impact the same customer, count each event in which customer was notified as a separate customer) | This number is the total number of customers impacted (de-energized) by a PSPS event. NOTE: This is a subset number of K40.
| 4.f. | N/A | # of medical baseline customers notified prior to a PSPS event impacting them | Actual Q1: 0; Actual Q2: 0; Actual Q3: 4; Actual Q4: 563 | # of customers impacted customers who were notified prior to PSPS initiation (if multiple PSPS events impact the same customer, count each event in which customer was notified as a separate customer) | This number is the total number of MBL customers impacted (de-energized) by a PSPS event. NOTE: This is a subset number of K41.
5. Other PSPS metrics | 5.a. | N/A | Number of PSPS events in which a notification was sent but no de-energization occurred | Actual Q1: 0; Actual Q2: 1; Actual Q3: 1; Actual Q4: 1 | Number of events
| 5.b. | N/A | Average number of customers located on de-energized circuit | Actual Q1: 0; Actual Q2: 0; Actual Q3: 209; Actual Q4: 17757 | Number of customers | This should be total customers de-energized, non-unique
| 5.c. | N/A | Customer hours of PSPS per RFW OH circuit mile day | Actual Q1: 0; Actual Q2: 0; Actual Q3: 254; Actual Q4: 4139 | =1.c. / RFW OH circuit mile days in time period
|  | N/A | Customer hours of PSPS per HWW OH circuit mile day | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 8462 | =1.c. / HWW OH circuit mile days in time period
|  | N/A | Customer hours of PSPS per high FPIOH circuit mile day | Actual Q1: 0; Actual Q2: 0; Actual Q3: 3; Actual Q4: 5085 | =1.c. / FPI OH circuit mile days in time period
| 5.d. | N/A | Median time between de-energization, due to PSPS, and inspection of a circuit segment | Actual Q1: 0; Actual Q2: 0; Actual Q3: 8.68; Actual Q4: 9.39 | Time between de-energization and inspection on a circuit-segment basis in hours | De-en to prep-to-restore time (=MEDIAN,[ARRAY])
| 5.e. | N/A | 95 percentile of time between de-energization, due to PSPS, and inspection of a circuit segment | Actual Q1: 0; Actual Q2: 0; Actual Q3: 9.58; Actual Q4: 17.58 | Time between de-energization and inspection on a circuit-segment basis in hours | De-en to prep-to-restore time (=PERCENTILE.INC,[ARRAY])
| 5.f. | N/A | Median time between de-energization, due to fast-trip, and inspection of a circuit segment | Actual Q1: 2.71; Actual Q2: 5.77; Actual Q3: 5.4; Actual Q4: 3.3 | Time between de-energization and inspection on a circuit-segment basis in hours | Fast curve (FC) events are outages where FC settings were enabled on HFRA circuits and not solely where outages were due to FC. Median time of entire outage durations instead of inspection on circuit-segment
| 5.g. | N/A | 95 percentile of time between de-energization, due to fast-trip, and inspection of a circuit segment | Actual Q2: 29.97; Actual Q3: 31.89; Actual Q4: 22.52 | Time between de-energization and inspection on a circuit-segment basis in hours | Fast curve (FC) events are outages where FC settings were enabled on HFRA circuits and not solely where outages were due to FC. 95th percentile of entire outage durations instead of inspection on circuit-segment. 5% of durations are above value
| 5.h. | N/A | Number of risk events occurring on a de-energized circuit | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 1 | Number of risk events

## Table 11
Utility | Southern California Edison | Notes:
Table No. | 11 | Territory spend refers to the sum total of initiative spending across all areas, including HFTDs. HFTD spend refers to initiative spending applied to HFTDs, and is a subset of territory spend.
Date Modified | 2023-02-01 | CAPEX = Capital expenditure; OPEX = Operating expenditure.
|  | As data is submitted each reporting period, replace projections for the current reporting period with actuals. | [9 empty] | Actual | [15 empty] | Projected
The units for the spend data are thousands of dollars.
Table 11: Mitigation initiative financials | [11 empty] | CAPEX ($ thousands) |  | OPEX ($ thousands) |  | CAPEX ($ thousands) |  | OPEX ($ thousands) |  | CAPEX ($ thousands) |  | OPEX ($ thousands) |  | CAPEX ($ thousands) |  | OPEX ($ thousands) |  | CAPEX ($ thousands) |  | OPEX ($ thousands) |  | CAPEX ($ thousands) |  | OPEX ($ thousands) |  | CAPEX ($ thousands) |  | OPEX ($ thousands)
[12 empty] | Territory | HFTD | Territory | HFTD | Territory | HFTD | Territory | HFTD | Territory | HFTD | Territory | HFTD | Territory | HFTD | Territory | HFTD | Territory | HFTD | Territory | HFTD | Territory | HFTD | Territory | HFTD | Territory | HFTD | Territory | HFTD
WMPInitiativeCategory | WMPInitiativeActivity | UtilityInitiativeTrackingID | Primary driver targeted | Secondary driver targeted | Year initiated | If existing: most recent proceeding that has reviewed program | If new: memorandum account | Current compliance status - In / exceeding compliance with regulations | Associated rule(s) - if multiple, separate by semi-colon - ";" | If spend not disaggregated by category, note spend category or mark general operations | Comments | 2019 |  |  |  | 2020 |  |  |  | 2021 |  |  |  | 2022 |  |  |  | 2023 |  |  |  | 2024 |  |  |  | 2025 |  |  |  | Blank Meaning
Community Outreach and Engagement | Public outreach and education awareness program | DEP-1.2, DEP-4 |  |  | 2018 | 2021 GRC | [5 empty] | 0 | 0 | 4619.4442 | 4619.4442 | 0 | 0 | 5631.4495 | 5631.4495 | 0 | 0 | 9966.8437 | 9966.8437 | 0 | 0 | 11491.8888 | 11491.8888 | 0 | 0 | 14920.5266 | 14920.5266 | 0 | 0 | 14596.2014 | 14596.2014 | 0 | 0 | 14701.0467 | 14701.0467
Community Outreach and Engagement | Engagement with access and functional needs populations | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2010.1689 | 2010.1689 | 0 | 0 | 2048.8315 | 2048.8315 | 0 | 0 | 2088.5971 | 2088.5971
Community Outreach and Engagement | Collaboration on local wildfire mitigation planning | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Community Outreach and Engagement | Best practice sharing with other utilities | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency Preparedness | Emergency preparedness plan | DEP-2 |  |  | 2018 | 2021 GRC | [5 empty] | 0 | 0 | 7219.2467 | 7219.2467 | 0 | 0 | 9550.4243 | 9550.4243 | 11217.1415 | 11217.1415 | 15188.5218 | 15188.5218 | 0 | 0 | 9286.1932 | 9286.1932 | 0 | 0 | 15626.645 | 15626.645 | 0 | 0 | 13069.4328 | 13069.4328 | 0 | 0 | 13877.2942 | 13877.2942
Emergency Preparedness | External collaboration and coordination | DEP-5 |  |  | 2020 | 2021 GRC | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2158 | 2158 | 0 | 0 | 17545 | 17545 | 0 | 0 | 18200.35 | 18200.35 | 0 | 0 | 35000 | 35000 | 0 | 0 | 35000 | 35000 | 0 | 0 | 35000 | 35000
Emergency Preparedness | Public emergency communication strategy | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13210.0724 | 13210.0724 | 5664.6949 | 5664.6949 | 12101.0472 | 12101.0472 | 6530.528 | 6530.528 | 6502.7064 | 6502.7064 | 6580.523 | 6580.523 | 4060.9564 | 4060.9564 | 4954.923 | 4954.923
Emergency Preparedness | Preparedness and planning for service restoration | [10 empty] | 1181 | 1181 | 9414.0643 | 9414.0643 | 1796.1108 | 1796.1108 | 5327.909 | 5327.909 | 9340.933 | 9340.933 | 3529.6374 | 3529.6374 | 0 | 0 | 1379.4212 | 1379.4212 | 0 | 0 | 7472.8467 | 7472.8467 | 0 | 0 | 7698.2861 | 7698.2861 | 0 | 0 | 8121.5813 | 8121.5813
Emergency Preparedness | Customer support in wildfire and PSPS emergencies | PSPS-2, PSPS-3 |  |  | 2018 | 2021 GRC | [5 empty] | 585 | 585 | 1916.954 | 1916.954 | 6843.2439 | 6843.2439 | 11096.3629 | 11096.3629 | 3284.8591 | 3284.8591 | 29807.4054 | 29807.4054 | 5127.464 | 5127.464 | 18316.4034 | 18316.4034 | 5402.5095 | 5402.5095 | 29284.2712 | 29284.2712 | 203.2096 | 203.2096 | 25479.2155 | 25479.2155 | 609.1435 | 609.1435 | 27719.0639 | 27719.0639
Grid Design, Operations, and Maintenance | Covered conductor installation | SH-1, SH-14, SH-16 | Wire-to-wire contact | Contact from object | 2018 | 2021 GRC | [5 empty] | 239911 | 239911 | 0 | 0 | 546151.289 | 546151.289 | 0 | 0 | 897599.925 | 897599.925 | 544.928 | 544.928 | 791737.321 | 791737.321 | 1410.9025 | 1410.9025 | 897276.4647 | 897276.4647 | 857.0888 | 857.0888 | 843489.556 | 843489.556 | 872.6131 | 872.6131 | 628225.2809 | 628225.2809 | 898.6881 | 898.6881
Grid Design, Operations, and Maintenance | Other grid topology improvements to minimize risk of ignitions | SH-5, SH-6, SH-15 | Equipment failure | Contact from object | 2018 | 2021 GRC | [5 empty] | 11951 | 11951 | 419.7767 | 419.7767 | 15652.317 | 15652.317 | 64.5894 | 64.5894 | 8080.8071 | 8080.8071 | 146.0674 | 146.0674 | 3028.6486 | 3028.6486 | 1369.3512 | 1369.3512 | 7789.464 | 7789.464 | 6587.8019 | 6587.8019 | 4531.5688 | 4531.5688 | 1859.3015 | 1859.3015 | 9306.6221 | 9306.6221 | 1676.5649 | 1676.5649
Grid Design, Operations, and Maintenance | Other grid topology improvements to mitigate or reduce PSPS events | SH-4, SH-6, SH-14 | Equipment failure | Wire-to-wire contact | 2018 | 2021 GRC | [5 empty] | 70298 | 70298 | 258.1237 | 258.1237 | 8955.266 | 8955.266 | 3815.9816 | 3815.9816 | -386.8827 | -386.8827 | 35.8273 | 35.8273 | 23294.134 | 23294.134 | 3978.2626 | 3978.2626 | 4540.6995 | 4540.6995 | 3396.9985 | 3396.9985 | 4896.7466 | 4896.7466 | 4009.3694 | 4009.3694 | 4376.3478 | 4376.3478 | 4122.772 | 4122.772
Grid Design, Operations, and Maintenance | Other technologies and systems not listed above | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Undergrounding of electric lines and/or equipment | SH-2 | Contact from object | Wire-to-wire contact | 2019 | 2021 GRC | [5 empty] | 0 | 0 | 0 | 0 | 961.3883 | 961.3883 | 0 | 0 | 6585.8 | 6585.8 | 0 | 0 | 29704.2722 | 29704.2722 | 0 | 0 | 27962.4622 | 27962.4622 | 1340.5609 | 1340.5609 | 60897.0168 | 60897.0168 | 0 | 0 | 317077.8319 | 317077.8319 | 0 | 0
Grid Design, Operations, and Maintenance | Distribution pole replacements and reinforcements | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 723 | 723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Transmission pole/tower replacements and reinforcements | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Traditional overhead hardening | SH-10 | Contact from object | Wire-to-wire contact | 2018 | 2021 GRC | [5 empty] | 9378 | 9378 | 0 | 0 | 9653.5501 | 9653.5501 | 0 | 0 | 21939.7977 | 21939.7977 | 0 | 0 | 16835.2163 | 16835.2163 | 0 | 0 | 16696.7356 | 16696.7356 | 0 | 0 | 18202.4373 | 18202.4373 | 0 | 0 | 10569.5167 | 10569.5167 | 0 | 0
Grid Design, Operations, and Maintenance | Emerging grid hardening technology installations and pilots | SH-17, SH-18 | Contact from object | Equipment failure | 2018 | 2021 GRC | [5 empty] | 0 | 0 | 0 | 0 | 1854.5692 | 1854.5692 | 0 | 0 | 2707.16 | 2707.16 | 0 | 0 | 12035.799 | 12035.799 | 0 | 0 | 21175.7675 | 21175.7675 | 250 | 250 | 35878.1592 | 35878.1592 | 350 | 350 | 45796.0702 | 45796.0702 | 500 | 500
Grid Design, Operations, and Maintenance | Microgrids | SH-12 |  |  | 2020 | 2021 GRC | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Installation of system automation equipment |  | Contact from object | Equipment failure | 2018 | 2021 GRC | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2417.0831 | 0 | 0 | 0 | 2583.6406 | 0 | 0 | 0 | 2629.6186 | 0 | 0 | 0 | 1529.5106 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Line removals (in HFTD) | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129.7392 | 129.7392 | 0 | 0 | 130.2861 | 130.2861 | 0 | 0 | 166.0583 | 166.0583
Grid Design, Operations, and Maintenance | Asset inspections | IN-1.1, IN-1.2, IN-3, IN-4, IN-9 | Equipment failure | Contact from object | 2017 | 2021 GRC | [5 empty] | 282982 | 282982 | 354246.2778 | 296932.2778 | 121153.2787 | 121153.2787 | 225514.8033 | 158706.8033 | 98816.1884 | 98816.1884 | 178929.4706 | 110563.4706 | 0 | 0 | 124771.1925 | 51279.1126 | 0 | 0 | 137845.6705 | 53662.3654 | 0 | 0 | 139889.3929 | 52339.767 | 0 | 0 | 142187.4789 | 53875.9847
Grid Design, Operations, and Maintenance | Equipment inspections, maintenance, and repair | IN-1.1, IN-1.2, IN-5, IN-9 | Equipment failure | Contact from object | 2018 | 2021 GRC | [5 empty] | 461728 | 0 | 28980.5703 | 642.6569 | 380116 | 0 | 23067.5779 | 402.545 | 600166 | 0 | 11131.9386 | 149.3921 | 777990.792 | 101072.5531 | 59135.2663 | 50433.3382 | 734673.7227 | 121075.7227 | 210811.869 | 80004.869 | 600615.9109 | 137532.9109 | 219371.0786 | 84009.0786 | 448019.981 | 135864.981 | 92200.8908 | 86124.8908
Grid Design, Operations, and Maintenance | Asset management and inspection enterprise system(s) | DG-1, IN-8 |  |  | 2021 | 2021 GRC | [5 empty] | 13391 | 13391 | 1978.5651 | 1978.5651 | 28718.5992 | 28718.5992 | 14972.098 | 14972.098 | 18586.3693 | 18586.3693 | 3727.0452 | 3727.0452 | 21981.1596 | 21981.1596 | 6191.9582 | 6191.9582 | 15845.791 | 15845.791 | 6389.3436 | 6389.3436 | 9909.6095 | 9909.6095 | 5845.3828 | 5845.3828 | 4824.648 | 4824.648 | 5924.5923 | 5924.5923
Grid Design, Operations, and Maintenance | Quality assurance / quality control | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Open work orders | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Equipment Settings to Reduce Wildfire Risk (Grid Ops) | [10 empty] | 1488 | 0 | 0 | 0 | 957 | 0 | 0 | 0 | 2239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Grid Response Procedures and Notifications (Grid Ops) | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3246.2032 | 3246.2032 | 0 | 0 | 956.0878 | 956.0878 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Personnel Work Procedures and Training in Conditions of Elevated Fire Risk (Grid Ops) | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Workforce Planning | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214.4713 | 214.4713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Overview of the Service Territory | Environmental compliance and permitting | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20598.7345 | 20598.7345 | 0 | 0 | 38795.459 | 38795.459 | 0 | 0 | 41410.1563 | 41410.1563 | 0 | 0 | 46341.3738 | 46341.3738 | 0 | 0 | 48402.2851 | 48402.2851
Risk Methodology and Assessment | Risk Methodology and Assessment | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137.2665 | 137.2665
Situational Awareness and Forecasting | Environmental monitoring systems | SA-1, SA-8 |  |  | 2018 | 2021 GRC | [5 empty] | 4282 | 4282 | 3489.9124 | 3489.9124 | 7508.8599 | 7508.8599 | 3820.6021 | 3820.6021 | 5607.2372 | 5607.2372 | 5172.1206 | 5172.1206 | 4242.9726 | 4242.9726 | 4327.9919 | 4327.9919 | 6736.688 | 6736.688 | 8351.7318 | 8351.7318 | 1171.3343 | 1171.3343 | 9718.7062 | 9718.7062 | 447.9127 | 447.9127 | 11541.6158 | 11541.6158
Situational Awareness and Forecasting | Grid monitoring systems | SA-11, SH-8 | Equipment failure for SH-8 | Vandalism / Theft for SH-8 | 2019 | 2021 GRC | [5 empty] | 3445 | 3445 | 154.0196 | 154.0196 | 260.4045 | 260.4045 | 339.8448 | 339.8448 | 8362.0962 | 8362.0962 | 1080.6121 | 1080.6121 | 4392.4706 | 4392.4706 | 1767.047 | 1767.047 | 3527.9507 | 3527.9507 | 1489.6 | 1489.6 | 3521.5051 | 3521.5051 | 1327.1 | 1327.1 | 14758.104 | 14758.104 | 853.2 | 853.2
Situational Awareness and Forecasting | Ignition detection systems | SA-8, SA-10 |  |  | 2019 | 2021 GRC | [5 empty] | 970 | 970 | 469.0158 | 469.0158 | 94.0863 | 94.0863 | 2235.2265 | 2235.2265 | 0 | 0 | 2993.755 | 2993.755 | 75.3193 | 75.3193 | 3231.2059 | 3231.2059 | 263.656 | 263.656 | 5237.556 | 5237.556 | 131 | 131 | 5724.087 | 5724.087 | 0 | 0 | 5775.965 | 5775.965
Situational Awareness and Forecasting | Weather forecasting | SA-3 |  |  | 2018 | 2021 GRC | [5 empty] | 6486.703 | 6486.703 | 1384.3314 | 1384.3314 | 4105.9963 | 4105.9963 | 1657.6793 | 1657.6793 | 3500.3805 | 3500.3805 | 3014.4564 | 3014.4564 | 766.4946 | 766.4946 | 5355.8351 | 5355.8351 | 703.598 | 703.598 | 6220.982 | 6220.982 | 0 | 0 | 5951.601 | 5951.601 | 2500 | 2500 | 5826.691 | 5826.691
Situational Awareness and Forecasting | Fire potential index | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vegetation Management and Inspection | Vegetation Inspections | VM-1, VM-9, VM-10 | Contact with vegetation |  | 2018 | 2021 GRC | [5 empty] | 0 | 0 | 97485.368 | 4532.306 | 0 | 0 | 31621.7086 | 21656.0379 | 0 | 0 | 31678.8982 | 21800.3897 | 0 | 0 | 49438.6972 | 43016.7015 | 0 | 0 | 81105.7039 | 67112.195 | 0 | 0 | 91986.2131 | 75943.1076 | 0 | 0 | 150184.8399 | 131681.3157
Vegetation Management and Inspection | Pole clearing | VM-2 | Equipment failure |  | 2019 | 2021 GRC | [5 empty] | 0 | 0 | 1654.651 | 1654.651 | 0 | 0 | 7459.0831 | 7459.0831 | 0 | 0 | 11026.1923 | 11026.1923 | 0 | 0 | 13826.3234 | 13826.3234 | 0 | 0 | 23852.1798 | 23852.1798 | 0 | 0 | 25915.3922 | 25915.3922 | 0 | 0 | 26196.7627 | 26196.7627
Vegetation Management and Inspection | Wood and slash management | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vegetation Management and Inspection | Clearance | VM-1, VM-3, VM-4, VM-7, VM-8 | Contact with vegetation |  | 2018 | 2021 GRC | [5 empty] | 0 | 0 | 215651.827 | 213098.8392 | 0 | 0 | 411087.8115 | 300309.4911 | 0 | 0 | 382748.1553 | 262017.5643 | 0 | 0 | 386930.3271 | 263219.6136 | 0 | 0 | 418435.4697 | 289597.6914 | 0 | 0 | 450423.5052 | 315842.873 | 0 | 0 | 458877.9447 | 319521.2262
Vegetation Management and Inspection | Fall-in mitigation | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vegetation Management and Inspection | Substation defensible space | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vegetation Management and Inspection | High-risk species | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vegetation Management and Inspection | Fire-resilient right-of-ways | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.431 | 14.9564 | 0 | 0 | 3786.252 | 2416.829 | 0 | 0 | 4070.203 | 2598.0798 | 0 | 0 | 4599.005 | 2935.6231
Vegetation Management and Inspection | Emergency response vegetation management | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vegetation Management and Inspection | Vegetation management enterprise system | VM-6 |  |  | 2021 | 2021 GRC | [5 empty] | 4219 | 4219 | 0 | 0 | 16127.8644 | 16127.8644 | 1055.6305 | 1055.6305 | 11005.183 | 11005.183 | 634.5483 | 634.5483 | 7124.5736 | 7124.5736 | 3286.0347 | 3286.0347 | 2602.5663 | 2602.5663 | 3800.122 | 3800.122 | 2746.924 | 2746.924 | 4000.0344 | 4000.0344 | 2436.5738 | 2436.5738 | 4200 | 4200
Vegetation Management and Inspection | Quality assurance / quality control | [10 empty] | 0 | 0 | 989.08 | 989.08 | 0 | 0 | 3966.0336 | 3966.0336 | 0 | 0 | 3221.2003 | 3221.2003 | 0 | 0 | 5523.0197 | 5523.0197 | 0 | 0 | 10828.1436 | 10828.1436 | 0 | 0 | 11808.8854 | 11808.8854 | 0 | 0 | 12686.8561 | 12686.8561
Vegetation Management and Inspection | Open work orders | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vegetation Management and Inspection | Workforce Planning | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wildfire Mitigation Strategy Development | Wildfire Mitigation Strategy Development | [10 empty] | 0 | 0 | 42643.8299 | 42643.8299 | 0 | 0 | 32860.3867 | 32860.3867 | 0 | 0 | 13245.9608 | 13245.9608 | 0 | 0 | 8543.7308 | 8543.7308 | 0 | 0 | 4540.397 | 4540.397 | 0 | 0 | 4012.0099 | 4012.0099 | 0 | 0 | 3252.6215 | 3252.6215

## Table 12
Utility | Southern California Edison | Notes:
Table No. | 12
Date Modified | 2023-02-01
Table 12: WMP Midyear & End-of-Year Targets
Targets
[5 empty] | YTD end of Q2 | YTD end of Q3 | End of year | YTD end of Q2 | YTD end of Q3 | End of year | End of year
WMPInitiativeCategory | WMPInitiativeActivity | UtilityInitiativeTrackingID | TargetType | Units | 2023 | 2023 | 2023 | 2024 | 2024 | 2024 | 2025 | Method of Verification | Comments
Grid Design, Operations, and Maintenance | Asset inspections | IN-1.1 | Quantitative | # of structures in HFRA | 101320 | 172640 | Inspect 187,000 structures in HFRA | 101320 | 172640 | Inspect 187,000 structures in HFRA | Inspect 187,000 structures in HFRA | Listing of completed work orders
Grid Design, Operations, and Maintenance | Asset inspections | IN-1.2 | Quantitative | # of structures in HFRA | 14400 | 25800 | Inspect 28,000 structures in HFRA | 14400 | 25800 | Inspect 28,000 structures in HFRA | Inspect 28,000 structures in HFRA | Listing of completed work orders
Grid Design, Operations, and Maintenance | Asset inspections | IN-3 | Quantitative | # of distribution circuit miles in HFRA | 2295 | 5100 | Inspect 5,100 distribution overhead circuit miles in HFRA | 2295 | 5100 | Inspect 5,100 distribution overhead circuit miles in HFRA | Inspect 5,100 distribution overhead circuit miles in HFRA | Listing of completed work orders
Grid Design, Operations, and Maintenance | Asset inspections | IN-4 | Quantitative | # of transmission circuit miles in HFRA | 600 | 900 | Inspect 1,000 transmission overhead circuit miles in HFRA | 600 | 900 | Inspect 1,000 transmission overhead circuit miles in HFRA | Inspect 1,000 transmission overhead circuit miles in HFRA | Listing of completed work orders
Grid Design, Operations, and Maintenance | Asset inspections | IN-5 | Quantitative | # of structures in HFRA | 55 | 170 | Inspect 170 generation related assets in HFRA | 52 | 160 | Inspect 160 generation related assets in HFRA | Inspect 170 generation related assets in HFRA | Listing of completed work orders
Grid Design, Operations, and Maintenance | Asset Management and Inspection Enterprise System(s) | IN-8 | Qualitative | Qualitative Initiative | Complete detailed design to migrate the distribution ground inspection application to the single digital platform | Develop use cases to use in build of proof of concept (POC) to prove out design direction | Develop the detailed design to migrate the distribution ground inspection application to the single digital platform | Conduct requirements gathering for incorporating distribution ground and InspectCam capabilities in single digital platform | Initiate solution analysis for incorporating distribution ground and InspectCam capabilities in single digital platform | Execute the approved designs / recommendations for incorporating distribution ground and InspectCam capabilities into single digital platform | Monitor utilization of inspection work management tool, and make enhancements as necessary | Completed user acceptance testing, screenshots of tool enhancements
Grid Design, Operation, and Maintenance | Asset inspections | IN-9 | Quantitative | # Spans/splices | Line Vue: 30 X-Ray: 30 | Line Vue: 45 X-Ray: 45 | Will inspect 50 spans with Line Vue Will inspect 50 splices with X-Ray | N/A | N/A | Target to be developed based on an engineering analysis to be performed in 2023 | Target to be developed based on an engineering analysis to be performed in 2023 and 2024 | Listing of completed work orders
Grid Design, Operation, and Maintenance | Data Governance | DG-1 | Qualitative | Qualitative Initiative | WiSDM: Execute parallel run of QDR reporting Ezy: Completed solution analysis for LIDAR data management in support of Veg Mgmt and asset inspection | WiSDM: Execute final validation of semi-automated QDR reporting Ezy: Complete Migration of legacy LIDAR data to GCP | WiSDM: Enable semi-automated data aggregation and validations of Wildfire Data for SCE's Quarterly Data Request (QDR) submission and external portal for external data sharing Ezy: Enable LIDAR data management | N/A | N/A | N/A – Sunsetting in 2023 | N/A – Sunsetting in 2023 | WiSDM: WiSDM-generated QDR Ezy: Screenshots of tool by use case
Vegetation Management & Inspection | Vegetation Inspections | VM-1 | Quantitative | # grids | 305 | 447 | Inspect 550 grids and prescribe mitigation for hazardous trees with strike potential within those grids in SCE’s HFRA | 241 | 354 | Inspect 420 grids and prescribe mitigation for hazardous trees with strike potential within those grids in SCE’s HFRA Note: 2024 schedule will be developed at the circuit/span level | Inspect 460 grids and prescribe mitigation for hazardous trees with strike potential within those grids in SCE’s HFRA Note: 2025 schedule will be developed at the circuit/span level | Tracking of year-to-date completed grids/circuits for inspection and mitigation
Vegetation Management & Inspection | Pole Clearing | VM-2 | Quantitative | # poles brushed | 29870 | 63700 | Inspect and clear (where clearance is needed) 63,700 structures*, with the exception of poles for which there are customer access or environmental constraints *These structures are in addition to poles subject to PRC 4292 | 29870 | 63700 | Inspect and clear (where clearance is needed) 63,700 structures*, with the exception of poles for which there are customer access or environmental constraints *These structures are in addition to poles subject to PRC 4292 | Inspect and clear (where clearance is needed) 63,700 structures*, with the exception of poles for which there are customer access or environmental constraints *These structures are in addition to poles subject to PRC 4292 | Listing of work orders attempted, inspected and/or completed in calendar year
Vegetation Management & Inspection | Clearance | VM-3 | Quantitative | # of sites treated | 30 | 45 | Perform vegetation treatment and maintenance to 50 sites | 30 | 45 | Perform vegetation treatment and maintenance to 50 sites | Perform vegetation treatment and maintenance to 60 sites | Listing of all completed work orders
Vegetation Management & Inspection | Clearance | VM-4 | Quantitative | # grids | 345 | 530 | Inspect 650 grids and prescribe mitigation for dead and dying trees with strike potential within those grids | 296 | 446 | Inspect 510 grids and prescribe mitigation for dead and dying trees with strike potential within those grids Note: 2024 schedule will be developed at the circuit/span level, measurement method subject to change | Inspect 560 grids and prescribe mitigation for dead and dying trees with strike potential within those grids Note: 2025 schedule will be developed at the circuit/span level, measurement method subject to change | Tracking of year-to-date completed grids/circuits for inspection and mitigation
Vegetation Management & Inspection | Vegetation Management Enterprise System | VM-6 | Qualitative | Qualitative Initiative | Develop release schedule/plan for Arbora supplemental VM (emergent work) capabilities; and OCM and Business Readiness plan​ | Initiate UAT of developed capabilities | Enable supplemental Vegetation Management (emergent work) tree maintenance program capabilities in Arbora by end of year | Document backlog of enhancements identified during stabilization | Initiate creation of plan to prioritize and enable additional VM programs in Arbora | Monitor stabilization of Arbora and develop plan and begin execution of plan to enable additional VM maintenance programs | Monitor stabilization of Arbora and continue execution of plan to enable additional VM maintenance programs | System evidence of the capability to assign non-routine work activity in work management tool
Vegetation Management & Inspection | Clearance | VM-7 | Quantitative | # grids | 1088 | 1508 | SCE plans to inspect 1,900 grids within our distribution system | 1088 | 1508 | SCE plans to inspect 1,900 grids within our distribution system Note: 2024 schedule will be developed at the circuit/span level, measurement method subject to change | SCE plans to inspect 1,900 grids within our distribution system Note: 2025 schedule will be developed at the circuit/span level, measurement method subject to change | Listing of all completed work orders
Vegetation Management & Inspection | Clearance | VM-8 | Quantitative | # grids | 619 | 884 | SCE plans to inspect 1,000 grids within our transmission system | 619 | 884 | SCE plans to inspect 1,000 grids within our transmission system | SCE plans to inspect 1,000 grids within our transmission system | Listing of all completed work orders
Vegetation Management & Inspection | Vegetation Inspections | VM-9 | Quantitative | # circuit miles | 650 | 1020 | SCE will inspect at least 1,020 HFRA circuit miles *Subject to change based on technology, program adjustments, and grid/circuits layout | 650 | 1020 | SCE will inspect at least 1,020 HFRA circuit miles *Subject to change based on technology, program adjustments, and grid/circuits layout | SCE will inspect at least 1,020 HFRA circuit miles *Subject to change based on technology, program adjustments, and grid/circuits layout. Targets for 2025 for HFRA LiDAR miles assume continuation of support of ground inspections and do not reflect SCE’s planned transition to remote sensing for inspections | Listing of all completed work orders
Vegetation Management & Inspection | Vegetation Inspections | VM-10 | Quantitative | # circuit miles | 1390 | 1700 | SCE will inspect at least 1,820 HFRA circuit miles *Subject to change based on program adjustments and evolution of remote sensing technologies | 1146 | 1401 | SCE will inspect at least 1,500 HFRA circuit miles *Subject to change based on program adjustments and evolution of remote sensing technologies | SCE will inspect at least 1,750 HFRA circuit miles *Subject to change based on program adjustments and evolution of remote sensing technologies. Targets for 2025 for HFRA LiDAR miles assume continuation of support of ground inspections and do not reflect SCE’s planned transition to remote sensing for inspections | Listing of all completed work orders
Community Outreach and Engagement | Public Outreach and Education Awareness Program | DEP-1 | Quantitative | # of meetings | 4 | 4 | SCE will host at least four wildfire community safety meetings by region in targeted HFRA communities based on the impact of 2022 PSPS events and ongoing wildfire mitigation activities | TBD | TBD | Continue or revise – determined based on the outcome of 2023 | Continue or revise – determined based on the outcome of 2023-2024 | Link to the SCE.com site for meeting conducted and recordings posted
Community Outreach and Engagement | Public Outreach and Education Awareness Program | DEP-4 | Quantitative | # of surveys | 1 | 3 | SCE plans to conduct at least five PSPS‐related customer studies in 2023 | 1 | 2 | SCE plans to conduct at least three PSPS‐related customer studies in 2024 | SCE plans to conduct at least three PSPS‐related customer studies in 2025 | Detailed list of surveys with supporting information

## Table 13
Utility | Southern California Edison |  | Note: Provide a listing (as rows) of all work orders / notifications for corrective work on electric circuits that were open as of the end of the quarter.
Table No. | 13
Date Modified | 2023-02-01
Table 13: Open work orders / notifications
a. Work order number | b. Equipment Type | c. HFTD Tier | d. Line type | e. Date the work order was originally opened | f. Due date of the original work order | g. GO 95 rule 18 priority level of the original work order | h. Optional utility-specific repair priority | i. Date(s) the work order was reinspected or modified (if applicable) | j. Due date of the work order after it was reinspected or modified (if applicable) | k. Priority of the work order after it was reinspected or modified (if applicable) | l. Reason for reinspection (if applicable)
SCE to provide supplemental file due to file size

## Table 14
Utility | Southern California Edison
Table No. | 14
Date Modified | 2023-02-01
Table 14: HFTD Area Risk Summary
*EC to add all other risk categories to right of last required category.
HFTD Area | Overall Utility Risk | Ignition Risk | PSPS Risk | Ignition Likelihood | Equipment Likelihood of Ignition | Contact from Vegetation Likelihood of Ignition | Contact from Object Likelihood of Ignition | Burn Probability | PSPS Likelihood | Wildfire Consequence | Wildfire Hazard Intensity | Wildfire Exposure Potential | Wildfire Vulnerability | PSPS Consequence | PSPS Exposure Potential | Vulnerability of Community to PSPS
HFTD 2 Distribution | 45.0852 | 45.0202 | 0.065092 | 26.6514 | 15.6692 | 2.5808 | 8.4014 | N/A | 6.4775 | 1.6892 | N/A | N/A | 1.2106 | 0.010049 | N/A | 1.2106
HFTD 3 Distribution | 78.1875 | 78.1144 | 0.073069 | 43.4734 | 27.1394 | 2.2692 | 14.0648 | N/A | 9.6815 | 1.7968 | N/A | N/A | 1.2033 | 0.0075473 | N/A | 1.2033
HFTD 2 Transmision | 0.15388 | 0.15388 | 0 | 0.12044 | 0 | 0 | 0.12044 | N/A | 6.4775 | 1.2777 | N/A | N/A | 1.1944 |  | N/A | 1.1944
HFTD 3 Transmision | 1.1392 | 1.1392 | 0 | 0.70635 | 0.064583 | 0 | 0.64176 | N/A | 9.6815 | 1.6129 | N/A | N/A | 1.1722 |  | N/A | 1.1722
Non-HFTD Distribution | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Non-HFTD Transmision | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A

## Table 15
Utility | Southern California Edison
Table No. | 15
Date Modified | 2023-02-01
Table 15: Top Risk Circuit Scores
*EC to add all other risk categories to right of last required category.
Top- Risk Circuit/ Segment/ Span ID | Risk Granularity | Line Class | Circuit/ Segment/ Span Length (mi) | Inclusion Reason | HFTD Area | Overall Utility Risk | Ignition Risk | PSPS Risk | Ignition Likelihood | Equipment Likelihood of Ignition | Contact from Vegetation Likelihood of Ignition | Contact from Object Likelihood of Ignition | Burn Probability | PSPS Likelihood | Wildfire Consequence | Wildfire Hazard Intensity | Wildfire Exposure Potential | Wildfire Vulnerability | PSPS Consequence | PSPS Exposure Potential | Vulnerability of Community to PSPS
ABACUS | Circuit | Distribution | 1.5142 |  | HFTD 2 | 0.0032292 | 0.0024959 | 0.00073332 | 0.013282 | 0.0013146 | 0.0025002 | 0.0094675 | N/A | 0.003756 | 0.18791 | N/A | N/A | 1.0916 | 0.19524 | N/A | 1.0916
ABRAHAM | Circuit | Distribution | 0.63553 |  | HFTD 3 | 0.0019389 | 0.00058807 | 0.0013509 | 0.0092576 | 0.0045531 | 0.00055039 | 0.0041542 | N/A | 0.028091 | 0.063523 | N/A | N/A | 1.0725 | 0.04809 | N/A | 1.0725
ACADEMY | Circuit | Distribution | 8.4331 |  | HFTD 3 | 0.0028319 | 0.0028284 | 3.486e-06 | 0.017233 | 0.011904 | 0.00057857 | 0.0047503 | N/A | 0.0051271 | 0.16413 | N/A | N/A | 1.1303 | 0.00067992 | N/A | 1.1303
ACADIAN | Circuit | Distribution | 3.22 |  | HFTD 2 | 0.0056945 | 0.0056823 | 1.217e-05 | 0.0054217 | 0.0038996 | 0.0003887 | 0.0011334 | N/A | 0.0012927 | 1.0481 | N/A | N/A | 1.2148 | 0.0094144 | N/A | 1.2148
ACAPULCO | Circuit | Distribution | 4.8611 |  | HFTD 3 | 0.03159 | 0.03159 | 0 | 0.0090562 | 0.0037378 | 0.00062084 | 0.0046976 | N/A | 0.0039667 | 3.4882 | N/A | N/A | 1.3254 | 0 | N/A | 1.3254
ACCENT | Circuit | Distribution | 1.6871 |  | HFTD 2 | 0.0010556 | 0.001021 | 3.4584e-05 | 0.00098557 | 0.00037551 | 5.8064e-05 | 0.00055199 | N/A | 0.0056368 | 1.0359 | N/A | N/A | 1.136 | 0.0061354 | N/A | 1.136
ACE | Circuit | Distribution | 3.4795 |  | HFTD 3 | 0.0055279 | 0.0055279 | 0 | 0.015294 | 0.0090055 | 0.00078599 | 0.0055023 | N/A | 0 | 0.36145 | N/A | N/A | 1.0945 |  | N/A | 1.0945
ACOSTA | Circuit | Distribution | 6.5002 |  | HFTD 2 | 0.004774 | 0.0045013 | 0.00027279 | 0.0039769 | 0.00082866 | 0.00012126 | 0.0030269 | N/A | 0.040812 | 1.1319 | N/A | N/A | 1.2663 | 0.006684 | N/A | 1.2663
ACRES | Circuit | Distribution | 5.4457 |  | HFTD 3 | 0.007239 | 0.0072324 | 6.6668e-06 | 0.0081738 | 0.0040752 | 0.00055427 | 0.0035444 | N/A | 0.0059049 | 0.88482 | N/A | N/A | 1.1951 | 0.001129 | N/A | 1.1951
ACROBAT | Circuit | Distribution | 11.7854 | Top 5% Highest Risk | HFTD Tier 3 | 0.050249 | 0.050196 | 5.2917e-05 | 0.0073603 | 0.0035518 | 2.2646e-05 | 0.0037858 | N/A | 0.028823 | 6.8199 | N/A | N/A | 1.2277 | 0.0018359 | N/A | 1.2277
AGATE | Circuit | Distribution | 7.0064 |  | HFTD 2 | 0.002502 | 0.0024837 | 1.83e-05 | 0.010924 | 0.0037412 | 0.00078199 | 0.0064013 | N/A | 0.0030502 | 0.22735 | N/A | N/A | 1.1284 | 0.0059997 | N/A | 1.1284
AGNEW | Circuit | Distribution | 0.46742 |  | HFTD 2 | 0.0040557 | 0.0040557 | 0 | 0.00075414 | 9.819e-05 | 0.00046743 | 0.00018852 | N/A | 0.065651 | 5.3779 | N/A | N/A |  | 0 | N/A
AIDAN | Circuit | Distribution | 1.2003 |  | HFTD 2 | 0.016859 | 0.016822 | 3.7062e-05 | 0.0039118 | 0.0014199 | 0.00017433 | 0.0023176 | N/A | 0.0024943 | 4.3004 | N/A | N/A | 1.2175 | 0.014859 | N/A | 1.2175
ALLVIEW | Circuit | Distribution | 2.4986 |  | HFTD 3 | 0.017062 | 0.017037 | 2.5094e-05 | 0.015294 | 0.0094454 | 0.0020494 | 0.0037988 | N/A | 0.029806 | 1.114 | N/A | N/A | 1.0091 | 0.00084191 | N/A | 1.0091
ALOLA #2 | Circuit | Distribution | 2.4965 |  | HFTD 3 | 0.015973 | 0.015973 | 0 | 0.0010456 | 0.0007175 | 7.4325e-05 | 0.00025379 | N/A | 0.015177 | 15.2757 | N/A | N/A | 1.0077 | 0 | N/A | 1.0077
ALPINE | Circuit | Distribution | 8.8607 |  | HFTD 3 | 0.007266 | 0.0072484 | 1.7573e-05 | 0.0073246 | 0.0051989 | 0.00068078 | 0.0014449 | N/A | 0.067308 | 0.98959 | N/A | N/A | 1.2628 | 0.00026108 | N/A | 1.2628
AMBERJACK | Circuit | Distribution | 0.86958 |  | HFTD 2 | 0.010739 | 0.010655 | 8.4184e-05 | 0.003518 | 0.00091819 | 0.00013673 | 0.0024631 | N/A | 0.010701 | 3.0287 | N/A | N/A | 1.1166 | 0.0078668 | N/A | 1.1166
AMBERSKY | Circuit | Distribution | 2.4829 |  | HFTD 2 | 0.0016435 | 0.0016435 | 0 | 0.0095235 | 0.0037205 | 0.00094259 | 0.0048605 | N/A | 0.0013249 | 0.17258 | N/A | N/A | 1.1419 | 0 | N/A | 1.1419
AMBRUS | Circuit | Distribution | 3.2914 |  | HFTD 3 | 0.0021561 | 0.0021324 | 2.3696e-05 | 0.012574 | 0.0042276 | 0.00042767 | 0.0079189 | N/A | 0.005735 | 0.16959 | N/A | N/A | 1.0899 | 0.0041318 | N/A | 1.0899
AMETHYST | Circuit | Distribution | 1.3196 | Top 5% Highest Risk | HFTD Tier 3 | 0.049067 | 0.048881 | 0.00018646 | 0.0052222 | 0.0047179 | 6.4923e-05 | 0.00043937 | N/A | 0.014004 | 9.3602 | N/A | N/A | 1.1142 | 0.013315 | N/A | 1.1142
ANACONDA | Circuit | Distribution | 1.657 |  | HFTD 3 | 0.0018744 | 0.0011058 | 0.00076859 | 0.019342 | 0.013137 | 0.00016679 | 0.0060381 | N/A | 0.050274 | 0.057172 | N/A | N/A | 1.0894 | 0.015288 | N/A | 1.0894
ANGELES | Circuit | Distribution | 7.793 |  | HFTD 2 | 0.0050136 | 0.0050084 | 5.2176e-06 | 0.015213 | 0.0080648 | 0.0043356 | 0.0028123 | N/A | 0.015597 | 0.32922 | N/A | N/A | 1.2036 | 0.00033453 | N/A | 1.2036
ANGUS | Circuit | Distribution | 17.8189 |  | HFTD 3 | 0.0031732 | 0.0031541 | 1.9125e-05 | 0.0063502 | 0.003544 | 0.00028968 | 0.0025165 | N/A | 0.019265 | 0.4967 | N/A | N/A | 1.2769 | 0.00099272 | N/A | 1.2769
ANN | Circuit | Distribution | 0.5287 |  | HFTD 2 | 0.00010333 | 0.00010333 | 0 | 0.0071226 | 0.002713 | 0.00040671 | 0.0040029 | N/A | 0 | 0.014507 | N/A | N/A | 1.0487 |  | N/A | 1.0487
ANTON | Circuit | Distribution | 20.4451 |  | HFTD 3 | 0.00203 | 0.0020259 | 4.0421e-06 | 0.0057774 | 0.0041496 | 0.00037869 | 0.0012491 | N/A | 0.036123 | 0.35066 | N/A | N/A | 1.2269 | 0.0001119 | N/A | 1.2269
ANZAR | Circuit | Distribution | 3.168 |  | HFTD 3 | 0.0034011 | 0.0034011 | 0 | 0.0048544 | 0.0024281 | 1.7947e-05 | 0.0024083 | N/A | 0.0093635 | 0.70062 | N/A | N/A |  | 0 | N/A
APPALOUSA | Circuit | Distribution | 11.1694 |  | HFTD 2 | 0.0084238 | 0.0084233 | 4.6706e-07 | 0.0042796 | 0.0024427 | 4.9477e-05 | 0.0017874 | N/A | 0.0034582 | 1.9683 | N/A | N/A | 1.1057 | 0.00013506 | N/A | 1.1057
APPLETON | Circuit | Distribution | 6.5789 |  | HFTD 3 | 0.0010901 | 0.0010424 | 4.7659e-05 | 0.022246 | 0.0092747 | 0.0023984 | 0.010573 | N/A | 0.015059 | 0.046861 | N/A | N/A | 1.0801 | 0.0031647 | N/A | 1.0801
ARABIA | Circuit | Distribution | 1.166 |  | HFTD 2 | 0.001074 | 0.00086942 | 0.00020455 | 0.0084034 | 0.0045773 | 0.00067644 | 0.0031497 | N/A | 0.006085 | 0.10346 | N/A | N/A | 1.2393 | 0.033615 | N/A | 1.2393
ARAPAHO | Circuit | Distribution | 12.9573 |  | HFTD 2 | 0.036528 | 0.036526 | 1.8384e-06 | 0.0069995 | 0.0038808 | 9.4333e-05 | 0.0030244 | N/A | 0.0046119 | 5.2183 | N/A | N/A | 1.257 | 0.00039861 | N/A | 1.257
ARBORETUM | Circuit | Distribution | 9.9457 |  | HFTD 3 | 0.014013 | 0.014009 | 4.4559e-06 | 0.012466 | 0.0048672 | 0.0014312 | 0.0061675 | N/A | 0.0222 | 1.1238 | N/A | N/A | 1.1215 | 0.00020072 | N/A | 1.1215
ARCHIE | Circuit | Distribution | 19.0882 |  | HFTD 3 | 0.0053525 | 0.0053525 | 1.7459e-10 | 0.0025336 | 0.0012924 | 0.00019713 | 0.001044 | N/A | 0.0022993 | 2.1126 | N/A | N/A | 1.5 | 7.5932e-08 | N/A | 1.5
ARCTURUS | Circuit | Distribution | 2.8543 |  | HFTD 2 | 0.029273 | 0.029273 | 0 | 0.028404 | 0.0078177 | 0.0081568 | 0.012429 | N/A | 0.0013288 | 1.0306 | N/A | N/A | 1.3876 | 0 | N/A | 1.3876
ARGONAUT | Circuit | Distribution | 2.1118 |  | HFTD 2 | 0.010403 | 0.010401 | 1.9052e-06 | 0.0026761 | 0.0013222 | 0.00012705 | 0.0012269 | N/A | 0.0074037 | 3.8868 | N/A | N/A | 1.0683 | 0.00025733 | N/A | 1.0683
ARIEL | Circuit | Distribution | 0.29911 |  | HFTD 3 | 0.0068732 | 0.0068732 | 0 | 0.0013129 | 0.0011333 | 5.9336e-05 | 0.00012027 | N/A | 0.0026753 | 5.2352 | N/A | N/A | 1.2048 | 0 | N/A | 1.2048
ARLENE | Circuit | Distribution | 4.7365 |  | HFTD 3 | 0.0074198 | 0.0074168 | 3.0759e-06 | 0.0054541 | 0.0044998 | 0.00019424 | 0.0007601 | N/A | 0.010755 | 1.3598 | N/A | N/A | 1.1019 | 0.00028599 | N/A | 1.1019
ARLINGTON | Circuit | Distribution | 1.2923 |  | HFTD 2 | 0.0068214 | 0.0067013 | 0.00012015 | 0.010735 | 0.0056436 | 0.00046308 | 0.0046283 | N/A | 0.0020208 | 0.62424 | N/A | N/A | 1.1002 | 0.059456 | N/A | 1.1002
ARMADA | Circuit | Distribution | 4.9601 |  | HFTD 3 | 0.014429 | 0.014429 | 0 | 0.0043332 | 0.0017372 | 0.00020792 | 0.0023882 | N/A | 0.0040129 | 3.3299 | N/A | N/A | 1.0399 | 0 | N/A | 1.0399
ARMOUR | Circuit | Distribution | 6.2707 |  | HFTD 3 | 0.028183 | 0.028176 | 7.1821e-06 | 0.01469 | 0.0088638 | 0.0040277 | 0.0017986 | N/A | 0.033414 | 1.918 | N/A | N/A | 1.1298 | 0.00021494 | N/A | 1.1298
ARTIST | Circuit | Distribution | 3.4287 |  | HFTD 2 | 0.0023668 | 0.0023465 | 2.0259e-05 | 0.018866 | 0.0038896 | 0.00042936 | 0.014547 | N/A | 0.0032457 | 0.12438 | N/A | N/A | 1.09 | 0.0062417 | N/A | 1.09
ASHLEY | Circuit | Distribution | 2.5589 |  | HFTD 3 | 0.010149 | 0.010144 | 5.106e-06 | 0.011821 | 0.0080235 | 0.0026246 | 0.0011727 | N/A | 0.0093421 | 0.85817 | N/A | N/A | 1.1137 | 0.00054655 | N/A | 1.1137
ATENTO | Circuit | Distribution | 27.6181 |  | HFTD 3 | 0.0066747 | 0.0066698 | 4.8912e-06 | 0.0022055 | 0.0011347 | 0.00035234 | 0.00071845 | N/A | 0.040909 | 3.0241 | N/A | N/A | 1.3164 | 0.00011956 | N/A | 1.3164
ATLANTA | Circuit | Distribution | 5.6804 |  | HFTD 3 | 0.010663 | 0.010638 | 2.4895e-05 | 0.0031522 | 0.0013726 | 0.00013999 | 0.0016397 | N/A | 0.023576 | 3.3748 | N/A | N/A | 1.2066 | 0.0010559 | N/A | 1.2066
ATMORE | Circuit | Distribution | 5.1972 |  | HFTD 2 | 0.00047805 | 0.00045063 | 2.7419e-05 | 0.0024787 | 0.0013926 | 0.00017604 | 0.00091009 | N/A | 0.0033623 | 0.1818 | N/A | N/A | 1.0768 | 0.0081549 | N/A | 1.0768
AUBURN | Circuit | Distribution | 1.0044 |  | HFTD 2 | 0.0036388 | 0.0036359 | 2.8912e-06 | 0.0031061 | 0.00054738 | 0.00036702 | 0.0021917 | N/A | 0 | 1.1706 | N/A | N/A | 1.065 | inf | N/A | 1.065
AUTUMN | Circuit | Distribution | 6.1491 |  | HFTD 2 | 0.031925 | 0.031091 | 0.0008342 | 0.017917 | 0.0083842 | 0.0039971 | 0.0055359 | N/A | 0.10957 | 1.7352 | N/A | N/A | 1.0732 | 0.0076136 | N/A | 1.0732
AVANTI | Circuit | Distribution | 2.9796 |  | HFTD 2 | 0.0043251 | 0.0035955 | 0.00072961 | 0.01356 | 0.0059501 | 0.00017422 | 0.0074361 | N/A | 0.022586 | 0.26515 | N/A | N/A | 1.1265 | 0.032303 | N/A | 1.1265
AVENGER | Circuit | Distribution | 10.1505 |  | HFTD 2 | 0.0059943 | 0.0059879 | 6.431e-06 | 0.0058616 | 0.0024791 | 0.00035961 | 0.0030228 | N/A | 0.0029443 | 1.0216 | N/A | N/A | 1.1014 | 0.0021842 | N/A | 1.1014
AVENIDA | Circuit | Distribution | 8.6718 |  | HFTD 2 | 0.0037639 | 0.0037592 | 4.742e-06 | 0.0096262 | 0.0035711 | 0.0011817 | 0.0048734 | N/A | 0.012567 | 0.39052 | N/A | N/A | 1.1449 | 0.00037734 | N/A | 1.1449
AVIATOR | Circuit | Distribution | 14.5879 |  | HFTD 2 | 0.01731 | 0.017304 | 5.6719e-06 | 0.0099206 | 0.0051868 | 0.00012332 | 0.0046105 | N/A | 0.0028899 | 1.7442 | N/A | N/A | 1.1581 | 0.0019626 | N/A | 1.1581
BABYLON | Circuit | Distribution | 3.0178 |  | HFTD 2 | 0.0062465 | 0.0062465 | 0 | 0.0051522 | 0.00067868 | 0.00012827 | 0.0043452 | N/A | 0 | 1.2124 | N/A | N/A | 1.096 |  | N/A | 1.096
BACHELOR | Circuit | Distribution | 7.2399 |  | HFTD 2 | 0.00016547 | 0.00016547 | 0 | 0.011293 | 0.0031099 | 0.00055682 | 0.0076261 | N/A | 0.0021763 | 0.014653 | N/A | N/A | 1.1175 | 0 | N/A | 1.1175
BADGER | Circuit | Distribution | 2.2562 |  | HFTD 2 | 0.0063266 | 0.0053404 | 0.0009862 | 0.0088361 | 0.0039257 | 0.00014589 | 0.0047645 | N/A | 0.010047 | 0.60438 | N/A | N/A | 1.0973 | 0.098157 | N/A | 1.0973
BALCOM | Circuit | Distribution | 14.4869 |  | HFTD 3 | 0.0034365 | 0.0034224 | 1.4128e-05 | 0.0074203 | 0.0039044 | 0.00036636 | 0.0031496 | N/A | 0.0052098 | 0.46122 | N/A | N/A | 1.0544 | 0.0027119 | N/A | 1.0544
BALDWIN | Circuit | Distribution | 12.1375 |  | HFTD 2 | 0.0094308 | 0.0094231 | 7.6417e-06 | 0.01836 | 0.0073146 | 0.0039545 | 0.0070907 | N/A | 0.0086789 | 0.51325 | N/A | N/A | 1.0973 | 0.0008805 | N/A | 1.0973
BALLOON | Circuit | Distribution | 3.7926 |  | HFTD 3 | 0.02854 | 0.02853 | 1.0512e-05 | 0.0082361 | 0.0069702 | 4.1408e-05 | 0.0012245 | N/A | 0.00062973 | 3.464 | N/A | N/A | 1.0943 | 0.016693 | N/A | 1.0943
BARLEY FLATS | Circuit | Distribution | 2.749 |  | HFTD 2 | 0.011235 | 0.011134 | 0.00010134 | 0.013908 | 0.003184 | 0.0045642 | 0.00616 | N/A | 0.0041009 | 0.8005 | N/A | N/A | 1.0879 | 0.024711 | N/A | 1.0879
BARRINGTON | Circuit | Distribution | 20.356 |  | HFTD 3 | 0.0040566 | 0.0040514 | 5.2146e-06 | 0.0055134 | 0.0031121 | 0.00045285 | 0.0019485 | N/A | 0.02134 | 0.73482 | N/A | N/A | 1.164 | 0.00024436 | N/A | 1.164
BASIL | Circuit | Distribution | 1.6994 |  | HFTD 2 | 0.011761 | 0.011742 | 1.8716e-05 | 0.0044076 | 0.00029736 | 9.6928e-05 | 0.0040133 | N/A | 0.0039643 | 2.664 | N/A | N/A | 1.2989 | 0.0047212 | N/A | 1.2989
BAUXITE | Circuit | Distribution | 2.8693 |  | HFTD 2 | 0.0039634 | 0.0039634 | 0 | 0.016104 | 0.0049219 | 0.0016149 | 0.0095673 | N/A | 0.0013376 | 0.24611 | N/A | N/A | 1.1111 | 0 | N/A | 1.1111
BAYLINER | Circuit | Distribution | 3.2925 |  | HFTD 2 | 0.022086 | 0.022085 | 1.5625e-06 | 0.013472 | 0.0069668 | 0.00039204 | 0.006113 | N/A | 0.0024275 | 1.6393 | N/A | N/A | 1.1404 | 0.00064368 | N/A | 1.1404
BAZOOKA | Circuit | Distribution | 0.73365 |  | HFTD 2 | 0.00047143 | 0.00038138 | 9.0048e-05 | 0.0017665 | 0.00078589 | 3.7e-05 | 0.00094362 | N/A | 0.0036815 | 0.2159 | N/A | N/A | 1.0838 | 0.02446 | N/A | 1.0838
BEAR VALLEY | Circuit | Distribution | 16.6226 |  | HFTD 3 | 0.0012135 | 0.0011972 | 1.6249e-05 | 0.0044845 | 0.0027385 | 0.00046244 | 0.0012836 | N/A | 0.14652 | 0.26697 | N/A | N/A | 1.469 | 0.0001109 | N/A | 1.469
BECKER | Circuit | Distribution | 0.46611 |  | HFTD 2 | 0.0028817 | 0.0028712 | 1.0508e-05 | 0.007904 | 0.0025714 | 0.00030649 | 0.0050261 | N/A | 0.00069715 | 0.36326 | N/A | N/A | 1.0513 | 0.015072 | N/A | 1.0513
BEECHCRAFT | Circuit | Distribution | 1.1637 |  | HFTD 2 | 0.012545 | 0.012527 | 1.742e-05 | 0.0108 | 0.0063996 | 0.00028953 | 0.0041105 | N/A | 0.0015156 | 1.16 | N/A | N/A | 1.062 | 0.011494 | N/A | 1.062
BEELER | Circuit | Distribution | 2.9618 |  | HFTD 2 | 0.0092783 | 0.009276 | 2.3085e-06 | 0.0020753 | 0.00049658 | 3.4684e-05 | 0.001544 | N/A | 0.00079306 | 4.4697 | N/A | N/A | 1.1214 | 0.0029108 | N/A | 1.1214
BELPAC | Circuit | Distribution | 4.675 |  | HFTD 3 | 0.0011717 | 0.0011086 | 6.3103e-05 | 0.012627 | 0.007129 | 0.00098217 | 0.0045159 | N/A | 0.017705 | 0.087795 | N/A | N/A | 1.0473 | 0.0035642 | N/A | 1.0473
BENCH | Circuit | Distribution | 17.7961 |  | HFTD 3 | 0.035932 | 0.035926 | 5.7481e-06 | 0.0076107 | 0.0039471 | 0.00023791 | 0.0034258 | N/A | 0.024892 | 4.7204 | N/A | N/A | 1.3899 | 0.00023092 | N/A | 1.3899
BERKSHIRE | Circuit | Distribution | 6.3525 |  | HFTD 2 | 0.011279 | 0.011278 | 1.429e-06 | 0.011928 | 0.0073866 | 0.0013794 | 0.0031617 | N/A | 0.013406 | 0.9455 | N/A | N/A | 1.1991 | 0.0001066 | N/A | 1.1991
BERMITE | Circuit | Distribution | 1.2562 |  | HFTD 3 | 0.0079072 | 0.007884 | 2.3267e-05 | 0.069043 | 0.0053856 | 0.0001018 | 0.063555 | N/A | 0.0066829 | 0.11419 | N/A | N/A | 1.0743 | 0.0034817 | N/A | 1.0743
BEVERLY SL #1 | Circuit | Distribution | 0.50114 |  | HFTD 2 | 1.7113e-05 | 1.7113e-05 | 0 | 0.0083571 | 0.0017601 | 0.0044203 | 0.0021767 | N/A | 0.00019309 | 0.0020478 | N/A | N/A |  | 0 | N/A
BIANCO | Circuit | Distribution | 1.0013 | Top 5% Highest Risk | HFTD Tier 2 | 0.078765 | 0.078614 | 0.00015048 | 0.020213 | 0.0087217 | 0.0061977 | 0.0052933 | N/A | 0.0022045 | 3.8893 | N/A | N/A | 1.044 | 0.068259 | N/A | 1.044
BIDDER | Circuit | Distribution | 17.7986 |  | HFTD 3 | 0.0022546 | 0.0022545 | 1.022e-07 | 0.0091364 | 0.0047041 | 0.00084608 | 0.0035862 | N/A | 0 | 0.24676 | N/A | N/A | 1.0689 | inf | N/A | 1.0689
BIG CREEK-PORTAL | Circuit | Distribution | 18.2344 |  | HFTD 3 | 0.00057658 | 0.00057658 | 6.2175e-09 | 0.0035666 | 0.0022018 | 0.00034044 | 0.0010243 | N/A | 0.026118 | 0.16166 | N/A | N/A | 1.6316 | 2.3805e-07 | N/A | 1.6316
BIG FALLS | Circuit | Distribution | 3.221 |  | HFTD 3 | 0.0036905 | 0.0036854 | 5.0704e-06 | 0.018001 | 0.0092018 | 0.0033515 | 0.0054472 | N/A | 0.017389 | 0.20474 | N/A | N/A | 1.0115 | 0.00029158 | N/A | 1.0115
BIG ROCK | Circuit | Distribution | 11.9594 |  | HFTD 3 | 0.010184 | 0.010124 | 6.0071e-05 | 0.012946 | 0.0074085 | 0.00015069 | 0.0053868 | N/A | 0.026118 | 0.78203 | N/A | N/A | 1.1503 | 0.0023 | N/A | 1.1503
BIGFOOT | Circuit | Distribution | 1.8462 |  | HFTD 2 | 0.00032891 | 0.00032845 | 4.5809e-07 | 0.0056727 | 0.00082964 | 0.0013921 | 0.0034509 | N/A | 0.0080259 | 0.0579 | N/A | N/A | 1 | 5.7077e-05 | N/A | 1
BIRCHIM | Circuit | Distribution | 46.7887 |  | HFTD 2 | 0.0029919 | 0.0029919 | 0 | 0.0019887 | 0.00099624 | 0.00058739 | 0.00040508 | N/A | 0.1375 | 1.5045 | N/A | N/A | 1.2326 | 0 | N/A | 1.2326
BLACKBIRD | Circuit | Distribution | 0.67361 |  | HFTD 3 | 0.030058 | 0.030043 | 1.5333e-05 | 0.016738 | 0.008 | 0.00026991 | 0.0084678 | N/A | 0.0027278 | 1.7949 | N/A | N/A | 1.041 | 0.0056208 | N/A | 1.041
BLACKBURN | Circuit | Distribution | 4.2775 |  | HFTD 2 | 0.0033932 | 0.0033303 | 6.2813e-05 | 0.0058155 | 0.0015518 | 0.00016246 | 0.0041013 | N/A | 0.0055904 | 0.57266 | N/A | N/A | 1.1793 | 0.011236 | N/A | 1.1793
BLACKFOOT | Circuit | Distribution | 4.4528 | Top 5% Highest Risk | HFTD Tier 2 | 0.078461 | 0.078455 | 5.8973e-06 | 0.0056878 | 0.0020821 | 0.00036554 | 0.0032401 | N/A | 0.0020203 | 13.7937 | N/A | N/A | 1.1516 | 0.002919 | N/A | 1.1516
BLACKHILLS | Circuit | Distribution | 1.0953 |  | HFTD 2 | 0.010687 | 0.010013 | 0.00067336 | 0.014106 | 0.0017783 | 0.0013948 | 0.010932 | N/A | 0.0024889 | 0.70989 | N/A | N/A | 1.189 | 0.27054 | N/A | 1.189
BLEDSOE | Circuit | Distribution | 14.2924 |  | HFTD 2 | 0.0045678 | 0.0045639 | 3.8395e-06 | 0.0020022 | 0.0013944 | 5.732e-05 | 0.00055048 | N/A | 0.016529 | 2.2795 | N/A | N/A | 1.5395 | 0.00023229 | N/A | 1.5395
BLUE CUT | Circuit | Distribution | 33.4552 |  | HFTD 3 | 0.028065 | 0.02803 | 3.4885e-05 | 0.0071801 | 0.003745 | 3.7893e-05 | 0.0033973 | N/A | 0.16838 | 3.9038 | N/A | N/A | 1.3906 | 0.00020719 | N/A | 1.3906
BLUE RIDGE | Circuit | Distribution | 3.2345 |  | HFTD 3 | 0.0019742 | 0.0019737 | 5.2624e-07 | 0.0085963 | 0.0054074 | 0.00027507 | 0.0029139 | N/A | 0.010629 | 0.22959 | N/A | N/A | 1 | 4.9509e-05 | N/A | 1
BLUEBERRY | Circuit | Distribution | 0.33114 |  | HFTD 2 | 0.0015908 | 0.0013733 | 0.00021754 | 0.021835 | 0.0098343 | 0.00051869 | 0.011482 | N/A | 0.00087225 | 0.062894 | N/A | N/A | 1.0518 | 0.24941 | N/A | 1.0518
BOA | Circuit | Distribution | 1.8395 |  | HFTD 3 | 0.021613 | 0.021548 | 6.5116e-05 | 0.027146 | 0.011746 | 0.00011742 | 0.015283 | N/A | 0.0069043 | 0.79378 | N/A | N/A | 1.0618 | 0.0094312 | N/A | 1.0618
BOBBIT | Circuit | Distribution | 0.88254 |  | HFTD 2 | 0.0025 | 0.0022807 | 0.00021928 | 0.001953 | 0.00053475 | 0.00027075 | 0.0011475 | N/A | 0.0006553 | 1.1678 | N/A | N/A | 1.1009 | 0.33463 | N/A | 1.1009
BOBBY | Circuit | Distribution | 2.3983 |  | HFTD 2 | 0.011347 | 0.011342 | 5.0233e-06 | 0.019362 | 0.0078667 | 0.001496 | 0.0099989 | N/A | 0.00028737 | 0.58579 | N/A | N/A | 1.1364 | 0.01748 | N/A | 1.1364
BOBSLED | Circuit | Distribution | 2.0355 |  | HFTD 2 | 0.0052885 | 0.0021723 | 0.0031162 | 0.030585 | 0.004235 | 0.0038623 | 0.022487 | N/A | 0.033002 | 0.071025 | N/A | N/A | 1.0267 | 0.094425 | N/A | 1.0267
BODKIN | Circuit | Distribution | 1.427 | Top 5% Highest Risk | HFTD Tier 3 | 0.050751 | 0.050747 | 3.9556e-06 | 0.0073702 | 0.0055309 | 0.00011556 | 0.0017237 | N/A | 0.00074979 | 6.8855 | N/A | N/A | 1.2151 | 0.0052757 | N/A | 1.2151
BOGART | Circuit | Distribution | 1.5654 |  | HFTD 2 | 0.0032611 | 0.0032611 | 0 | 0.029372 | 0.0060142 | 0.016247 | 0.0071113 | N/A | 0 | 0.11103 | N/A | N/A | 1.0722 |  | N/A | 1.0722
BOLLERO | Circuit | Distribution | 1.3124 |  | HFTD 2 | 0.0031212 | 0.0029836 | 0.00013759 | 0.0034498 | 0.0011782 | 0.00023728 | 0.0020343 | N/A | 0.0031259 | 0.86484 | N/A | N/A | 1.2012 | 0.044016 | N/A | 1.2012
BOMBAY | Circuit | Distribution | 3.0529 |  | HFTD 2 | 0.0037241 | 0.0037103 | 1.3726e-05 | 0.0065178 | 0.00097274 | 0.00016694 | 0.0053781 | N/A | 0.0044814 | 0.56927 | N/A | N/A | 1.0712 | 0.0030629 | N/A | 1.0712
BONANZA | Circuit | Distribution | 32.685 |  | HFTD 3 | 0.020599 | 0.02059 | 8.7688e-06 | 0.0097214 | 0.0051655 | 0.00021749 | 0.0043384 | N/A | 0.054973 | 2.118 | N/A | N/A | 1.1566 | 0.00015951 | N/A | 1.1566
BONNEVILLE | Circuit | Distribution | 10.4374 |  | HFTD 2 | 0.0016003 | 0.0015985 | 1.7646e-06 | 0.0010965 | 0.00041618 | 3.6633e-05 | 0.00064369 | N/A | 0.0097669 | 1.4579 | N/A | N/A | 1.2509 | 0.00018067 | N/A | 1.2509
BONNIE | Circuit | Distribution | 0.26442 |  | HFTD 2 | 0.004603 | 0.0045453 | 5.7692e-05 | 0.013458 | 0.0075546 | 0.0035859 | 0.0023176 | N/A | 0.00093606 | 0.33774 | N/A | N/A | 1.0419 | 0.061632 | N/A | 1.0419
BOOTLEGGER | Circuit | Distribution | 62.3131 |  | HFTD 3 | 0.020622 | 0.020616 | 6.2715e-06 | 0.0026126 | 0.0018904 | 9.0372e-05 | 0.00063176 | N/A | 0.056642 | 7.891 | N/A | N/A | 1.1583 | 0.00011072 | N/A | 1.1583
BORCHARD | Circuit | Distribution | 2.8695 |  | HFTD 3 | 0.0071473 | 0.0071277 | 1.9606e-05 | 0.025445 | 0.011318 | 0.00082576 | 0.013301 | N/A | 0.0070662 | 0.28012 | N/A | N/A | 1.0448 | 0.0027747 | N/A | 1.0448
BORDEAUX | Circuit | Distribution | 0.51144 |  | HFTD 3 | 0.01358 | 0.013537 | 4.3152e-05 | 0.0030114 | 0.00051036 | 9.733e-05 | 0.0024037 | N/A | 0.00086233 | 4.4952 | N/A | N/A | 1.0766 | 0.050041 | N/A | 1.0766
BOULDER | Circuit | Distribution | 8.9596 |  | HFTD 2 | 0.0030789 | 0.0030559 | 2.3006e-05 | 0.0061593 | 0.0025455 | 0.00058437 | 0.0030294 | N/A | 0.022852 | 0.49615 | N/A | N/A | 1.2584 | 0.0010067 | N/A | 1.2584
BOUQUET | Circuit | Distribution | 21.8696 |  | HFTD 3 | 0.038445 | 0.038437 | 8.2001e-06 | 0.0082383 | 0.005257 | 0.00022806 | 0.0027533 | N/A | 0.0315 | 4.6656 | N/A | N/A | 1.135 | 0.00026032 | N/A | 1.135
BRADLEY | Circuit | Distribution | 1.685 |  | HFTD 2 | 0.0072271 | 0.0072271 | 0 | 0.002542 | 0.0012167 | 0.00012108 | 0.0012042 | N/A | 0 | 2.8431 | N/A | N/A | 1.0841 |  | N/A | 1.0841
BRAKEMAN | Circuit | Distribution | 7.0477 |  | HFTD 2 | 0.0041605 | 0.0041605 | 0 | 0.0089917 | 0.0038616 | 0.00075323 | 0.0043768 | N/A | 0.0023832 | 0.4627 | N/A | N/A | 1.0822 | 0 | N/A | 1.0822
BRAND | Circuit | Distribution | 1.5346 |  | HFTD 3 | 0.00058186 | 0.00029505 | 0.00028681 | 0.023631 | 0.012321 | 0.0040642 | 0.0072455 | N/A | 0.013325 | 0.012486 | N/A | N/A | 1.061 | 0.021524 | N/A | 1.061
BRAUN | Circuit | Distribution | 0.26648 |  | HFTD 2 | 0.0030583 | 0.0030174 | 4.089e-05 | 0.0093079 | 0.0015592 | 0.0015591 | 0.0061895 | N/A | 7.6631e-05 | 0.32418 | N/A | N/A | 1.0891 | 0.5336 | N/A | 1.0891
BRENNAN | Circuit | Distribution | 6.54 |  | HFTD 3 | 0.022008 | 0.021921 | 8.7177e-05 | 0.0076356 | 0.0033409 | 0.00064126 | 0.0036535 | N/A | 0.015629 | 2.8709 | N/A | N/A | 1.1256 | 0.0055779 | N/A | 1.1256
BROADCAST | Circuit | Distribution | 14.5412 |  | HFTD 3 | 0.0013945 | 0.0013944 | 1.1989e-07 | 0.0014032 | 0.0007149 | 6.2782e-05 | 0.00062551 | N/A | 0.02267 | 0.99372 | N/A | N/A | 1.6 | 5.2886e-06 | N/A | 1.6
BROOKINGS | Circuit | Distribution | 0.29152 |  | HFTD 3 | 5.5723e-05 | 5.5131e-05 | 5.9215e-07 | 0.0050178 | 0.0020172 | 0.00082168 | 0.002179 | N/A | 0.024078 | 0.010987 | N/A | N/A | 1 | 2.4594e-05 | N/A | 1
BRUMFIELD | Circuit | Distribution | 1.1456 |  | HFTD 2 | 0.014814 | 0.014812 | 2.0878e-06 | 0.0042658 | 0.002019 | 0.00010353 | 0.0021433 | N/A | 0.00067762 | 3.4722 | N/A | N/A | 1.0184 | 0.0030811 | N/A | 1.0184
BRYDON | Circuit | Distribution | 4.2192 |  | HFTD 3 | 0.0077381 | 0.0077189 | 1.9186e-05 | 0.0095234 | 0.0048765 | 0.00033894 | 0.004308 | N/A | 0.0067233 | 0.81052 | N/A | N/A | 1.1749 | 0.0028537 | N/A | 1.1749
BRYN MAWR | Circuit | Distribution | 1.4355 |  | HFTD 3 | 0.0070994 | 0.0070831 | 1.6252e-05 | 0.0045137 | 0.0021 | 0.00041369 | 0.0020001 | N/A | 0.0010493 | 1.5692 | N/A | N/A | 1.0552 | 0.015487 | N/A | 1.0552
BUCKBOARD | Circuit | Distribution | 2.5689 |  | HFTD 2 | 0.003137 | 0.0031207 | 1.6329e-05 | 0.0053261 | 0.002334 | 0.00036583 | 0.0026262 | N/A | 0.0022624 | 0.58593 | N/A | N/A | 1.2333 | 0.0072175 | N/A | 1.2333
BUCKHORN | Circuit | Distribution | 44.0293 |  | HFTD 3 | 0.0032446 | 0.0032384 | 6.2131e-06 | 0.0036654 | 0.0024814 | 0.00016004 | 0.0010239 | N/A | 0.027717 | 0.8835 | N/A | N/A | 1.1199 | 0.00022416 | N/A | 1.1199
BUCKNER | Circuit | Distribution | 7.3119 |  | HFTD 3 | 0.002065 | 0.0019981 | 6.6826e-05 | 0.012631 | 0.0071623 | 0.0018878 | 0.0035813 | N/A | 0.017907 | 0.15819 | N/A | N/A | 1.0761 | 0.0037319 | N/A | 1.0761
BUFFER | Circuit | Distribution | 4.7902 |  | HFTD 3 | 0.0059165 | 0.0058859 | 3.0657e-05 | 0.0015547 | 0.00086476 | 9.2996e-05 | 0.00059694 | N/A | 0.01102 | 3.7859 | N/A | N/A | 1.2075 | 0.0027819 | N/A | 1.2075
BUNDY | Circuit | Distribution | 0.69105 |  | HFTD 2 | 0.012678 | 0.012603 | 7.4968e-05 | 0.0089332 | 0.0052204 | 0.00015788 | 0.003555 | N/A | 0.0003639 | 1.4108 | N/A | N/A | 1.0488 | 0.20601 | N/A | 1.0488
BURGUNDY | Circuit | Distribution | 2.8656 |  | HFTD 2 | 0.0028698 | 0.002468 | 0.00040179 | 0.0065757 | 0.0015934 | 0.0004794 | 0.0045028 | N/A | 0.0039544 | 0.37533 | N/A | N/A | 1.3631 | 0.10161 | N/A | 1.3631
BURLESON | Circuit | Distribution | 3.78 |  | HFTD 3 | 0.00043007 | 8.4409e-05 | 0.00034566 | 0.0069177 | 0.004087 | 0.00043902 | 0.0023917 | N/A | 0.065383 | 0.012202 | N/A | N/A | 1.097 | 0.0052867 | N/A | 1.097
BURNS | Circuit | Distribution | 2.5887 |  | HFTD 2 | 0.027913 | 0.027882 | 3.0905e-05 | 0.0088052 | 0.0033262 | 0.0033426 | 0.0021364 | N/A | 0.0048702 | 3.1665 | N/A | N/A | 1.1249 | 0.0063457 | N/A | 1.1249
BURNT MOUNTAIN | Circuit | Distribution | 12.7913 | Top 5% Highest Risk | HFTD Tier 2 | 0.047468 | 0.047428 | 3.9249e-05 | 0.0062446 | 0.0052439 | 0.00023612 | 0.0007646 | N/A | 0.017528 | 7.5951 | N/A | N/A | 1.0933 | 0.0022392 | N/A | 1.0933
BUTTERFIELD | Circuit | Distribution | 6.6482 |  | HFTD 2 | 0.015488 | 0.015473 | 1.5488e-05 | 0.00423 | 0.0020076 | 9.2719e-05 | 0.0021297 | N/A | 0.010871 | 3.6578 | N/A | N/A | 1.0688 | 0.0014247 | N/A | 1.0688
CABANA | Circuit | Distribution | 1.1873 |  | HFTD 2 | 0.025329 | 0.024859 | 0.00047066 | 0.014455 | 0.0044128 | 0.00030266 | 0.0097397 | N/A | 0.0072044 | 1.7197 | N/A | N/A | 1.0963 | 0.065329 | N/A | 1.0963
CABOOSE | Circuit | Distribution | 0.26705 |  | HFTD 2 | 5.5299e-05 | 5.5299e-05 | 0 | 0.0052666 | 0.0017416 | 0.00035608 | 0.003169 | N/A | 0 | 0.0105 | N/A | N/A | 1.0664 |  | N/A | 1.0664
CACHUMA | Circuit | Distribution | 45.7843 |  | HFTD 3 | 0.0038361 | 0.0038331 | 3.0481e-06 | 0.0055793 | 0.0032023 | 0.00057628 | 0.0018007 | N/A | 0.016904 | 0.68701 | N/A | N/A | 1.1603 | 0.00018032 | N/A | 1.1603
CACTUS | Circuit | Distribution | 0.90122 |  | HFTD 2 | 0.0018557 | 0.0018526 | 3.0384e-06 | 0.0032055 | 0.0015917 | 5.1681e-05 | 0.001562 | N/A | 0.0023319 | 0.57796 | N/A | N/A | 1.4825 | 0.001303 | N/A | 1.4825
CADENA | Circuit | Distribution | 2.1159 |  | HFTD 3 | 0.0013479 | 0.0013349 | 1.2994e-05 | 0.011141 | 0.0058751 | 0.00056829 | 0.0046981 | N/A | 0.0079238 | 0.11982 | N/A | N/A | 1.0296 | 0.0016399 | N/A | 1.0296
CADILLAC | Circuit | Distribution | 1.4882 |  | HFTD 2 | 0.0052792 | 0.0052782 | 1.0105e-06 | 0.010266 | 0.0056447 | 0.00044987 | 0.0041713 | N/A | 0.00034576 | 0.51415 | N/A | N/A | 1.1546 | 0.0029226 | N/A | 1.1546
CADWAY | Circuit | Distribution | 5.9685 |  | HFTD 3 | 0.0045792 | 0.0045405 | 3.8726e-05 | 0.013603 | 0.0064788 | 0.00067937 | 0.0064445 | N/A | 0.0054196 | 0.3338 | N/A | N/A | 1.0924 | 0.0071455 | N/A | 1.0924
CAESAR | Circuit | Distribution | 3.4979 |  | HFTD 3 | 0.0026324 | 0.0024869 | 0.00014544 | 0.020624 | 0.0046907 | 7.0533e-05 | 0.015863 | N/A | 0.034279 | 0.12059 | N/A | N/A | 1.1102 | 0.0042427 | N/A | 1.1102
CAIN RANCH | Circuit | Distribution | 1.8893 |  | HFTD 2 | 0.0024717 | 0.002454 | 1.7675e-05 | 0.0031406 | 0.0018554 | 4.5246e-05 | 0.00124 | N/A | 0.0098133 | 0.78138 | N/A | N/A | 1.4421 | 0.0018011 | N/A | 1.4421
CAL POLY | Circuit | Distribution | 0.72598 |  | HFTD 2 | 0.0058505 | 0.0058375 | 1.2974e-05 | 0.01039 | 0.004567 | 0.0013979 | 0.0044254 | N/A | 0.0003445 | 0.56182 | N/A | N/A | 1.1971 | 0.03766 | N/A | 1.1971
CALAMAR | Circuit | Distribution | 7.9294 |  | HFTD 3 | 0.0029346 | 0.0029346 | 6.2957e-09 | 0.0023226 | 0.0017049 | 0.00011133 | 0.00050634 | N/A | 0.0028664 | 1.2635 | N/A | N/A | 1.2581 | 2.1964e-06 | N/A | 1.2581
CALGROVE | Circuit | Distribution | 16.2648 |  | HFTD 3 | 0.0025957 | 0.0025502 | 4.5534e-05 | 0.0082164 | 0.0044616 | 0.00014505 | 0.0036097 | N/A | 0.034589 | 0.31038 | N/A | N/A | 1.1838 | 0.0013164 | N/A | 1.1838
CALIBER | Circuit | Distribution | 16.1115 |  | HFTD 2 | 0.025436 | 0.025402 | 3.4033e-05 | 0.0043415 | 0.001638 | 1.6088e-05 | 0.0026874 | N/A | 0.018462 | 5.8509 | N/A | N/A | 1.2188 | 0.0018434 | N/A | 1.2188
CALIENTE | Circuit | Distribution | 27.7673 |  | HFTD 3 | 0.03682 | 0.036819 | 5.9827e-07 | 0.0095953 | 0.0072024 | 3.8779e-05 | 0.0023542 | N/A | 0.025144 | 3.8372 | N/A | N/A | 1.0726 | 2.3794e-05 | N/A | 1.0726
CALIMESA | Circuit | Distribution | 9.2271 |  | HFTD 2 | 0.024607 | 0.024603 | 3.4007e-06 | 0.0068763 | 0.0039276 | 0.00017725 | 0.0027714 | N/A | 0.011118 | 3.578 | N/A | N/A | 1.1003 | 0.00030588 | N/A | 1.1003
CALORA | Circuit | Distribution | 0.3697 |  | HFTD 2 | 0.00042479 | 0.00035983 | 6.4967e-05 | 0.003752 | 0.00028074 | 0.00010408 | 0.0033671 | N/A | 0.00078592 | 0.095903 | N/A | N/A | 1.0676 | 0.082664 | N/A | 1.0676
CALSPAR | Circuit | Distribution | 0.29921 |  | HFTD 2 | 0.010187 | 0.010133 | 5.419e-05 | 0.0087722 | 0.0055926 | 0.00044593 | 0.0027337 | N/A | 0.00012076 | 1.1551 | N/A | N/A | 1.0851 | 0.44875 | N/A | 1.0851
CALSTATE | Circuit | Distribution | 1.0648 |  | HFTD 3 | 0.0082926 | 0.0078088 | 0.00048376 | 0.0031089 | 0.0023124 | 0.00017108 | 0.00062542 | N/A | 0.015106 | 2.5117 | N/A | N/A | 1.1554 | 0.032025 | N/A | 1.1554
CAMP ANGELUS | Circuit | Distribution | 3.6005 |  | HFTD 3 | 0.0016985 | 0.0016797 | 1.8845e-05 | 0.010158 | 0.0079488 | 0.00063784 | 0.001571 | N/A | 0.032827 | 0.16536 | N/A | N/A | 1.5172 | 0.00057407 | N/A | 1.5172
CAMP NELSON | Circuit | Distribution | 7.4758 |  | HFTD 2 | 0.0039659 | 0.003964 | 1.8596e-06 | 0.015436 | 0.011383 | 0.003208 | 0.00084455 | N/A | 0.0068214 | 0.25681 | N/A | N/A | 1.318 | 0.00027261 | N/A | 1.318
CAMPANULA | Circuit | Distribution | 27.8429 |  | HFTD 2 | 0.018934 | 0.018886 | 4.8734e-05 | 0.0061502 | 0.0041147 | 9.6434e-05 | 0.001939 | N/A | 0.023037 | 3.0708 | N/A | N/A | 1.2867 | 0.0021155 | N/A | 1.2867
CAMPBELL | Circuit | Distribution | 3.6338 |  | HFTD 2 | 0.00052021 | 0.00052021 | 0 | 0.0014649 | 0.00035924 | 0.0002252 | 0.00088049 | N/A | 0 | 0.35511 | N/A | N/A | 1.1208 |  | N/A | 1.1208
CAMPROCK | Circuit | Distribution | 4.44 |  | HFTD 2 | 8.6781e-05 | 8.6137e-05 | 6.4449e-07 | 0.0012149 | 0.00071966 | 2.4951e-06 | 0.00049274 | N/A | 0.0051334 | 0.0709 | N/A | N/A | 1.1924 | 0.00012555 | N/A | 1.1924
CANAL | Circuit | Distribution | 4.6496 |  | HFTD 3 | 0.0062282 | 0.006228 | 1.61e-07 | 0.0048624 | 0.0026354 | 0.00042081 | 0.0018062 | N/A | 0.0063259 | 1.2808 | N/A | N/A | 1.7237 | 2.5451e-05 | N/A | 1.7237
CANCUN | Circuit | Distribution | 0.36744 |  | HFTD 3 | 0.0040743 | 0.0040646 | 9.7049e-06 | 0.013121 | 0.0011532 | 0.00080924 | 0.011159 | N/A | 0.00032458 | 0.30977 | N/A | N/A | 1.0659 | 0.0299 | N/A | 1.0659
CANEBRAKE | Circuit | Distribution | 65.5423 |  | HFTD 3 | 0.023837 | 0.023837 | 0 | 0.0066443 | 0.0049997 | 0.00021049 | 0.001434 | N/A | 0.15232 | 3.5877 | N/A | N/A | 1.1683 | 0 | N/A | 1.1683
CANET | Circuit | Distribution | 17.1257 |  | HFTD 3 | 0.0029952 | 0.0029922 | 3.0041e-06 | 0.013226 | 0.0070381 | 0.00055032 | 0.0056379 | N/A | 0.0084673 | 0.22623 | N/A | N/A | 1.0586 | 0.00035478 | N/A | 1.0586
CANTINA | Circuit | Distribution | 2.1155 |  | HFTD 2 | 0.0031639 | 0.0027053 | 0.00045853 | 0.013434 | 0.005771 | 0.0015586 | 0.0061044 | N/A | 0.0098752 | 0.20138 | N/A | N/A | 1.0312 | 0.046432 | N/A | 1.0312
CAPANERO | Circuit | Distribution | 7.2024 |  | HFTD 2 | 0.013544 | 0.013544 | 0 | 0.0073345 | 0.0057192 | 0.0014249 | 0.00019037 | N/A | 0.002461 | 1.8466 | N/A | N/A | 1.3969 | 0 | N/A | 1.3969
CARANCHO | Circuit | Distribution | 37.2134 |  | HFTD 3 | 0.0075431 | 0.0075429 | 1.2184e-07 | 0.0055388 | 0.003029 | 0.00034516 | 0.0021646 | N/A | 0.013659 | 1.3618 | N/A | N/A | 1.117 | 8.9201e-06 | N/A | 1.117
CARATAN | Circuit | Distribution | 2.9395 |  | HFTD 2 | 0.00022144 | 0.00022097 | 4.6716e-07 | 0.0019617 | 0.00125 | 8.585e-05 | 0.00062579 | N/A | 0.00031118 | 0.11264 | N/A | N/A | 1.1555 | 0.0015013 | N/A | 1.1555
CARBINE | Circuit | Distribution | 2.5048 |  | HFTD 2 | 0.036683 | 0.036671 | 1.1279e-05 | 0.0050303 | 0.0030916 | 0.00011546 | 0.0018232 | N/A | 0.0015154 | 7.2901 | N/A | N/A | 1.0962 | 0.0074426 | N/A | 1.0962
CARDINAL | Circuit | Distribution | 4.8972 |  | HFTD 3 | 0.030932 | 0.030931 | 1.2003e-06 | 0.014558 | 0.012312 | 0.0010684 | 0.0011777 | N/A | 0.001221 | 2.1246 | N/A | N/A | 1.542 | 0.00098302 | N/A | 1.542
CAREY | Circuit | Distribution | 1.1049 |  | HFTD 2 | 0.0023049 | 0.0017893 | 0.00051567 | 0.0058959 | 0.0025404 | 0.00050619 | 0.0028493 | N/A | 0.0021767 | 0.30348 | N/A | N/A | 1.0731 | 0.2369 | N/A | 1.0731
CARLET | Circuit | Distribution | 3.0191 |  | HFTD 3 | 0.011947 | 0.011909 | 3.8067e-05 | 0.026404 | 0.013521 | 0.0011799 | 0.011703 | N/A | 0.0053024 | 0.45104 | N/A | N/A | 1.0581 | 0.0071792 | N/A | 1.0581
CARMELITA | Circuit | Distribution | 4.5327 |  | HFTD 2 | 0.0016643 | 0.0009921 | 0.00067223 | 0.0099894 | 0.006619 | 0.0018153 | 0.0015551 | N/A | 0.0071879 | 0.099315 | N/A | N/A | 1.1317 | 0.093522 | N/A | 1.1317
CARNEGIE | Circuit | Distribution | 1.0304 |  | HFTD 2 | 0.0063845 | 0.0063613 | 2.3262e-05 | 0.014313 | 0.010579 | 0.0012868 | 0.0024475 | N/A | 0.00015994 | 0.44444 | N/A | N/A | 1.0974 | 0.14544 | N/A | 1.0974
CARRIAGE | Circuit | Distribution | 4.7493 |  | HFTD 2 | 0.009451 | 0.0092783 | 0.00017271 | 0.0092693 | 0.0032125 | 0.00028892 | 0.0057679 | N/A | 0.0068823 | 1.001 | N/A | N/A | 1.1695 | 0.025094 | N/A | 1.1695
CARVER | Circuit | Distribution | 15.7689 |  | HFTD 2 | 0.00051702 | 0.00051702 | 0 | 0.0010129 | 0.00074539 | 4.5753e-05 | 0.00022173 | N/A | 0.0012608 | 0.51045 | N/A | N/A | 1.0852 | 0 | N/A | 1.0852
CASCADA | Circuit | Distribution | 1.9705 |  | HFTD 3 | 0.0070259 | 0.007024 | 1.8366e-06 | 0.0066922 | 0.0042117 | 0.0014547 | 0.0010257 | N/A | 0.018727 | 1.0496 | N/A | N/A | 1.4344 | 9.807e-05 | N/A | 1.4344
CASCADE | Circuit | Distribution | 5.0854 |  | HFTD 3 | 0.014128 | 0.014128 | 0 | 0.0028252 | 0.0022526 | 0.00023362 | 0.00033893 | N/A | 0 | 5.0007 | N/A | N/A | 1.1004 |  | N/A | 1.1004
CASE | Circuit | Distribution | 6.2752 |  | HFTD 2 | 0.0075019 | 0.0075019 | 3.5728e-09 | 0.0032069 | 0.00097392 | 9.8882e-05 | 0.0021341 | N/A | 0.0045969 | 2.3393 | N/A | N/A | 1.3333 | 7.7722e-07 | N/A | 1.3333
CASEY | Circuit | Distribution | 0.6257 |  | HFTD 3 | 0.002725 | 0.0026922 | 3.274e-05 | 0.011516 | 0.0065594 | 0.00079814 | 0.0041586 | N/A | 0.00021008 | 0.23378 | N/A | N/A | 1.0704 | 0.15584 | N/A | 1.0704
CASPER | Circuit | Distribution | 2.058 |  | HFTD 2 | 9.4991e-05 | 9.3968e-05 | 1.0231e-06 | 0.0022284 | 0.0012606 | 8.5571e-05 | 0.00088228 | N/A | 0.0029859 | 0.042168 | N/A | N/A | 1.4897 | 0.00034266 | N/A | 1.4897
CASSIDY | Circuit | Distribution | 5.1732 |  | HFTD 3 | 0.0029079 | 0.0028657 | 4.2187e-05 | 0.02103 | 0.011488 | 0.00044661 | 0.0090955 | N/A | 0.0026302 | 0.13627 | N/A | N/A | 1.0708 | 0.016039 | N/A | 1.0708
CASTRO | Circuit | Distribution | 28.6841 |  | HFTD 3 | 0.009872 | 0.0098608 | 1.1189e-05 | 0.0071082 | 0.0051587 | 0.00032697 | 0.0016226 | N/A | 0.019018 | 1.3872 | N/A | N/A | 1.2407 | 0.00058834 | N/A | 1.2407
CATARACT | Circuit | Distribution | 1.0456 |  | HFTD 2 | 0.0080949 | 0.0080268 | 6.8154e-05 | 0.022628 | 0.0086205 | 0.0005724 | 0.013435 | N/A | 0.0014496 | 0.35473 | N/A | N/A | 1.1667 | 0.047017 | N/A | 1.1667
CEDAR GLEN | Circuit | Distribution | 8.2504 |  | HFTD 3 | 0.025431 | 0.025407 | 2.3828e-05 | 0.011752 | 0.0078829 | 0.0018146 | 0.0020546 | N/A | 0.047768 | 2.1619 | N/A | N/A | 1.0568 | 0.00049883 | N/A | 1.0568
CEDAR PINES | Circuit | Distribution | 3.434 |  | HFTD 3 | 0.0025621 | 0.0025349 | 2.7197e-05 | 0.0084624 | 0.0057706 | 0.0011324 | 0.0015595 | N/A | 0.050338 | 0.29954 | N/A | N/A | 1.4249 | 0.00054028 | N/A | 1.4249
CELLO | Circuit | Distribution | 1.5378 |  | HFTD 3 | 0.0061528 | 0.0060894 | 6.3432e-05 | 0.010571 | 0.0056138 | 0.00011346 | 0.0048432 | N/A | 0.013376 | 0.57608 | N/A | N/A | 1.09 | 0.004742 | N/A | 1.09
CENTAUR | Circuit | Distribution | 0.56172 |  | HFTD 2 | 0.0061904 | 0.0061303 | 6.0094e-05 | 0.013653 | 0.0063924 | 0.00053697 | 0.0067232 | N/A | 0.002347 | 0.44903 | N/A | N/A | 1.1136 | 0.025605 | N/A | 1.1136
CERAMIC | Circuit | Distribution | 0.51044 |  | HFTD 2 | 0.0025527 | 0.0025103 | 4.2372e-05 | 0.0031893 | 0.0015991 | 0.00031563 | 0.0012746 | N/A | 0.00074907 | 0.7871 | N/A | N/A | 1.1456 | 0.056566 | N/A | 1.1456
CEREAL | Circuit | Distribution | 10.6516 |  | HFTD 3 | 0.018766 | 0.018763 | 3.6846e-06 | 0.014138 | 0.0074037 | 0.00093827 | 0.0057964 | N/A | 0.011698 | 1.3271 | N/A | N/A | 1.1783 | 0.00031499 | N/A | 1.1783
CERRITO | Circuit | Distribution | 1.7188 |  | HFTD 3 | 0.010478 | 0.010388 | 8.9759e-05 | 0.0064886 | 0.0018879 | 0.0013582 | 0.0032426 | N/A | 0.010769 | 1.601 | N/A | N/A | 1.1782 | 0.0083349 | N/A | 1.1782
CEYLON | Circuit | Distribution | 1.7119 |  | HFTD 2 | 0.0042075 | 0.0041869 | 2.0553e-05 | 0.01084 | 0.0030372 | 0.0016389 | 0.006164 | N/A | 0.00038093 | 0.38625 | N/A | N/A | 1.1474 | 0.053955 | N/A | 1.1474
CHALON | Circuit | Distribution | 0.86189 |  | HFTD 2 | 0.0172 | 0.0172 | 0 | 0.0024811 | 0.001542 | 0.00016663 | 0.00077241 | N/A | 0.0080259 | 6.9327 | N/A | N/A | 2 | 0 | N/A | 2
CHAMPION | Circuit | Distribution | 0.34892 |  | HFTD 2 | 0.020431 | 0.020431 | 0 | 0.0017813 | 0.00081743 | 0.00051186 | 0.00045201 | N/A | 0.0040129 | 11.4695 | N/A | N/A | 1.0651 | 0 | N/A | 1.0651
CHANTRY | Circuit | Distribution | 5.9262 |  | HFTD 3 | 0.013156 | 0.013136 | 2.0052e-05 | 0.016848 | 0.0066857 | 0.0032183 | 0.0069445 | N/A | 0.0077523 | 0.77966 | N/A | N/A | 1.0521 | 0.0025865 | N/A | 1.0521
CHARDONNAY | Circuit | Distribution | 31.4013 |  | HFTD 3 | 0.013816 | 0.013816 | 1.5467e-07 | 0.0024724 | 0.0014362 | 0.00014293 | 0.00089327 | N/A | 0.0069593 | 5.5882 | N/A | N/A | 1.2249 | 2.2225e-05 | N/A | 1.2249
CHARIOT | Circuit | Distribution | 1.6207 |  | HFTD 3 | 0.015612 | 0.015353 | 0.00025928 | 0.04133 | 0.013433 | 0.00013013 | 0.027767 | N/A | 0.024078 | 0.37147 | N/A | N/A | 1.0933 | 0.010769 | N/A | 1.0933
CHARLIE | Circuit | Distribution | 3.0094 |  | HFTD 2 | 0.0029804 | 0.0026352 | 0.00034519 | 0.0047839 | 0.0025269 | 8.9681e-05 | 0.0021673 | N/A | 0.009084 | 0.55085 | N/A | N/A | 1.293 | 0.037999 | N/A | 1.293
CHARLTON | Circuit | Distribution | 2.1557 |  | HFTD 2 | 0.0058008 | 0.0057307 | 7.0091e-05 | 0.010838 | 0.0046194 | 0.002706 | 0.0035122 | N/A | 0.0024146 | 0.52877 | N/A | N/A | 1.1286 | 0.029027 | N/A | 1.1286
CHATEAU | Circuit | Distribution | 0.83903 |  | HFTD 2 | 0.001231 | 0.001231 | 0 | 0.0067763 | 0.0052991 | 8.0193e-05 | 0.0013969 | N/A | 0.023251 | 0.18166 | N/A | N/A |  | 0 | N/A
CHATTANOOGA | Circuit | Distribution | 1.8805 |  | HFTD 2 | 0.022523 | 0.022488 | 3.4979e-05 | 0.0091025 | 0.0039022 | 0.0013113 | 0.0038891 | N/A | 0.0040449 | 2.4705 | N/A | N/A | 1.0687 | 0.0086477 | N/A | 1.0687
CHAWA | Circuit | Distribution | 76.0674 |  | HFTD 3 | 0.011725 | 0.011724 | 5.5994e-07 | 0.0020093 | 0.0015302 | 7.0603e-05 | 0.00040846 | N/A | 0.0093208 | 5.8349 | N/A | N/A | 1.1602 | 6.0075e-05 | N/A | 1.1602
CHELLA | Circuit | Distribution | 0.91495 |  | HFTD 2 | 0.005073 | 0.0050666 | 6.4033e-06 | 0.016917 | 0.0063022 | 0.0012616 | 0.0093532 | N/A | 0 | 0.2995 | N/A | N/A | 1.0895 | inf | N/A | 1.0895
CHEVELLE | Circuit | Distribution | 6.416 |  | HFTD 3 | 0.0042789 | 0.0040284 | 0.00025047 | 0.0011018 | 0.00074451 | 6.1936e-05 | 0.00029534 | N/A | 0.045345 | 3.6562 | N/A | N/A | 1.2144 | 0.0055238 | N/A | 1.2144
CHICO | Circuit | Distribution | 0.55044 |  | HFTD 2 | 0.0057877 | 0.0057877 | 0 | 0.045461 | 0.010315 | 0.01796 | 0.017186 | N/A | 0.00012055 | 0.12731 | N/A | N/A | 1.0347 | 0 | N/A | 1.0347
CHILLON | Circuit | Distribution | 7.8973 |  | HFTD 3 | 0.013423 | 0.013375 | 4.7529e-05 | 0.007705 | 0.0063708 | 0.00033731 | 0.00099692 | N/A | 0.065309 | 1.7359 | N/A | N/A | 1.3457 | 0.00072776 | N/A | 1.3457
CHINA PEAK | Circuit | Distribution | 2.4883 |  | HFTD 3 | 0.004475 | 0.0044744 | 5.9334e-07 | 0.027931 | 0.017994 | 0.0014531 | 0.0084838 | N/A | 0.0088978 | 0.1602 | N/A | N/A | 1.125 | 6.6683e-05 | N/A | 1.125
CHOLLA | Circuit | Distribution | 12.7876 |  | HFTD 2 | 0.018891 | 0.018887 | 3.6823e-06 | 0.0046667 | 0.0034254 | 0.00020254 | 0.0010387 | N/A | 0.028021 | 4.0472 | N/A | N/A | 1.2014 | 0.00013141 | N/A | 1.2014
CHUCK WAGON | Circuit | Distribution | 0.78716 |  | HFTD 3 | 0.01225 | 0.012205 | 4.4882e-05 | 0.01863 | 0.0064854 | 0.00021766 | 0.011927 | N/A | 0.0031712 | 0.65513 | N/A | N/A | 1.07 | 0.014153 | N/A | 1.07
CHUMASH | Circuit | Distribution | 0.39535 | Top 5% Highest Risk | HFTD Tier 3 | 0.049156 | 0.049147 | 8.5758e-06 | 0.044912 | 0.016901 | 0.0020436 | 0.025968 | N/A | 0.014714 | 1.0943 | N/A | N/A | 1.0515 | 0.00058283 | N/A | 1.0515
CIENIGITAS | Circuit | Distribution | 0.98264 |  | HFTD 2 | 0.0037659 | 0.0036552 | 0.00011072 | 0.0050006 | 0.0041207 | 0.00022379 | 0.00065613 | N/A | 0.0012919 | 0.73094 | N/A | N/A | 1.0386 | 0.085701 | N/A | 1.0386
CIRCLE | Circuit | Distribution | 10.6322 |  | HFTD 2 | 0.039453 | 0.039452 | 4.7507e-07 | 0.010723 | 0.0056569 | 6.0159e-05 | 0.0050058 | N/A | 0.018805 | 3.6793 | N/A | N/A | 1.7341 | 2.5263e-05 | N/A | 1.7341
CISCO | Circuit | Distribution | 0.6594 |  | HFTD 3 | 0.014136 | 0.0141 | 3.5709e-05 | 0.012405 | 0.0086122 | 0.000462 | 0.0033307 | N/A | 0.0023684 | 1.1367 | N/A | N/A | 1.0861 | 0.015078 | N/A | 1.0861
CITY OF BANNING #2 | Circuit | Distribution | 0.37327 |  | HFTD 3 | 0.0032459 | 0.0032459 | 0 | 0.0014506 | 0.00013114 | 4.2347e-05 | 0.0012771 | N/A | 0 | 2.2377 | N/A | N/A |  |  | N/A
CLARINET | Circuit | Distribution | 9.2693 |  | HFTD 3 | 0.006829 | 0.0067739 | 5.5044e-05 | 0.0093209 | 0.0038912 | 0.0002451 | 0.0051846 | N/A | 0.030124 | 0.72675 | N/A | N/A | 1.2025 | 0.0018273 | N/A | 1.2025
CLEMSON | Circuit | Distribution | 2.2601 |  | HFTD 2 | 0.0021046 | 0.0020674 | 3.7184e-05 | 0.0061158 | 0.0027119 | 0.0009025 | 0.0025014 | N/A | 0.0028842 | 0.33804 | N/A | N/A | 1.128 | 0.012892 | N/A | 1.128
CLOVE | Circuit | Distribution | 5.112 |  | HFTD 3 | 0.043762 | 0.04376 | 2.6032e-06 | 0.014401 | 0.0059223 | 0.00058812 | 0.0078902 | N/A | 0.0085943 | 3.0387 | N/A | N/A | 1.2044 | 0.0003029 | N/A | 1.2044
CLUB OAKS | Circuit | Distribution | 4.63 |  | HFTD 3 | 0.0071504 | 0.0071502 | 1.2914e-07 | 0.0087401 | 0.0067813 | 0.00044478 | 0.001514 | N/A | 0.010027 | 0.8181 | N/A | N/A |  | 1.2879e-05 | N/A
CLYDESDALE | Circuit | Distribution | 6.4705 |  | HFTD 2 | 0.013397 | 0.013397 | 0 | 0.0038355 | 0.0029341 | 0.00014251 | 0.00075889 | N/A | 0 | 3.4929 | N/A | N/A | 1.2014 |  | N/A | 1.2014
COACHELLA | Circuit | Distribution | 8.2951 |  | HFTD 2 | 0.0002994 | 0.0002994 | 0 | 0.00011036 | 7.0621e-05 | 5.1844e-06 | 3.4556e-05 | N/A | 0.021162 | 2.7129 | N/A | N/A | 1.0902 | 0 | N/A | 1.0902
COBRA | Circuit | Distribution | 1.6957 |  | HFTD 3 | 0.00075569 | 0.00062039 | 0.0001353 | 0.017988 | 0.012168 | 0.00039039 | 0.0054295 | N/A | 0.016274 | 0.034489 | N/A | N/A | 1.0719 | 0.0083137 | N/A | 1.0719
CODONA | Circuit | Distribution | 0.36972 |  | HFTD 2 | 0.0049006 | 0.0049006 | 0 | 0.0093738 | 0.0056551 | 0.00053131 | 0.0031875 | N/A | 0 | 0.52279 | N/A | N/A | 1.0623 |  | N/A | 1.0623
COJO | Circuit | Distribution | 5.1333 |  | HFTD 2 | 0.00051239 | 0.00051198 | 4.0711e-07 | 0.0045918 | 0.0021497 | 0.00026102 | 0.0021811 | N/A | 0.021147 | 0.1115 | N/A | N/A | 1.2297 | 1.9252e-05 | N/A | 1.2297
COLDWATER | Circuit | Distribution | 1.1595 |  | HFTD 2 | 0.00013328 | 0.00013291 | 3.7108e-07 | 0.017952 | 0.0052698 | 0.0084168 | 0.0042658 | N/A | 0.0025552 | 0.0074033 | N/A | N/A | 1.1908 | 0.00014522 | N/A | 1.1908
COLLIER | Circuit | Distribution | 5.7381 |  | HFTD 3 | 0.024585 | 0.02458 | 4.6902e-06 | 0.010614 | 0.0040347 | 0.00038289 | 0.0061969 | N/A | 0.0023684 | 2.3157 | N/A | N/A | 1.0743 | 0.0019804 | N/A | 1.0743
COLLINS | Circuit | Distribution | 0.77692 |  | HFTD 3 | 0.0015459 | 0.0010914 | 0.00045447 | 0.031006 | 0.006159 | 0.0003826 | 0.024464 | N/A | 0.017478 | 0.035201 | N/A | N/A | 1.048 | 0.026002 | N/A | 1.048
COLT | Circuit | Distribution | 0.76925 |  | HFTD 2 | 0.015067 | 0.015062 | 5.0565e-06 | 0.0057591 | 0.0030737 | 0.00018917 | 0.0024962 | N/A | 0.0029321 | 2.6153 | N/A | N/A | 1.0541 | 0.0017245 | N/A | 1.0541
CONCEPCION | Circuit | Distribution | 29.4063 |  | HFTD 2 | 0.00064993 | 0.0006477 | 2.2338e-06 | 0.0039395 | 0.0030709 | 0.00011514 | 0.00075352 | N/A | 0.061667 | 0.16441 | N/A | N/A | 1.222 | 3.6224e-05 | N/A | 1.222
CONCORD | Circuit | Distribution | 1.1406 |  | HFTD 2 | 0.0069128 | 0.0069128 | 0 | 0.012316 | 0.0028512 | 0.0049084 | 0.0045568 | N/A | 0 | 0.56127 | N/A | N/A | 1.0296 |  | N/A | 1.0296
CONDOR | Circuit | Distribution | 56.7259 |  | HFTD 3 | 0.0028138 | 0.0028128 | 1.0697e-06 | 0.00032496 | 0.00029616 | 9.1885e-06 | 1.9618e-05 | N/A | 0.02763 | 8.6557 | N/A | N/A | 1.5908 | 3.8716e-05 | N/A | 1.5908
CONEJO | Circuit | Distribution | 1.4858 |  | HFTD 3 | 0.00020909 | 0.00016084 | 4.8244e-05 | 0.018313 | 0.006143 | 0.001641 | 0.010529 | N/A | 0.0066882 | 0.0087831 | N/A | N/A | 1.046 | 0.0072133 | N/A | 1.046
CONESTOGA | Circuit | Distribution | 8.744 |  | HFTD 2 | 0.0044948 | 0.0044892 | 5.5455e-06 | 0.0080657 | 0.0042039 | 0.000615 | 0.0032467 | N/A | 0.0046406 | 0.55659 | N/A | N/A | 1.1305 | 0.001195 | N/A | 1.1305
CONFERENCE | Circuit | Distribution | 1.0782 |  | HFTD 3 | 0.0036051 | 0.0036051 | 0 | 0.025425 | 0.012792 | 0.0036648 | 0.0089689 | N/A | 0 | 0.14179 | N/A | N/A | 1.5318 |  | N/A | 1.5318
CONINE | Circuit | Distribution | 7.6383 |  | HFTD 3 | 0.016844 | 0.016839 | 5.8139e-06 | 0.0078529 | 0.0037029 | 0.00084397 | 0.003306 | N/A | 0.010405 | 2.1442 | N/A | N/A | 1.0938 | 0.00055876 | N/A | 1.0938
CONWAY | Circuit | Distribution | 15.035 |  | HFTD 2 | 0.002053 | 0.0020444 | 8.6731e-06 | 0.0016327 | 0.0011687 | 8.0399e-06 | 0.00045592 | N/A | 0.094933 | 1.2522 | N/A | N/A | 1.501 | 9.1361e-05 | N/A | 1.501
COOLER | Circuit | Distribution | 0.64014 |  | HFTD 3 | 0.014121 | 0.013848 | 0.00027294 | 0.005021 | 0.001333 | 0.00026474 | 0.0034233 | N/A | 0.021943 | 2.7581 | N/A | N/A | 1.1209 | 0.012439 | N/A | 1.1209
COOLEY | Circuit | Distribution | 2.4223 |  | HFTD 2 | 0.0021803 | 0.0019791 | 0.00020126 | 0.0065462 | 0.0031664 | 0.00012295 | 0.0032569 | N/A | 0.0035356 | 0.30232 | N/A | N/A | 1.0568 | 0.056924 | N/A | 1.0568
COPPERHEAD | Circuit | Distribution | 0.72918 |  | HFTD 3 | 0.00061122 | 0.00048415 | 0.00012708 | 0.063325 | 0.0095893 | 0.00040328 | 0.053333 | N/A | 0.0073864 | 0.0076454 | N/A | N/A | 1.0634 | 0.017204 | N/A | 1.0634
CORINTH | Circuit | Distribution | 4.4268 |  | HFTD 2 | 0.013396 | 0.013396 | 0 | 0.003958 | 0.0015862 | 0.00012607 | 0.0022458 | N/A | 0.0026492 | 3.3844 | N/A | N/A | 1.0733 | 0 | N/A | 1.0733
CORNWALL | Circuit | Distribution | 2.4042 |  | HFTD 2 | 0.0013255 | 0.0013234 | 2.116e-06 | 0.011293 | 0.0014518 | 0.00040664 | 0.0094343 | N/A | 0.00052012 | 0.11719 | N/A | N/A | 1.0914 | 0.0040683 | N/A | 1.0914
CORONITA | Circuit | Distribution | 0.4139 |  | HFTD 3 | 0.012757 | 0.012404 | 0.00035276 | 0.015668 | 0.0048121 | 0.000696 | 0.01016 | N/A | 0.014229 | 0.7917 | N/A | N/A | 1.1193 | 0.024791 | N/A | 1.1193
CORSAIR | Circuit | Distribution | 67.0329 |  | HFTD 3 | 0.0036817 | 0.0036815 | 1.8881e-07 | 0.001367 | 0.0010792 | 5.0108e-05 | 0.00023767 | N/A | 0.0068429 | 2.6931 | N/A | N/A | 1.151 | 2.7593e-05 | N/A | 1.151
CORTESE | Circuit | Distribution | 1.94 |  | HFTD 3 | 0.0088599 | 0.0088572 | 2.7135e-06 | 0.010454 | 0.0049275 | 0.0012515 | 0.0042754 | N/A | 0.0065316 | 0.84722 | N/A | N/A | 1.0491 | 0.00041544 | N/A | 1.0491
COTTAGE GROVE | Circuit | Distribution | 3.7584 |  | HFTD 3 | 0.017631 | 0.017578 | 5.2915e-05 | 0.0090483 | 0.004969 | 0.002844 | 0.0012353 | N/A | 0.058028 | 1.9427 | N/A | N/A | 1.0712 | 0.00091188 | N/A | 1.0712
COULTER | Circuit | Distribution | 0.88387 |  | HFTD 3 | 0.00048714 | 0.00048702 | 1.177e-07 | 0.0052431 | 0.0023254 | 0.0013697 | 0.001548 | N/A | 0.020065 | 0.092888 | N/A | N/A | 2 | 5.866e-06 | N/A | 2
COVE | Circuit | Distribution | 2.6439 |  | HFTD 2 | 0.022463 | 0.021122 | 0.0013405 | 0.031064 | 0.025621 | 0.00025303 | 0.00519 | N/A | 0.043492 | 0.67996 | N/A | N/A | 1.5247 | 0.030821 | N/A | 1.5247
COVENTRY | Circuit | Distribution | 14.782 |  | HFTD 3 | 0.017423 | 0.017409 | 1.4337e-05 | 0.010333 | 0.0061932 | 0.00062788 | 0.0035121 | N/A | 0.018725 | 1.6847 | N/A | N/A | 1.0447 | 0.0007657 | N/A | 1.0447
COVEVIEW | Circuit | Distribution | 1.6682 |  | HFTD 2 | 0.0012745 | 0.0012629 | 1.1602e-05 | 0.016137 | 0.0081084 | 0.0014045 | 0.0066239 | N/A | 0.0053442 | 0.07826 | N/A | N/A | 1.1379 | 0.002171 | N/A | 1.1379
CRAB | Circuit | Distribution | 9.4993 |  | HFTD 3 | 0.006183 | 0.006183 | 0 | 0.011818 | 0.0062125 | 0.0010309 | 0.0045751 | N/A | 0.025129 | 0.52316 | N/A | N/A |  | 0 | N/A
CRABTREE | Circuit | Distribution | 4.2056 |  | HFTD 3 | 0.0014877 | 0.0014712 | 1.652e-05 | 0.0079014 | 0.0038192 | 4.8552e-05 | 0.0040336 | N/A | 0.006528 | 0.18619 | N/A | N/A | 1.0732 | 0.0025306 | N/A | 1.0732
CRAM | Circuit | Distribution | 4.8348 |  | HFTD 3 | 0.0026526 | 0.0025273 | 0.00012529 | 0.0023015 | 0.00070087 | 0.00015478 | 0.0014458 | N/A | 0.01028 | 1.0981 | N/A | N/A | 1.1318 | 0.012188 | N/A | 1.1318
CRAWFORD | Circuit | Distribution | 0.4137 | Top 5% Highest Risk | HFTD Tier 2 | 0.099942 | 0.099628 | 0.0003141 | 0.038771 | 0.012888 | 0.012459 | 0.013423 | N/A | 0.020505 | 2.5697 | N/A | N/A | 1.6352 | 0.015318 | N/A | 1.6352
CRESCENTA | Circuit | Distribution | 20.6805 |  | HFTD 3 | 0.018011 | 0.017984 | 2.7096e-05 | 0.01404 | 0.0075412 | 0.0029196 | 0.0035794 | N/A | 0.040434 | 1.2809 | N/A | N/A | 1.4458 | 0.00067014 | N/A | 1.4458
CRESTLINE | Circuit | Distribution | 10.175 |  | HFTD 3 | 0.015607 | 0.015533 | 7.4432e-05 | 0.011276 | 0.0075749 | 0.0014866 | 0.0022142 | N/A | 0.086652 | 1.3775 | N/A | N/A | 1.2957 | 0.00085897 | N/A | 1.2957
CRESTWIND | Circuit | Distribution | 1.3713 |  | HFTD 2 | 0.0037764 | 0.0037764 | 0 | 0.048003 | 0.028068 | 0.0078915 | 0.012044 | N/A | 0.0013376 | 0.07867 | N/A | N/A | 1.3366 | 0 | N/A | 1.3366
CROFT | Circuit | Distribution | 3.6724 |  | HFTD 2 | 0.040148 | 0.040124 | 2.3797e-05 | 0.015476 | 0.0065023 | 0.00082179 | 0.0081515 | N/A | 0.0050694 | 2.5927 | N/A | N/A | 1.0489 | 0.0046942 | N/A | 1.0489
CROSBY | Circuit | Distribution | 4.6763 |  | HFTD 3 | 0.0073254 | 0.0073211 | 4.312e-06 | 0.015858 | 0.01024 | 0.0011967 | 0.0044216 | N/A | 0.0076352 | 0.46166 | N/A | N/A | 1.3991 | 0.00056475 | N/A | 1.3991
CROSSON | Circuit | Distribution | 7.7499 |  | HFTD 2 | 0.016804 | 0.016789 | 1.5566e-05 | 0.013712 | 0.0071231 | 0.0014144 | 0.0051743 | N/A | 0.0038141 | 1.2244 | N/A | N/A | 1.0621 | 0.0040813 | N/A | 1.0621
CROWLEY | Circuit | Distribution | 12.0894 |  | HFTD 2 | 0.0021688 | 0.0021389 | 2.9936e-05 | 0.002844 | 0.002349 | 2.5725e-05 | 0.00046929 | N/A | 0.055103 | 0.75206 | N/A | N/A | 1.3299 | 0.00054328 | N/A | 1.3299
CRUMNER | Circuit | Distribution | 9.9077 |  | HFTD 3 | 0.027397 | 0.027368 | 2.8788e-05 | 0.01937 | 0.010702 | 0.001258 | 0.0074101 | N/A | 0.018533 | 1.4129 | N/A | N/A | 1.0389 | 0.0015534 | N/A | 1.0389
CRUMP | Circuit | Distribution | 3.8557 |  | HFTD 3 | 0.0098125 | 0.0097916 | 2.0891e-05 | 0.016822 | 0.0077847 | 0.0056795 | 0.003358 | N/A | 0.031226 | 0.58207 | N/A | N/A | 1.278 | 0.00066902 | N/A | 1.278
CRUZ | Circuit | Distribution | 1.7662 |  | HFTD 3 | 0.0044441 | 0.0044154 | 2.8749e-05 | 0.018884 | 0.010602 | 0.00020766 | 0.008074 | N/A | 0.00059623 | 0.23381 | N/A | N/A | 1.0409 | 0.048219 | N/A | 1.0409
CUDDEBACK | Circuit | Distribution | 16.9618 |  | HFTD 3 | 0.021984 | 0.021984 | 0 | 0.0033773 | 0.0028245 | 0.00012218 | 0.00043062 | N/A | 0.048796 | 6.5094 | N/A | N/A | 1.0444 | 0 | N/A | 1.0444
CUERVO | Circuit | Distribution | 0.34393 |  | HFTD 2 | 0.0025965 | 0.002402 | 0.0001945 | 0.0094859 | 0.0021183 | 0.00051723 | 0.0068504 | N/A | 0.011468 | 0.25322 | N/A | N/A | 1.0786 | 0.016959 | N/A | 1.0786
CUPPLES | Circuit | Distribution | 1.3763 |  | HFTD 2 | 1.7049e-06 | 7.9529e-07 | 9.0965e-07 | 8.8827e-05 | 7.576e-05 | 1.0273e-06 | 1.204e-05 | N/A | 0.0033313 | 0.0089533 | N/A | N/A | 1.1667 | 0.00027306 | N/A | 1.1667
CUSHENBURY | Circuit | Distribution | 6.4263 |  | HFTD 2 | 0.0013577 | 0.0013573 | 4.2814e-07 | 0.00141 | 0.00072008 | 2.407e-05 | 0.00066581 | N/A | 0.02274 | 0.96266 | N/A | N/A | 1 | 1.8828e-05 | N/A | 1
CUTHBERT | Circuit | Distribution | 18.6093 |  | HFTD 3 | 0.018886 | 0.018857 | 2.8953e-05 | 0.017748 | 0.012723 | 0.00044391 | 0.004581 | N/A | 0.037277 | 1.0625 | N/A | N/A | 1.0945 | 0.00077669 | N/A | 1.0945
CUYAMA | Circuit | Distribution | 33.0191 |  | HFTD 2 | 0.0013057 | 0.0013057 | 2.7986e-08 | 0.0038575 | 0.0022607 | 7.9131e-05 | 0.0015176 | N/A | 0.01154 | 0.33847 | N/A | N/A | 1.012 | 2.4251e-06 | N/A | 1.012
DALBA | Circuit | Distribution | 7.7025 |  | HFTD 3 | 0.0093375 | 0.0093015 | 3.5973e-05 | 0.011268 | 0.0078642 | 0.0015133 | 0.0018906 | N/A | 0.033846 | 0.82548 | N/A | N/A | 1.0873 | 0.0010629 | N/A | 1.0873
DARTMOUTH | Circuit | Distribution | 13.351 |  | HFTD 3 | 0.0051442 | 0.005118 | 2.6144e-05 | 0.0034996 | 0.0020572 | 0.00013638 | 0.001306 | N/A | 0.019688 | 1.4624 | N/A | N/A | 1.198 | 0.0013279 | N/A | 1.198
DAVENPORT | Circuit | Distribution | 60.0093 |  | HFTD 3 | 0.028392 | 0.028391 | 1.5464e-06 | 0.003628 | 0.0030515 | 0.00019235 | 0.0003842 | N/A | 0.032533 | 7.8254 | N/A | N/A | 1.1516 | 4.7534e-05 | N/A | 1.1516
DEACON | Circuit | Distribution | 3.6674 |  | HFTD 2 | 0.001246 | 0.0012291 | 1.6945e-05 | 0.0045102 | 0.0022732 | 9.4208e-05 | 0.0021428 | N/A | 0.0015071 | 0.27251 | N/A | N/A | 1.0977 | 0.011244 | N/A | 1.0977
DEALER | Circuit | Distribution | 37.6273 |  | HFTD 2 | 0.038577 | 0.038556 | 2.1379e-05 | 0.0069387 | 0.0041198 | 4.1536e-05 | 0.0027774 | N/A | 0.033302 | 5.5566 | N/A | N/A | 1.1764 | 0.00064196 | N/A | 1.1764
DEL CARBON | Circuit | Distribution | 8.8972 |  | HFTD 3 | 0.01637 | 0.016367 | 3.3189e-06 | 0.011633 | 0.0070514 | 0.0010872 | 0.0034942 | N/A | 0.0063027 | 1.407 | N/A | N/A | 1.2431 | 0.00052659 | N/A | 1.2431
DELUZ | Circuit | Distribution | 9.053 |  | HFTD 3 | 0.0021476 | 0.0021476 | 0 | 0.0023642 | 0.0016184 | 9.1397e-05 | 0.0006544 | N/A | 0.0036812 | 0.90839 | N/A | N/A | 1.0747 | 0 | N/A | 1.0747
DENTAL | Circuit | Distribution | 2.318 |  | HFTD 2 | 0.029424 | 0.029418 | 5.9877e-06 | 0.014488 | 0.0051916 | 0.0016024 | 0.0076938 | N/A | 0.0013465 | 2.0305 | N/A | N/A | 1.1899 | 0.0044468 | N/A | 1.1899
DEVILS GATE | Circuit | Distribution | 3.1675 |  | HFTD 2 | 0.0033057 | 0.0032596 | 4.6085e-05 | 0.012812 | 0.0041069 | 0.003424 | 0.0052814 | N/A | 0.006152 | 0.25441 | N/A | N/A | 1.0964 | 0.007491 | N/A | 1.0964
DEVINE | Circuit | Distribution | 6.238 |  | HFTD 3 | 0.001039 | 0.00098329 | 5.5663e-05 | 0.024069 | 0.010151 | 0.0012738 | 0.012644 | N/A | 0.0099906 | 0.040853 | N/A | N/A | 1.0507 | 0.0055716 | N/A | 1.0507
DICE | Circuit | Distribution | 4.4746 | Top 5% Highest Risk | HFTD Tier 2 | 0.044979 | 0.044979 | 3.2345e-07 | 0.011617 | 0.0073722 | 1.1254e-05 | 0.0042336 | N/A | 0.023979 | 3.8718 | N/A | N/A | 1.6667 | 1.3489e-05 | N/A | 1.6667
DILL | Circuit | Distribution | 0.48504 |  | HFTD 2 | 0.0022459 | 0.0021781 | 6.7823e-05 | 0.0077911 | 0.0037803 | 0.00012082 | 0.00389 | N/A | 0.0040776 | 0.27956 | N/A | N/A | 1.1418 | 0.016633 | N/A | 1.1418
DINELY | Circuit | Distribution | 2.7901 | Top 5% Highest Risk | HFTD Tier 3 | 0.058626 | 0.058626 | 1.1249e-08 | 0.0088835 | 0.0055073 | 0.0002992 | 0.003077 | N/A | 0.020257 | 6.5994 | N/A | N/A | 2 | 5.5529e-07 | N/A | 2
DINKEY CREEK | Circuit | Distribution | 6.1186 |  | HFTD 3 | 0.00036302 | 0.00036281 | 2.1158e-07 | 0.007466 | 0.0048156 | 0.0011607 | 0.0014896 | N/A | 0.0038562 | 0.048595 | N/A | N/A | 1.2614 | 5.4866e-05 | N/A | 1.2614
DOBLE | Circuit | Distribution | 14.8798 |  | HFTD 2 | 0.0002296 | 0.0002295 | 1.0017e-07 | 0.0010563 | 0.00081992 | 6.3252e-06 | 0.00023003 | N/A | 0.023424 | 0.21727 | N/A | N/A | 1 | 4.2765e-06 | N/A | 1
DOCTORS | Circuit | Distribution | 3.2685 |  | HFTD 3 | 0.029713 | 0.029685 | 2.8656e-05 | 0.010159 | 0.0055526 | 0.0022987 | 0.0023073 | N/A | 0.0040211 | 2.9221 | N/A | N/A | 1.1191 | 0.0071263 | N/A | 1.1191
DOLORES | Circuit | Distribution | 1.4256 | Top 5% Highest Risk | HFTD Tier 3 | 0.049344 | 0.049327 | 1.7188e-05 | 0.029254 | 0.021757 | 0.0034505 | 0.0040458 | N/A | 0.017979 | 1.6862 | N/A | N/A | 1.6831 | 0.00095599 | N/A | 1.6831
DOLPHIN | Circuit | Distribution | 0.96603 |  | HFTD 2 | 0.00044953 | 0.00044929 | 2.407e-07 | 0.0013956 | 0.00035745 | 0.00019549 | 0.00084264 | N/A | 0.0016129 | 0.32194 | N/A | N/A | 1.1875 | 0.00014923 | N/A | 1.1875
DOMIC | Circuit | Distribution | 6.5975 |  | HFTD 2 | 0.0057639 | 0.0057079 | 5.6004e-05 | 0.0051411 | 0.0015602 | 0.0012661 | 0.0023148 | N/A | 0.0024768 | 1.1102 | N/A | N/A | 1.1304 | 0.022611 | N/A | 1.1304
DONLON | Circuit | Distribution | 5.8385 |  | HFTD 2 | 0.0062648 | 0.0062455 | 1.9304e-05 | 0.0099105 | 0.0055295 | 0.0011614 | 0.0032196 | N/A | 0.0029393 | 0.63019 | N/A | N/A | 1.162 | 0.0065673 | N/A | 1.162
DONNER | Circuit | Distribution | 1.7777 |  | HFTD 3 | 0.0040905 | 0.0040755 | 1.494e-05 | 0.0070122 | 0.0046197 | 7.6184e-05 | 0.0023164 | N/A | 0.0012167 | 0.5812 | N/A | N/A | 1.055 | 0.012279 | N/A | 1.055
DOROF | Circuit | Distribution | 0.62025 |  | HFTD 2 | 0.0052711 | 0.0052484 | 2.2686e-05 | 0.0065283 | 0.0035639 | 0.00024179 | 0.0027226 | N/A | 0.00052361 | 0.80395 | N/A | N/A | 1.12 | 0.043326 | N/A | 1.12
DOWELL | Circuit | Distribution | 0.99615 |  | HFTD 2 | 0.0010332 | 0.0010332 | 0 | 0.034653 | 0.023438 | 0.0055618 | 0.0056524 | N/A | 0 | 0.029816 | N/A | N/A | 1.198 |  | N/A | 1.198
DREYER | Circuit | Distribution | 0.96772 |  | HFTD 2 | 0.011243 | 0.011112 | 0.00013029 | 0.013971 | 0.006157 | 0.00075924 | 0.0070545 | N/A | 0.0017144 | 0.79541 | N/A | N/A | 1.2317 | 0.075994 | N/A | 1.2317
DRILLER | Circuit | Distribution | 4.6942 |  | HFTD 3 | 0.0071996 | 0.0071996 | 0 | 0.024959 | 0.010494 | 0.00090776 | 0.013557 | N/A | 0 | 0.28846 | N/A | N/A | 1.0728 |  | N/A | 1.0728
DRINKWATER | Circuit | Distribution | 1.8487 |  | HFTD 3 | 0.0075992 | 0.007599 | 1.5404e-07 | 0.0036513 | 0.001027 | 0.00015662 | 0.0024676 | N/A | 0.012039 | 2.0812 | N/A | N/A | 1.6707 | 1.2796e-05 | N/A | 1.6707
DRISKILL | Circuit | Distribution | 15.2379 |  | HFTD 3 | 0.0053383 | 0.005326 | 1.2297e-05 | 0.0039895 | 0.0023486 | 0.00032573 | 0.0013152 | N/A | 0.0054428 | 1.335 | N/A | N/A | 1.1548 | 0.0022593 | N/A | 1.1548
DUFFER | Circuit | Distribution | 0.72071 |  | HFTD 3 | 0.004469 | 0.004354 | 0.00011504 | 0.0076895 | 0.0044706 | 0.0003884 | 0.0028305 | N/A | 0.00056415 | 0.56623 | N/A | N/A | 1.0808 | 0.20391 | N/A | 1.0808
DUKE | Circuit | Distribution | 2.59 |  | HFTD 2 | 0.018822 | 0.018706 | 0.00011591 | 0.0033874 | 0.0029156 | 0.00012732 | 0.00034452 | N/A | 0.0067519 | 5.5221 | N/A | N/A | 1.1244 | 0.017167 | N/A | 1.1244
DWP DRINKWATER | Circuit | Distribution | 0.49851 |  | HFTD 3 | 0.0042375 | 0.0042375 | 0 | 0.0011259 | 0.00017107 | 5.6878e-05 | 0.00089795 | N/A | 0.0035153 | 3.7636 | N/A | N/A |  | 0 | N/A
DYNAMO | Circuit | Distribution | 14.002 |  | HFTD 2 | 0.0016068 | 0.0016064 | 3.9602e-07 | 0.00074883 | 0.00055644 | 3.1701e-06 | 0.00018923 | N/A | 0.12708 | 2.1452 | N/A | N/A | 1.6316 | 3.1164e-06 | N/A | 1.6316
DYSART | Circuit | Distribution | 7.525 |  | HFTD 2 | 0.015518 | 0.015517 | 7.2927e-07 | 0.0029389 | 0.0024666 | 0.00015025 | 0.00032207 | N/A | 0.019493 | 5.2799 | N/A | N/A | 1.4113 | 3.7411e-05 | N/A | 1.4113
EAGLE CREST | Circuit | Distribution | 7.8063 |  | HFTD 3 | 0.021215 | 0.021215 | 1.3297e-07 | 0.0043009 | 0.0034611 | 3.9591e-05 | 0.00080016 | N/A | 0.0049708 | 4.9326 | N/A | N/A | 1.0317 | 2.6749e-05 | N/A | 1.0317
EASTER | Circuit | Distribution | 7.1072 |  | HFTD 2 | 0.012897 | 0.012879 | 1.7113e-05 | 0.0040518 | 0.0011017 | 5.6989e-05 | 0.0028931 | N/A | 0.0071747 | 3.1787 | N/A | N/A | 1.1375 | 0.0023852 | N/A | 1.1375
EBERT | Circuit | Distribution | 0.57414 |  | HFTD 2 | 0.001793 | 0.0017275 | 6.5486e-05 | 0.0017373 | 0.00026814 | 6.8485e-05 | 0.0014007 | N/A | 0.0066882 | 0.99435 | N/A | N/A | 1.1635 | 0.0097913 | N/A | 1.1635
ECHO | Circuit | Distribution | 1.2279 |  | HFTD 3 | 0.0069952 | 0.0064551 | 0.00054011 | 0.0088653 | 0.0078283 | 0.00019645 | 0.00084062 | N/A | 0.00048855 | 0.72812 | N/A | N/A | 1.1581 | 1.1055 | N/A | 1.1581
EGMONT | Circuit | Distribution | 0.32151 |  | HFTD 2 | 0.0063575 | 0.0063039 | 5.3696e-05 | 0.0063911 | 0.0015964 | 0.00044409 | 0.0043506 | N/A | 0.00071972 | 0.98635 | N/A | N/A | 1.2756 | 0.074607 | N/A | 1.2756
EL MIRADOR | Circuit | Distribution | 18.1976 |  | HFTD 2 | 0.0023654 | 0.0023654 | 0 | 0.0028807 | 0.001424 | 0.00028741 | 0.0011693 | N/A | 0 | 0.82112 | N/A | N/A | 1.0908 |  | N/A | 1.0908
ELAINE | Circuit | Distribution | 0.59939 |  | HFTD 3 | 0.0021966 | 0.0021966 | 0 | 0.0081652 | 0.0037466 | 0.00069382 | 0.0037247 | N/A | 0.0026753 | 0.26902 | N/A | N/A | 1.0077 | 0 | N/A | 1.0077
ELECTRA | Circuit | Distribution | 1.0263 |  | HFTD 3 | 0.0079553 | 0.0079407 | 1.4609e-05 | 0.0044768 | 0.0018365 | 4.7573e-05 | 0.0025927 | N/A | 0.005326 | 1.7738 | N/A | N/A | 1.0229 | 0.002743 | N/A | 1.0229
ELSTER | Circuit | Distribution | 47.8583 |  | HFTD 2 | 0.0044688 | 0.0044687 | 1.3015e-07 | 0.0051329 | 0.0027454 | 0.00054581 | 0.0018417 | N/A | 0.0012996 | 0.8706 | N/A | N/A | 1.164 | 0.00010015 | N/A | 1.164
ENCANTO | Circuit | Distribution | 3.917 |  | HFTD 3 | 0.0031006 | 0.0031006 | 0 | 0.010266 | 0.0050488 | 0.0029791 | 0.0022381 | N/A | 0.00051069 | 0.30203 | N/A | N/A | 1.075 | 0 | N/A | 1.075
ENCHANTED | Circuit | Distribution | 4.583 |  | HFTD 3 | 0.028303 | 0.028269 | 3.3953e-05 | 0.0075785 | 0.0043701 | 0.00025436 | 0.002954 | N/A | 0.039128 | 3.7301 | N/A | N/A | 1.1264 | 0.00086774 | N/A | 1.1264
ENERGY | Circuit | Distribution | 21.4058 |  | HFTD 3 | 0.031294 | 0.031262 | 3.2475e-05 | 0.005014 | 0.0041032 | 8.7853e-05 | 0.00082299 | N/A | 0.062087 | 6.2348 | N/A | N/A | 1.3349 | 0.00052305 | N/A | 1.3349
EQUINOX | Circuit | Distribution | 18.3744 |  | HFTD 2 | 0.0044061 | 0.0044057 | 4.4257e-07 | 0.0047348 | 0.0034131 | 0.00011042 | 0.0012113 | N/A | 0.0022125 | 0.93049 | N/A | N/A | 1.3674 | 0.00020003 | N/A | 1.3674
ERIN | Circuit | Distribution | 3.2172 |  | HFTD 2 | 0.0037733 | 0.0037246 | 4.8716e-05 | 0.011334 | 0.0024656 | 0.00046515 | 0.0084028 | N/A | 0.0027448 | 0.32863 | N/A | N/A | 1.0626 | 0.017748 | N/A | 1.0626
ERRINGER | Circuit | Distribution | 11.0675 |  | HFTD 3 | 0.00074187 | 0.00068642 | 5.5445e-05 | 0.021609 | 0.013856 | 0.0015979 | 0.0061554 | N/A | 0.011919 | 0.031766 | N/A | N/A | 1.0663 | 0.0046518 | N/A | 1.0663
ERSKINE | Circuit | Distribution | 51.3345 | Top 5% Highest Risk | HFTD Tier 3 | 0.051696 | 0.051677 | 1.8641e-05 | 0.0098267 | 0.0066995 | 9.4874e-05 | 0.0030323 | N/A | 0.051644 | 5.2589 | N/A | N/A | 1.1637 | 0.00036096 | N/A | 1.1637
ESCALA | Circuit | Distribution | 6.7709 |  | HFTD 3 | 0.0039944 | 0.0039939 | 5.0387e-07 | 0.0017807 | 0.00030448 | 0.00010168 | 0.0013745 | N/A | 0.0038035 | 2.2429 | N/A | N/A | 1.2331 | 0.00013247 | N/A | 1.2331
ESCAMILLA | Circuit | Distribution | 0.63029 |  | HFTD 2 | 0.0001613 | 0.0001613 | 0 | 0.01133 | 0.0036337 | 0.00083723 | 0.0068594 | N/A | 0 | 0.014236 | N/A | N/A | 1.0489 |  | N/A | 1.0489
ESTABAN | Circuit | Distribution | 11.507 |  | HFTD 2 | 0.0024641 | 0.0024496 | 1.4542e-05 | 0.0022477 | 0.0017339 | 0.0001408 | 0.00037306 | N/A | 0.0034147 | 1.0898 | N/A | N/A | 1.1213 | 0.0042588 | N/A | 1.1213
ETHANAC | Circuit | Distribution | 0.60296 |  | HFTD 2 | 0.00097268 | 0.00044082 | 0.00053187 | 0.0029533 | 0.0012403 | 0.00016616 | 0.0015468 | N/A | 0.0024487 | 0.14926 | N/A | N/A | 1.0767 | 0.2172 | N/A | 1.0767
EVERETT | Circuit | Distribution | 2.9854 |  | HFTD 3 | 0.01016 | 0.010078 | 8.219e-05 | 0.016519 | 0.0088095 | 0.00079525 | 0.0069142 | N/A | 0.0064656 | 0.61009 | N/A | N/A | 1.0549 | 0.012712 | N/A | 1.0549
EVITA | Circuit | Distribution | 3.5336 |  | HFTD 3 | 0.0026839 | 0.0026578 | 2.6077e-05 | 0.0052033 | 0.0027287 | 0.00018557 | 0.002289 | N/A | 0.0066882 | 0.5108 | N/A | N/A | 1.0582 | 0.0038989 | N/A | 1.0582
FAIRLANE | Circuit | Distribution | 1.1218 |  | HFTD 2 | 0.0038495 | 0.0018619 | 0.0019876 | 0.005154 | 0.00086959 | 0.0017912 | 0.0024933 | N/A | 0.021402 | 0.36124 | N/A | N/A | 1.241 | 0.092869 | N/A | 1.241
FANO | Circuit | Distribution | 1.9144 |  | HFTD 2 | 0.014829 | 0.014789 | 3.9866e-05 | 0.011366 | 0.0043034 | 0.00045166 | 0.0066111 | N/A | 0.0020168 | 1.3011 | N/A | N/A | 1.2243 | 0.019767 | N/A | 1.2243
FARMINGTON | Circuit | Distribution | 9.1987 |  | HFTD 2 | 0.019386 | 0.019386 | 0 | 0.0046966 | 0.0029769 | 0.00012302 | 0.0015967 | N/A | 0 | 4.1277 | N/A | N/A | 1.0826 |  | N/A | 1.0826
FAYE | Circuit | Distribution | 31.1691 |  | HFTD 3 | 0.036168 | 0.036148 | 1.9462e-05 | 0.0083235 | 0.0043651 | 0.00014164 | 0.0038167 | N/A | 0.12513 | 4.3429 | N/A | N/A | 1.242 | 0.00015554 | N/A | 1.242
FELDSPAR | Circuit | Distribution | 12.535 |  | HFTD 2 | 0.0072261 | 0.0072261 | 0 | 0.010569 | 0.0054791 | 0.0019291 | 0.0031605 | N/A | 0 | 0.68373 | N/A | N/A | 1.5004 |  | N/A | 1.5004
FERRARA | Circuit | Distribution | 12.5729 |  | HFTD 3 | 0.008208 | 0.0081346 | 7.3483e-05 | 0.0098868 | 0.0070067 | 0.00011515 | 0.0027649 | N/A | 0.06602 | 0.82277 | N/A | N/A | 1.2295 | 0.001113 | N/A | 1.2295
FIELDGATE | Circuit | Distribution | 1.6438 |  | HFTD 2 | 0.002679 | 0.002679 | 0 | 0.013563 | 0.0038157 | 0.0016124 | 0.0081347 | N/A | 0 | 0.19753 | N/A | N/A | 1.1825 |  | N/A | 1.1825
FINGAL | Circuit | Distribution | 30.6029 |  | HFTD 3 | 0.022413 | 0.022413 | 0 | 0.004435 | 0.0036162 | 7.6132e-05 | 0.00074267 | N/A | 0.060576 | 5.0537 | N/A | N/A | 1.3854 | 0 | N/A | 1.3854
FLAGSTAFF | Circuit | Distribution | 0.7327 |  | HFTD 2 | 0.0088148 | 0.0087666 | 4.8205e-05 | 0.0067401 | 0.0023307 | 0.00043097 | 0.0039784 | N/A | 0.0051148 | 1.3007 | N/A | N/A | 1.094 | 0.0094245 | N/A | 1.094
FLANDERS | Circuit | Distribution | 4.3489 |  | HFTD 2 | 0.040266 | 0.040266 | 6.3289e-07 | 0.028797 | 0.023354 | 0.0030809 | 0.0023626 | N/A | 0.01617 | 1.3982 | N/A | N/A | 1.6129 | 3.9141e-05 | N/A | 1.6129
FLEETWOOD | Circuit | Distribution | 2.5035 |  | HFTD 2 | 0.0051411 | 0.0050975 | 4.3615e-05 | 0.010079 | 0.0057362 | 0.00040593 | 0.0039365 | N/A | 0.0023258 | 0.50577 | N/A | N/A | 1.1233 | 0.018753 | N/A | 1.1233
FLINTRIDGE | Circuit | Distribution | 4.3659 |  | HFTD 2 | 0.009657 | 0.0096541 | 2.876e-06 | 0.023355 | 0.013459 | 0.0083713 | 0.0015256 | N/A | 0.013181 | 0.41335 | N/A | N/A | 1.3664 | 0.00021819 | N/A | 1.3664
FLOODGATE | Circuit | Distribution | 34.6575 |  | HFTD 2 | 0.028815 | 0.028777 | 3.7846e-05 | 0.0063693 | 0.0027192 | 0.00016854 | 0.0034816 | N/A | 0.0017845 | 4.5181 | N/A | N/A | 1.1908 | 0.021208 | N/A | 1.1908
FLYCATCHER | Circuit | Distribution | 38.3951 |  | HFTD 3 | 0.011061 | 0.011018 | 4.3576e-05 | 0.0026 | 0.0021867 | 1.2709e-05 | 0.00040059 | N/A | 0.10428 | 4.2377 | N/A | N/A | 1.1553 | 0.00041786 | N/A | 1.1553
FLYING D | Circuit | Distribution | 47.9256 |  | HFTD 2 | 0.0081105 | 0.00811 | 4.7987e-07 | 0.004933 | 0.0036443 | 6.0069e-05 | 0.0012286 | N/A | 0.011718 | 1.644 | N/A | N/A | 1.0804 | 4.0951e-05 | N/A | 1.0804
FLYNN | Circuit | Distribution | 2.9925 |  | HFTD 2 | 0.006225 | 0.0061994 | 2.5577e-05 | 0.00514 | 0.0024886 | 0.00085702 | 0.0017944 | N/A | 0.0018727 | 1.2061 | N/A | N/A | 1.0209 | 0.013658 | N/A | 1.0209
FOOTHILL | Circuit | Distribution | 1.0663 |  | HFTD 2 | 0.0024734 | 0.0024178 | 5.5613e-05 | 0.0075318 | 0.0016014 | 0.00065989 | 0.0052706 | N/A | 0.0012688 | 0.32101 | N/A | N/A | 1.0703 | 0.04383 | N/A | 1.0703
FRAN - 569 JA | Circuit | Distribution | 0.7382 |  | HFTD 2 | 0.00014864 | 0.00014864 | 0 | 0.0096636 | 0.00074646 | 0.00046298 | 0.0084542 | N/A | 0 | 0.015382 | N/A | N/A |  |  | N/A
FRISBIE | Circuit | Distribution | 2.5213 |  | HFTD 2 | 0.003565 | 0.003145 | 0.00041991 | 0.0048307 | 0.0024533 | 0.00017787 | 0.0021995 | N/A | 0.013381 | 0.65106 | N/A | N/A | 1.1754 | 0.031382 | N/A | 1.1754
FRONTIER | Circuit | Distribution | 0.55432 |  | HFTD 3 | 0.001373 | 0.001373 | 0 | 0.0055746 | 0.00090531 | 0.00026903 | 0.0044003 | N/A | 0 | 0.24629 | N/A | N/A | 1.0942 |  | N/A | 1.0942
FROZEN | Circuit | Distribution | 14.689 |  | HFTD 3 | 0.00030968 | 0.00030966 | 1.8008e-08 | 0.00021566 | 5.8017e-05 | 1.0377e-05 | 0.00014727 | N/A | 0.054253 | 1.4358 | N/A | N/A |  | 3.3193e-07 | N/A
FULLBACK | Circuit | Distribution | 0.61657 |  | HFTD 2 | 0.0025852 | 0.0025852 | 0 | 0.0014432 | 0.00018254 | 6.9058e-05 | 0.0011916 | N/A | 0 | 1.7913 | N/A | N/A | 1.0626 |  | N/A | 1.0626
GABBERT | Circuit | Distribution | 6.9794 |  | HFTD 3 | 0.006253 | 0.0061785 | 7.4497e-05 | 0.0075213 | 0.0051568 | 0.00031032 | 0.0020542 | N/A | 0.028026 | 0.82147 | N/A | N/A | 1.0906 | 0.0026581 | N/A | 1.0906
GALAHAD | Circuit | Distribution | 47.3374 |  | HFTD 3 | 0.0085923 | 0.0085844 | 7.9372e-06 | 0.0059511 | 0.0047824 | 0.00017501 | 0.0009937 | N/A | 0.044006 | 1.4425 | N/A | N/A | 1.1783 | 0.00018037 | N/A | 1.1783
GALENA | Circuit | Distribution | 2.1756 |  | HFTD 2 | 0.0038567 | 0.0035366 | 0.00032013 | 0.0036281 | 0.0014018 | 0.00020337 | 0.002023 | N/A | 0.0014533 | 0.97475 | N/A | N/A | 1.217 | 0.22028 | N/A | 1.217
GAMBLER | Circuit | Distribution | 53.7254 | Top 5% Highest Risk | HFTD Tier 2 | 0.046403 | 0.046396 | 7.3834e-06 | 0.0077376 | 0.0047547 | 1.5612e-05 | 0.0029673 | N/A | 0.0534 | 5.9961 | N/A | N/A | 1.3731 | 0.00013827 | N/A | 1.3731
GARBONI | Circuit | Distribution | 5.3991 |  | HFTD 2 | 0.018344 | 0.018344 | 0 | 0.010045 | 0.0053621 | 0.0001184 | 0.0045649 | N/A | 0.001262 | 1.8261 | N/A | N/A | 1.1175 | 0 | N/A | 1.1175
GARDEN | Circuit | Distribution | 2.1933 |  | HFTD 2 | 0.0067891 | 0.0067816 | 7.5164e-06 | 0.011591 | 0.0077015 | 0.0008886 | 0.0030007 | N/A | 0 | 0.58509 | N/A | N/A | 1.0532 | inf | N/A | 1.0532
GARY - 568 JA | Circuit | Distribution | 0.46361 |  | HFTD 2 | 5.1187e-05 | 5.1187e-05 | 0 | 0.0048911 | 0.00041125 | 0.00029068 | 0.0041892 | N/A | 0 | 0.010465 | N/A | N/A |  |  | N/A
GILLIBRAND | Circuit | Distribution | 9.5793 |  | HFTD 3 | 0.00032945 | 0.0002004 | 0.00012905 | 0.014923 | 0.0074625 | 0.00015421 | 0.0073062 | N/A | 0.037038 | 0.013429 | N/A | N/A | 1.1687 | 0.0034841 | N/A | 1.1687
GILMAN | Circuit | Distribution | 4.829 |  | HFTD 3 | 0.0060088 | 0.0060087 | 8.2233e-08 | 0.0051521 | 0.0025318 | 4.0223e-05 | 0.0025801 | N/A | 0.018429 | 1.1663 | N/A | N/A | 1.5333 | 4.4621e-06 | N/A | 1.5333
GINGER | Circuit | Distribution | 14.8165 |  | HFTD 3 | 0.0046968 | 0.0046953 | 1.5239e-06 | 0.0041358 | 0.0021328 | 0.00021686 | 0.0017861 | N/A | 0.01675 | 1.1353 | N/A | N/A | 1.367 | 9.0975e-05 | N/A | 1.367
GLASSCOCK | Circuit | Distribution | 13.3238 |  | HFTD 3 | 0.00042524 | 0.00036016 | 6.5076e-05 | 0.023678 | 0.014536 | 0.0012612 | 0.0078806 | N/A | 0.015783 | 0.015211 | N/A | N/A | 1.1649 | 0.0041231 | N/A | 1.1649
GLOBE MILLS | Circuit | Distribution | 0.84032 |  | HFTD 2 | 0.0084516 | 0.0082032 | 0.00024842 | 0.007041 | 0.0034898 | 0.00039308 | 0.0031582 | N/A | 0.0012472 | 1.165 | N/A | N/A | 1.157 | 0.19918 | N/A | 1.157
GNATCATCHER | Circuit | Distribution | 45.8363 |  | HFTD 3 | 0.0041523 | 0.0041508 | 1.4604e-06 | 0.00063564 | 0.00058756 | 1.0227e-05 | 3.7853e-05 | N/A | 0.025545 | 6.5301 | N/A | N/A | 1.52 | 5.7172e-05 | N/A | 1.52
GOLDSMITH | Circuit | Distribution | 8.7082 |  | HFTD 3 | 0.0027929 | 0.0026798 | 0.00011308 | 0.022885 | 0.011378 | 0.0023871 | 0.0091201 | N/A | 0.021761 | 0.1171 | N/A | N/A | 1.1244 | 0.0051963 | N/A | 1.1244
GORGE | Circuit | Distribution | 8.944 |  | HFTD 3 | 0.04101 | 0.040991 | 1.8386e-05 | 0.023882 | 0.014935 | 0.0011634 | 0.0077829 | N/A | 0.02246 | 1.7164 | N/A | N/A | 1.2365 | 0.00081863 | N/A | 1.2365
GOWAN | Circuit | Distribution | 1.3894 |  | HFTD 2 | 0.019744 | 0.019385 | 0.00035855 | 0.006672 | 0.001419 | 0.0002496 | 0.0050034 | N/A | 0.0023296 | 2.9055 | N/A | N/A | 1.1086 | 0.15391 | N/A | 1.1086
GRAHAM | Circuit | Distribution | 1.6613 |  | HFTD 3 | 0.0051131 | 0.0051131 | 0 | 0.001851 | 0.0015268 | 0.00011132 | 0.00021288 | N/A | 0.0052649 | 2.7623 | N/A | N/A | 1.1706 | 0 | N/A | 1.1706
GRANDAD | Circuit | Distribution | 11.3615 |  | HFTD 3 | 0.00072975 | 0.00072975 | 5.9686e-09 | 0.0046177 | 0.0032921 | 0.00011092 | 0.0012147 | N/A | 0 | 0.15803 | N/A | N/A | 1.452 | inf | N/A | 1.452
GRANNY SMITH | Circuit | Distribution | 25.571 |  | HFTD 3 | 0.018516 | 0.018516 | 1.7204e-07 | 0.0048638 | 0.0022113 | 0.00030128 | 0.0023512 | N/A | 0.013949 | 3.8068 | N/A | N/A | 1.1391 | 1.2333e-05 | N/A | 1.1391
GRAPEFRUIT | Circuit | Distribution | 0.7543 |  | HFTD 2 | 0.0097793 | 0.0097454 | 3.3906e-05 | 0.016989 | 0.0088129 | 0.00088317 | 0.007293 | N/A | 0.0010559 | 0.57363 | N/A | N/A | 1.0389 | 0.03211 | N/A | 1.0389
GREAT SALT | Circuit | Distribution | 5.3464 |  | HFTD 2 | 0.010195 | 0.010189 | 6.8491e-06 | 0.0024915 | 0.0010717 | 4.4048e-05 | 0.0013757 | N/A | 0.0039614 | 4.0894 | N/A | N/A | 1.2031 | 0.0017289 | N/A | 1.2031
GREEN BEAR | Circuit | Distribution | 7.3949 |  | HFTD 3 | 0.00326 | 0.0032299 | 3.0122e-05 | 0.0096541 | 0.0068181 | 0.0017275 | 0.0011086 | N/A | 0.029229 | 0.33456 | N/A | N/A | 1.3621 | 0.0010305 | N/A | 1.3621
GREENWELL | Circuit | Distribution | 0.79943 |  | HFTD 2 | 7.2072e-05 | 7.1711e-05 | 3.6069e-07 | 0.0018212 | 0.0015126 | 0.00020714 | 0.00010146 | N/A | 0.004472 | 0.039377 | N/A | N/A | 1.4211 | 8.0655e-05 | N/A | 1.4211
GRENADE | Circuit | Distribution | 2.0404 |  | HFTD 2 | 0.0019359 | 0.001818 | 0.00011785 | 0.021311 | 0.012724 | 0.0047263 | 0.0038603 | N/A | 0.0032665 | 0.08531 | N/A | N/A | 1.0414 | 0.036076 | N/A | 1.0414
GRIDLOCK | Circuit | Distribution | 0.70772 |  | HFTD 2 | 0.000232 | 0.00022329 | 8.711e-06 | 0.0081697 | 0.0053941 | 0.00041815 | 0.0023574 | N/A | 0.0002575 | 0.027331 | N/A | N/A | 1.0757 | 0.033829 | N/A | 1.0757
GROUSE | Circuit | Distribution | 3.5216 |  | HFTD 3 | 8.9048e-05 | 8.8991e-05 | 5.7071e-08 | 0.0010934 | 0.00050861 | 0.00010239 | 0.00048239 | N/A | 0.010378 | 0.08139 | N/A | N/A | 1 | 5.4992e-06 | N/A | 1
GRUWELL | Circuit | Distribution | 5.8887 |  | HFTD 2 | 0.023166 | 0.02316 | 5.9167e-06 | 0.0073691 | 0.0030304 | 0.001703 | 0.0026357 | N/A | 0.0045673 | 3.1429 | N/A | N/A | 1.1143 | 0.0012955 | N/A | 1.1143
GUARD | Circuit | Distribution | 1.6087 |  | HFTD 2 | 0.013829 | 0.013827 | 1.3797e-06 | 0.0093847 | 0.0043584 | 9.3394e-05 | 0.0049329 | N/A | 0.00082565 | 1.4734 | N/A | N/A | 1.0677 | 0.0016711 | N/A | 1.0677
GUFFY | Circuit | Distribution | 4.1932 |  | HFTD 3 | 0.039085 | 0.03908 | 4.2951e-06 | 0.011737 | 0.00728 | 0.00040827 | 0.0040489 | N/A | 0.0032353 | 3.3296 | N/A | N/A | 1.0972 | 0.0013276 | N/A | 1.0972
GUINNESS | Circuit | Distribution | 0.36391 |  | HFTD 2 | 0.0010043 | 0.00077162 | 0.00023271 | 0.0013962 | 0.00034252 | 0.00044704 | 0.00060662 | N/A | 0.0016759 | 0.55266 | N/A | N/A | 1.1312 | 0.13886 | N/A | 1.1312
GUITAR | Circuit | Distribution | 26.6471 |  | HFTD 3 | 0.0040657 | 0.0040657 | 0 | 0.0044069 | 0.0028788 | 0.00010212 | 0.001426 | N/A | 0.035243 | 0.92257 | N/A | N/A | 1.1957 | 0 | N/A | 1.1957
GULL LAKE | Circuit | Distribution | 4.9311 |  | HFTD 2 | 0.0081069 | 0.0080442 | 6.2725e-05 | 0.0066806 | 0.0025719 | 0.0025261 | 0.0015826 | N/A | 0.019258 | 1.2041 | N/A | N/A | 1.2301 | 0.0032571 | N/A | 1.2301
GUNSITE | Circuit | Distribution | 2.483 |  | HFTD 3 | 6.0347e-05 | 6.0347e-05 | 0 | 0.0018987 | 0.00065091 | 8.0808e-05 | 0.0011669 | N/A | 0.0013376 | 0.031784 | N/A | N/A | 1.75 | 0 | N/A | 1.75
GUSHER | Circuit | Distribution | 1.797 |  | HFTD 2 | 0.0081068 | 0.0081068 | 0 | 0.0067976 | 0.0017634 | 0.00032172 | 0.0047124 | N/A | 0 | 1.1926 | N/A | N/A | 1.049 |  | N/A | 1.049
GUST | Circuit | Distribution | 20.0078 |  | HFTD 3 | 0.014988 | 0.014982 | 6.1307e-06 | 0.0042738 | 0.0032583 | 0.00015583 | 0.0008596 | N/A | 0.073101 | 3.5055 | N/A | N/A | 1.2359 | 8.3865e-05 | N/A | 1.2359
GUTIERREZ | Circuit | Distribution | 3.8674 |  | HFTD 2 | 0.0091237 | 0.0091047 | 1.8982e-05 | 0.0098797 | 0.0058467 | 0.0011369 | 0.0028962 | N/A | 0.011521 | 0.92155 | N/A | N/A | 1.1067 | 0.0016477 | N/A | 1.1067
HACIENDA | Circuit | Distribution | 0.29134 |  | HFTD 3 | 0.0041671 | 0.003481 | 0.00068608 | 0.021097 | 0.0089588 | 0.0010886 | 0.01105 | N/A | 0.0026342 | 0.165 | N/A | N/A | 1.0816 | 0.26045 | N/A | 1.0816
HACKBERRY | Circuit | Distribution | 5.0829 |  | HFTD 3 | 0.027065 | 0.027065 | 0 | 0.015122 | 0.0063413 | 0.0012354 | 0.0075458 | N/A | 0 | 1.7898 | N/A | N/A | 1.1717 |  | N/A | 1.1717
HACKLER | Circuit | Distribution | 2.5318 |  | HFTD 2 | 0.0026868 | 0.0026464 | 4.0328e-05 | 0.013226 | 0.0057426 | 0.00023634 | 0.007247 | N/A | 0.0077642 | 0.20009 | N/A | N/A | 1.0793 | 0.0051941 | N/A | 1.0793
HAMMERHEAD | Circuit | Distribution | 0.52091 |  | HFTD 2 | 0.0058889 | 0.0058195 | 6.9419e-05 | 0.0022024 | 0.0003068 | 0.00012435 | 0.0017713 | N/A | 0.0072821 | 2.6423 | N/A | N/A | 1.0454 | 0.0095328 | N/A | 1.0454
HAMMOCK | Circuit | Distribution | 6.2512 |  | HFTD 2 | 0.02046 | 0.02046 | 9.1618e-08 | 0.0036779 | 0.00094151 | 0.00025306 | 0.0024833 | N/A | 0.0035581 | 5.5629 | N/A | N/A | 1.2 | 2.5749e-05 | N/A | 1.2
HAMPSHIRE | Circuit | Distribution | 19.7914 |  | HFTD 3 | 0.0026845 | 0.0026742 | 1.0326e-05 | 0.016116 | 0.0061556 | 0.0011241 | 0.0088367 | N/A | 0.01066 | 0.16593 | N/A | N/A | 1.1075 | 0.00096866 | N/A | 1.1075
HANDY | Circuit | Distribution | 0.96507 |  | HFTD 2 | 0.0002234 | 8.4032e-05 | 0.00013936 | 0.0090986 | 0.0024724 | 0.0016047 | 0.0050216 | N/A | 0.0030596 | 0.0092357 | N/A | N/A | 1.2643 | 0.04555 | N/A | 1.2643
HARNAGE | Circuit | Distribution | 3.9269 |  | HFTD 2 | 0.013018 | 0.013005 | 1.2788e-05 | 0.010125 | 0.00511 | 0.00043473 | 0.0045807 | N/A | 0.0015631 | 1.2844 | N/A | N/A | 1.0759 | 0.0081809 | N/A | 1.0759
HASKELL | Circuit | Distribution | 11.8301 |  | HFTD 2 | 0.0072391 | 0.0072351 | 4.065e-06 | 0.01754 | 0.0091969 | 0.00204 | 0.0063027 | N/A | 0.014167 | 0.4125 | N/A | N/A | 1.189 | 0.00028694 | N/A | 1.189
HASS | Circuit | Distribution | 19.4998 |  | HFTD 3 | 0.011594 | 0.011584 | 1.0175e-05 | 0.0082295 | 0.0039423 | 0.00081771 | 0.0034695 | N/A | 0.014884 | 1.4076 | N/A | N/A | 1.2636 | 0.00068361 | N/A | 1.2636
HAVEN | Circuit | Distribution | 0.3924 |  | HFTD 2 | 8.9348e-05 | 5.7956e-05 | 3.1392e-05 | 0.0047778 | 0.0019642 | 0.00072865 | 0.0020849 | N/A | 0.00083657 | 0.01213 | N/A | N/A | 1.0696 | 0.037525 | N/A | 1.0696
HEAPS PEAK | Circuit | Distribution | 3.7816 |  | HFTD 3 | 0.013229 | 0.013228 | 1.1651e-06 | 0.018644 | 0.012025 | 0.0019999 | 0.0046198 | N/A | 0.035477 | 0.70947 | N/A | N/A | 1.5439 | 3.2841e-05 | N/A | 1.5439
HELENA | Circuit | Distribution | 2.8336 |  | HFTD 2 | 0.008357 | 0.0083362 | 2.0813e-05 | 0.010223 | 0.0071456 | 0.0024287 | 0.00064853 | N/A | 0.00308 | 0.81545 | N/A | N/A | 1.098 | 0.0067574 | N/A | 1.098
HELENKA | Circuit | Distribution | 21.0169 |  | HFTD 2 | 0.038384 | 0.038382 | 1.7249e-06 | 0.008584 | 0.0059557 | 0.00021988 | 0.0024084 | N/A | 0.005703 | 4.4713 | N/A | N/A | 1.2405 | 0.00030246 | N/A | 1.2405
HELICOPTER | Circuit | Distribution | 4.8125 |  | HFTD 2 | 0.0048178 | 0.0048038 | 1.4004e-05 | 0.0088859 | 0.0025109 | 8.5813e-05 | 0.0062891 | N/A | 0.0017493 | 0.54061 | N/A | N/A | 1.1098 | 0.0080055 | N/A | 1.1098
HEMACINTO | Circuit | Distribution | 0.4428 |  | HFTD 2 | 0.0065751 | 0.0063596 | 0.00021549 | 0.011949 | 0.0042702 | 0.0011162 | 0.0065623 | N/A | 0.0006856 | 0.53224 | N/A | N/A | 1.1299 | 0.31431 | N/A | 1.1299
HENDERSON | Circuit | Distribution | 5.0567 |  | HFTD 2 | 0.00076469 | 0.00075465 | 1.0046e-05 | 0.0026316 | 0.0011217 | 8.9393e-05 | 0.0014205 | N/A | 0.0042815 | 0.28676 | N/A | N/A | 1.1009 | 0.0023463 | N/A | 1.1009
HERZ | Circuit | Distribution | 1.5364 |  | HFTD 2 | 0.0029118 | 0.0021929 | 0.00071892 | 0.0075866 | 0.0019751 | 0.001059 | 0.0045526 | N/A | 0.001607 | 0.28904 | N/A | N/A | 1.1571 | 0.44737 | N/A | 1.1571
HESSION | Circuit | Distribution | 3.573 |  | HFTD 2 | 0.00022276 | 0.00010368 | 0.00011908 | 8.0887e-05 | 4.9488e-05 | 9.4977e-06 | 2.1901e-05 | N/A | 0.031955 | 1.2818 | N/A | N/A | 1.2664 | 0.0037265 | N/A | 1.2664
HI LINE | Circuit | Distribution | 20.0973 |  | HFTD 3 | 0.0037965 | 0.0037965 | 0 | 0.0025269 | 0.00055608 | 3.7537e-05 | 0.0019333 | N/A | 0 | 1.5024 | N/A | N/A | 1.2888 |  | N/A | 1.2888
HIGH SCHOOL | Circuit | Distribution | 5.7336 |  | HFTD 3 | 0.011261 | 0.011253 | 7.7212e-06 | 0.010363 | 0.0062922 | 0.0014769 | 0.0025942 | N/A | 0.056481 | 1.0859 | N/A | N/A | 1.3251 | 0.0001367 | N/A | 1.3251
HIGHBALL | Circuit | Distribution | 2.722 |  | HFTD 2 | 0.0062741 | 0.0060826 | 0.00019151 | 0.014125 | 0.0089112 | 0.00049344 | 0.0047202 | N/A | 0.0010993 | 0.43063 | N/A | N/A | 1.1242 | 0.1742 | N/A | 1.1242
HILLARD | Circuit | Distribution | 3.8341 |  | HFTD 2 | 0.021301 | 0.0213 | 9.606e-07 | 0.019202 | 0.0076925 | 0.0095116 | 0.0019979 | N/A | 0.017328 | 1.1092 | N/A | N/A | 1.235 | 5.5437e-05 | N/A | 1.235
HILLCREST | Circuit | Distribution | 15.5527 |  | HFTD 3 | 0.0021615 | 0.002151 | 1.046e-05 | 0.019879 | 0.0079464 | 0.0023679 | 0.0095648 | N/A | 0.015689 | 0.1082 | N/A | N/A | 1.1739 | 0.00066675 | N/A | 1.1739
HILLFIELD | Circuit | Distribution | 7.0766 |  | HFTD 3 | 0.0016501 | 0.0015929 | 5.7272e-05 | 0.015818 | 0.010478 | 0.00051013 | 0.0048293 | N/A | 0.010597 | 0.1007 | N/A | N/A | 1.1118 | 0.0054044 | N/A | 1.1118
HILTON | Circuit | Distribution | 0.52254 |  | HFTD 2 | 0.0019218 | 0.0018708 | 5.0919e-05 | 0.018563 | 0.010335 | 0.0030898 | 0.0051379 | N/A | 0.0020237 | 0.10078 | N/A | N/A | 1.2557 | 0.025161 | N/A | 1.2557
HONEYCRISP | Circuit | Distribution | 0.80656 |  | HFTD 2 | 0.0046461 | 0.0044274 | 0.00021877 | 0.0023644 | 0.0017874 | 0.00017082 | 0.00040611 | N/A | 0.0094438 | 1.8725 | N/A | N/A | 1.138 | 0.023166 | N/A | 1.138
HONEYWELL | Circuit | Distribution | 2.002 |  | HFTD 2 | 0.00079697 | 0.0007741 | 2.2867e-05 | 0.011682 | 0.008884 | 0.00096351 | 0.0018341 | N/A | 0.0028476 | 0.066267 | N/A | N/A | 1.0802 | 0.0080305 | N/A | 1.0802
HOOK CREEK | Circuit | Distribution | 2.9535 |  | HFTD 3 | 0.0079988 | 0.0079988 | 0 | 0.013386 | 0.0091594 | 0.0026122 | 0.0016142 | N/A | 0 | 0.59756 | N/A | N/A | 1.1535 |  | N/A | 1.1535
HOOLIGAN | Circuit | Distribution | 6.5694 |  | HFTD 3 | 0.0054692 | 0.0054116 | 5.7647e-05 | 0.017629 | 0.0086465 | 0.0010808 | 0.0079021 | N/A | 0.010589 | 0.30697 | N/A | N/A | 1.1543 | 0.0054439 | N/A | 1.1543
HOPE | Circuit | Distribution | 0.26121 |  | HFTD 2 | 0.00095896 | 8.2739e-06 | 0.00095069 | 0.0010111 | 0.00039318 | 7.7204e-05 | 0.00054076 | N/A | 0.020047 | 0.0081827 | N/A | N/A | 1.0978 | 0.047423 | N/A | 1.0978
HORIZON | Circuit | Distribution | 13.6743 |  | HFTD 2 | 0.016024 | 0.01601 | 1.3886e-05 | 0.012278 | 0.0060165 | 0.0036464 | 0.0026149 | N/A | 0.015135 | 1.304 | N/A | N/A | 1.0484 | 0.00091745 | N/A | 1.0484
HORNTOAD | Circuit | Distribution | 20.6568 |  | HFTD 3 | 0.026846 | 0.026833 | 1.3089e-05 | 0.010708 | 0.0050961 | 0.00070421 | 0.0049072 | N/A | 0.018409 | 2.506 | N/A | N/A | 1.3975 | 0.00071101 | N/A | 1.3975
HORTON | Circuit | Distribution | 0.95554 |  | HFTD 2 | 0.0020698 | 0.0020089 | 6.0936e-05 | 0.005187 | 0.0010895 | 0.00013067 | 0.0039669 | N/A | 0.0020509 | 0.38729 | N/A | N/A | 1.0592 | 0.029711 | N/A | 1.0592
HOSPAT | Circuit | Distribution | 0.66658 |  | HFTD 3 | 0.0022194 | 0.0018145 | 0.0004049 | 0.019245 | 0.015522 | 0.00077513 | 0.0029479 | N/A | 0.002384 | 0.094282 | N/A | N/A | 1.1839 | 0.16984 | N/A | 1.1839
HOSPITAL | Circuit | Distribution | 2.5311 |  | HFTD 3 | 0.002109 | 0.002098 | 1.0997e-05 | 0.01604 | 0.011313 | 0.0013643 | 0.003362 | N/A | 0.0067825 | 0.1308 | N/A | N/A | 1.0221 | 0.0016213 | N/A | 1.0221
HOSS | Circuit | Distribution | 2.7132 |  | HFTD 3 | 0.01161 | 0.011296 | 0.00031413 | 0.013512 | 0.0066439 | 0.00048952 | 0.006379 | N/A | 0.013012 | 0.83599 | N/A | N/A | 1.1235 | 0.024141 | N/A | 1.1235
HOT SPRINGS | Circuit | Distribution | 5.6132 |  | HFTD 2 | 0.016305 | 0.016219 | 8.6546e-05 | 0.014788 | 0.0086017 | 0.0031371 | 0.0030491 | N/A | 0.0055883 | 1.0968 | N/A | N/A | 1.0597 | 0.015487 | N/A | 1.0597
HOVATTER | Circuit | Distribution | 3.3318 |  | HFTD 2 | 0.001305 | 0.0010341 | 0.00027094 | 0.022859 | 0.0067887 | 0.00069088 | 0.015379 | N/A | 0.0086332 | 0.045236 | N/A | N/A | 1.1978 | 0.031384 | N/A | 1.1978
HUBBLE | Circuit | Distribution | 0.71419 |  | HFTD 2 | 0.012053 | 0.00052097 | 0.011532 | 0.0054699 | 0.004537 | 1.8096e-05 | 0.00091472 | N/A | 0.0019165 | 0.095244 | N/A | N/A | 1.102 | 6.0174 | N/A | 1.102
HUCKLEBERRY | Circuit | Distribution | 20.7143 |  | HFTD 3 | 0.015513 | 0.015507 | 6.3147e-06 | 0.0028276 | 0.0014375 | 2.2299e-05 | 0.0013678 | N/A | 0.07407 | 5.4842 | N/A | N/A | 1.1691 | 8.5253e-05 | N/A | 1.1691
HUGHES LAKE | Circuit | Distribution | 78.448 |  | HFTD 3 | 0.012306 | 0.01229 | 1.5738e-05 | 0.0020439 | 0.0015987 | 9.3025e-05 | 0.00035219 | N/A | 0.083669 | 6.013 | N/A | N/A | 1.2038 | 0.0001881 | N/A | 1.2038
HUGO | Circuit | Distribution | 0.90886 |  | HFTD 3 | 0.0044894 | 0.0044892 | 1.7753e-07 | 0.0028888 | 0.0019971 | 8.3813e-05 | 0.00080792 | N/A | 0 | 1.554 | N/A | N/A | 1.4031 | inf | N/A | 1.4031
HURLEY | Circuit | Distribution | 6.5422 |  | HFTD 2 | 0.00087569 | 0.00078556 | 9.0127e-05 | 0.0044268 | 0.0020519 | 0.00025525 | 0.0021196 | N/A | 0.019576 | 0.17746 | N/A | N/A | 1.0541 | 0.004604 | N/A | 1.0541
HURST | Circuit | Distribution | 19.7288 |  | HFTD 3 | 0.036289 | 0.036266 | 2.3055e-05 | 0.013836 | 0.0078548 | 0.0017999 | 0.0041815 | N/A | 0.027838 | 2.6211 | N/A | N/A | 1.0986 | 0.00082819 | N/A | 1.0986
ICE HOUSE | Circuit | Distribution | 1.205 |  | HFTD 3 | 0.0054605 | 0.0054597 | 7.85e-07 | 0.015954 | 0.014951 | 0.00014103 | 0.00086262 | N/A | 0.02274 | 0.34221 | N/A | N/A | 1.0276 | 3.4521e-05 | N/A | 1.0276
IDA | Circuit | Distribution | 9.7561 | Top 5% Highest Risk | HFTD Tier 2 | 0.05393 | 0.05389 | 4.0024e-05 | 0.0048475 | 0.0025615 | 0.00058815 | 0.0016979 | N/A | 0.011396 | 11.1169 | N/A | N/A | 1.1149 | 0.0035122 | N/A | 1.1149
IMPALA | Circuit | Distribution | 16.1784 |  | HFTD 3 | 0.0016965 | 0.0016666 | 2.9935e-05 | 0.0013922 | 0.00067751 | 0.00026338 | 0.00045136 | N/A | 0.066996 | 1.197 | N/A | N/A | 1.2939 | 0.00044681 | N/A | 1.2939
INDEPENDENCE | Circuit | Distribution | 1.2652 |  | HFTD 2 | 0.0055996 | 0.0055331 | 6.6487e-05 | 0.0039097 | 0.00092111 | 0.00042184 | 0.0025667 | N/A | 0.0081211 | 1.4152 | N/A | N/A | 1.0337 | 0.008187 | N/A | 1.0337
INTAKE | Circuit | Distribution | 24.898 |  | HFTD 2 | 0.0052307 | 0.0052307 | 0 | 0.0021275 | 0.0015264 | 0.00023974 | 0.00036136 | N/A | 0 | 2.4586 | N/A | N/A | 1.0935 |  | N/A | 1.0935
INTERIOR | Circuit | Distribution | 26.9073 |  | HFTD 3 | 0.0042932 | 0.0042932 | 0 | 0.0023865 | 0.00071425 | 4.1319e-05 | 0.0016309 | N/A | 0 | 1.799 | N/A | N/A | 1.1624 |  | N/A | 1.1624
INTERN | Circuit | Distribution | 0.76898 |  | HFTD 3 | 0.0088673 | 0.0088169 | 5.0456e-05 | 0.0079052 | 0.0028294 | 0.00046242 | 0.0046134 | N/A | 0.0016854 | 1.1153 | N/A | N/A | 1.0722 | 0.029937 | N/A | 1.0722
INTERPACE | Circuit | Distribution | 10.4563 |  | HFTD 3 | 0.0023195 | 0.0023194 | 1.3711e-07 | 0.0042504 | 0.002063 | 4.7841e-05 | 0.0021396 | N/A | 0.0093061 | 0.54569 | N/A | N/A | 1.1667 | 1.4733e-05 | N/A | 1.1667
INTREPID | Circuit | Distribution | 6.1899 |  | HFTD 3 | 0.00024052 | 0.0001746 | 6.592e-05 | 0.0062937 | 0.0025311 | 0.00038037 | 0.0033823 | N/A | 0.014669 | 0.027742 | N/A | N/A | 1.069 | 0.0044938 | N/A | 1.069
INVADER | Circuit | Distribution | 7.8105 |  | HFTD 2 | 0.0039404 | 0.0034853 | 0.00045507 | 0.0080612 | 0.006216 | 4.8214e-05 | 0.001797 | N/A | 0.062614 | 0.43235 | N/A | N/A | 1.2936 | 0.0072678 | N/A | 1.2936
INYO LUMBER | Circuit | Distribution | 2.9856 |  | HFTD 2 | 0.024754 | 0.023675 | 0.0010791 | 0.0069912 | 0.0054211 | 0.00047523 | 0.001095 | N/A | 0.021448 | 3.3864 | N/A | N/A | 1.1469 | 0.05031 | N/A | 1.1469
IRAN | Circuit | Distribution | 0.63822 |  | HFTD 2 | 0.00057021 | 0.00031363 | 0.00025658 | 0.0044291 | 0.0016161 | 0.00036346 | 0.0024495 | N/A | 0.0015938 | 0.070812 | N/A | N/A | 1.2091 | 0.16099 | N/A | 1.2091
JADE | Circuit | Distribution | 0.69397 |  | HFTD 3 | 0.0088771 | 0.0087466 | 0.00013056 | 0.010957 | 0.0056071 | 0.00045249 | 0.0048975 | N/A | 0.005689 | 0.79826 | N/A | N/A | 1.134 | 0.022949 | N/A | 1.134
JAKE | Circuit | Distribution | 5.031 |  | HFTD 2 | 0.041298 | 0.041298 | 2.9761e-07 | 0.020063 | 0.005303 | 0.0093744 | 0.0053852 | N/A | 0.0020737 | 2.0584 | N/A | N/A | 1.011 | 0.00014352 | N/A | 1.011
JARVIS | Circuit | Distribution | 34.4038 |  | HFTD 3 | 0.0032147 | 0.0032083 | 6.4498e-06 | 0.0033627 | 0.00092552 | 0.00031535 | 0.0021218 | N/A | 0.024886 | 0.95408 | N/A | N/A | 1.1401 | 0.00025917 | N/A | 1.1401
JEEP | Circuit | Distribution | 18.6234 |  | HFTD 3 | 0.010142 | 0.010056 | 8.5974e-05 | 0.0057568 | 0.0040979 | 0.00065361 | 0.0010053 | N/A | 0.07533 | 1.7468 | N/A | N/A | 1.2811 | 0.0011413 | N/A | 1.2811
JELLYSTONE | Circuit | Distribution | 34.8891 |  | HFTD 2 | 0.042357 | 0.042337 | 2.0179e-05 | 0.0061098 | 0.0048305 | 0.00011077 | 0.0011685 | N/A | 0.054012 | 6.9294 | N/A | N/A | 1.2665 | 0.0003736 | N/A | 1.2665
JENKS LAKE | Circuit | Distribution | 14.7112 |  | HFTD 3 | 0.0013743 | 0.0013741 | 1.8382e-07 | 0.0088098 | 0.0054104 | 0.00086347 | 0.0025359 | N/A | 0.020674 | 0.15598 | N/A | N/A | 1.1465 | 8.8912e-06 | N/A | 1.1465
JERRY | Circuit | Distribution | 4.6367 |  | HFTD 2 | 0.0019395 | 0.0019327 | 6.8583e-06 | 0.0039677 | 0.0013762 | 0.00011132 | 0.0024802 | N/A | 0.0007736 | 0.4871 | N/A | N/A | 1.0449 | 0.0088655 | N/A | 1.0449
JERUSALEM | Circuit | Distribution | 0.82533 |  | HFTD 2 | 0.0044747 | 0.004461 | 1.3705e-05 | 0.0039862 | 0.0026228 | 6.5617e-05 | 0.0012978 | N/A | 0.0022181 | 1.1191 | N/A | N/A | 1.0665 | 0.0061787 | N/A | 1.0665
JOB | Circuit | Distribution | 5.4054 |  | HFTD 3 | 0.0039498 | 0.0039024 | 4.7387e-05 | 0.010068 | 0.0060412 | 0.0017294 | 0.0022977 | N/A | 0.048329 | 0.38759 | N/A | N/A | 1.266 | 0.00098049 | N/A | 1.266
JOHNBOY | Circuit | Distribution | 0.27332 |  | HFTD 3 | 0.0013879 | 0.0012021 | 0.00018579 | 0.031891 | 0.018508 | 0.0014315 | 0.011951 | N/A | 0.0080259 | 0.037695 | N/A | N/A | 1.0309 | 0.023149 | N/A | 1.0309
JOHNSONDALE | Circuit | Distribution | 3.5789 |  | HFTD 2 | 0.0033508 | 0.0033506 | 1.2298e-07 | 0.0062272 | 0.0030425 | 0.0020937 | 0.001091 | N/A | 0.0026753 | 0.53807 | N/A | N/A | 1.1219 | 4.5967e-05 | N/A | 1.1219
JORDAN | Circuit | Distribution | 162.5195 |  | HFTD 2 | 0.0010458 | 0.0010457 | 1.6273e-07 | 0.0012486 | 0.0010712 | 6.8385e-05 | 0.00010892 | N/A | 0.014321 | 0.83751 | N/A | N/A | 1.1876 | 1.1364e-05 | N/A | 1.1876
JUAREZ | Circuit | Distribution | 1.0657 |  | HFTD 2 | 0.0047408 | 0.0047311 | 9.6753e-06 | 0.017663 | 0.0031995 | 0.00076395 | 0.013699 | N/A | 0.00060728 | 0.26786 | N/A | N/A | 1.0598 | 0.015932 | N/A | 1.0598
JUBILEE | Circuit | Distribution | 0.51152 |  | HFTD 2 | 0.015958 | 0.015861 | 9.7111e-05 | 0.0050941 | 0.0025101 | 0.00028915 | 0.0022948 | N/A | 0.0021218 | 3.1135 | N/A | N/A | 1.0792 | 0.045768 | N/A | 1.0792
JUDSON | Circuit | Distribution | 0.44591 |  | HFTD 2 | 0.0071086 | 0.006989 | 0.00011955 | 0.0070872 | 0.0031261 | 0.00043416 | 0.003527 | N/A | 0.0004081 | 0.98614 | N/A | N/A | 1.052 | 0.29295 | N/A | 1.052
JULIUS | Circuit | Distribution | 6.2537 |  | HFTD 3 | 0.00073782 | 0.0007091 | 2.8719e-05 | 0.0091055 | 0.0062136 | 8.2658e-05 | 0.0028093 | N/A | 0.019315 | 0.077876 | N/A | N/A | 1.0577 | 0.0014869 | N/A | 1.0577
JUMBO | Circuit | Distribution | 0.64717 |  | HFTD 3 | 0.0011401 | 0.0011401 | 0 | 0.0095035 | 0.0020082 | 0.00063627 | 0.0068591 | N/A | 0.23944 | 0.11996 | N/A | N/A |  | 0 | N/A
JUPITER | Circuit | Distribution | 3.8138 |  | HFTD 2 | 0.0027504 | 0.0027504 | 0 | 0.023086 | 0.017037 | 0.0010998 | 0.0049493 | N/A | 0 | 0.11914 | N/A | N/A | 1.2979 |  | N/A | 1.2979
KANAN | Circuit | Distribution | 0.47952 |  | HFTD 3 | 0.0061509 | 0.0047039 | 0.001447 | 0.020356 | 0.0071405 | 0.0011233 | 0.012093 | N/A | 0.020065 | 0.23108 | N/A | N/A | 1.0982 | 0.072117 | N/A | 1.0982
KEENE | Circuit | Distribution | 37.6774 |  | HFTD 2 | 0.0044729 | 0.004468 | 4.888e-06 | 0.0026799 | 0.0020429 | 6.7495e-06 | 0.0006303 | N/A | 0.0012344 | 1.6672 | N/A | N/A | 1.3685 | 0.0039598 | N/A | 1.3685
KELLER | Circuit | Distribution | 1.39 |  | HFTD 2 | 0.014948 | 0.014948 | 0 | 0.0061999 | 0.0044005 | 0.00015732 | 0.001642 | N/A | 0 | 2.4111 | N/A | N/A | 1.0908 |  | N/A | 1.0908
KENO | Circuit | Distribution | 43.5679 | Top 5% Highest Risk | HFTD Tier 2 | 0.063753 | 0.063698 | 5.5064e-05 | 0.0062353 | 0.0042115 | 3.581e-05 | 0.001988 | N/A | 0.042354 | 10.2157 | N/A | N/A | 1.4892 | 0.0013001 | N/A | 1.4892
KERRY | Circuit | Distribution | 4.2578 |  | HFTD 2 | 0.0027295 | 0.0027268 | 2.6561e-06 | 0.006176 | 0.0026813 | 0.00034082 | 0.0031538 | N/A | 0.004625 | 0.44152 | N/A | N/A | 1.0935 | 0.00057429 | N/A | 1.0935
KEWAMEE | Circuit | Distribution | 0.57129 |  | HFTD 3 | 0.0094814 | 0.0093464 | 0.00013495 | 0.037832 | 0.006983 | 0.0011234 | 0.029725 | N/A | 0.0030459 | 0.24705 | N/A | N/A | 1.1131 | 0.044306 | N/A | 1.1131
KICKAPOO TRAIL | Circuit | Distribution | 49.4026 |  | HFTD 2 | 0.02749 | 0.02748 | 1.011e-05 | 0.0061631 | 0.0041268 | 0.00024609 | 0.0017902 | N/A | 0.053347 | 4.4588 | N/A | N/A | 1.0918 | 0.00018951 | N/A | 1.0918
KILKENNY | Circuit | Distribution | 4.4061 |  | HFTD 2 | 0.0036152 | 0.0036152 | 0 | 0.015432 | 0.0069472 | 0.0024807 | 0.0060039 | N/A | 0 | 0.23427 | N/A | N/A | 1.0918 |  | N/A | 1.0918
KILTS | Circuit | Distribution | 3.2791 |  | HFTD 2 | 0.0060797 | 0.0060546 | 2.5082e-05 | 0.007063 | 0.0028147 | 0.00044363 | 0.0038047 | N/A | 0.0029855 | 0.85723 | N/A | N/A | 1.1829 | 0.0084014 | N/A | 1.1829
KIMDALE | Circuit | Distribution | 49.0462 |  | HFTD 2 | 0.012758 | 0.012756 | 1.2835e-06 | 0.0033726 | 0.0025217 | 9.4641e-05 | 0.00075627 | N/A | 0.0087361 | 3.7824 | N/A | N/A | 1.2906 | 0.00014692 | N/A | 1.2906
KINGSFORD | Circuit | Distribution | 1.4332 |  | HFTD 2 | 0.0013035 | 0.0011985 | 0.00010497 | 0.0048544 | 0.0006346 | 0.00023735 | 0.0039825 | N/A | 0.0070282 | 0.24689 | N/A | N/A | 1.0624 | 0.014936 | N/A | 1.0624
KINNELOA | Circuit | Distribution | 3.8193 |  | HFTD 2 | 0.01665 | 0.016615 | 3.4271e-05 | 0.018966 | 0.013292 | 0.0024398 | 0.0032333 | N/A | 0.0022013 | 0.87609 | N/A | N/A | 1.1813 | 0.015568 | N/A | 1.1813
KINSEY | Circuit | Distribution | 38.6246 |  | HFTD 2 | 0.0019719 | 0.0019698 | 2.1578e-06 | 0.0028755 | 0.0012189 | 2.4894e-05 | 0.0016317 | N/A | 0.030701 | 0.68503 | N/A | N/A | 1.3641 | 7.0284e-05 | N/A | 1.3641
KIRBY | Circuit | Distribution | 0.81155 |  | HFTD 2 | 0.008332 | 0.0081442 | 0.00018776 | 0.014747 | 0.0058426 | 0.0030398 | 0.0058643 | N/A | 0.00023453 | 0.55228 | N/A | N/A | 1.0499 | 0.80059 | N/A | 1.0499
KLEVEN | Circuit | Distribution | 1.9284 |  | HFTD 3 | 0.021358 | 0.021337 | 2.0525e-05 | 0.013446 | 0.0084986 | 0.00026678 | 0.0046809 | N/A | 0.0032363 | 1.5868 | N/A | N/A | 1.1264 | 0.0063422 | N/A | 1.1264
KONA | Circuit | Distribution | 0.49136 |  | HFTD 2 | 0.0069435 | 0.0013869 | 0.0055566 | 0.0019353 | 0.0015798 | 5.4268e-05 | 0.00030116 | N/A | 0.0003509 | 0.71665 | N/A | N/A | 1.0793 | 15.8355 | N/A | 1.0793
KOREA | Circuit | Distribution | 1.1236 |  | HFTD 2 | 0.014169 | 0.014075 | 9.4776e-05 | 0.010299 | 0.0056792 | 0.00061423 | 0.0040055 | N/A | 0.0021654 | 1.3666 | N/A | N/A | 1.2609 | 0.043769 | N/A | 1.2609
KUEHNER | Circuit | Distribution | 4.933 |  | HFTD 3 | 0.0021689 | 0.0020248 | 0.00014416 | 0.025888 | 0.011919 | 0.00075425 | 0.013214 | N/A | 0.013463 | 0.078213 | N/A | N/A | 1.1265 | 0.010708 | N/A | 1.1265
KUFFEL | Circuit | Distribution | 3.4317 | Top 5% Highest Risk | HFTD Tier 3 | 0.049037 | 0.049004 | 3.3038e-05 | 0.018832 | 0.014145 | 0.001573 | 0.0031138 | N/A | 0.039338 | 2.6022 | N/A | N/A | 1.1861 | 0.00083984 | N/A | 1.1861
KULBERG | Circuit | Distribution | 1.8218 |  | HFTD 2 | 0.0062305 | 0.0062278 | 2.6894e-06 | 0.0035363 | 0.0013263 | 0.00020495 | 0.0020051 | N/A | 0.0010668 | 1.7611 | N/A | N/A | 1.0779 | 0.0025209 | N/A | 1.0779
KWIS | Circuit | Distribution | 0.78287 |  | HFTD 2 | 0.00028309 | 0.00027646 | 6.6316e-06 | 0.0047558 | 0.0012716 | 0.00063394 | 0.0028503 | N/A | 9.6583e-05 | 0.058131 | N/A | N/A | 1.0614 | 0.068662 | N/A | 1.0614
LA GRANDE | Circuit | Distribution | 1.0791 | Top 5% Highest Risk | HFTD Tier 2 | 0.044947 | 0.044764 | 0.0001828 | 0.013655 | 0.0074317 | 0.00031452 | 0.0059084 | N/A | 0.0035347 | 3.2783 | N/A | N/A | 1.1127 | 0.051716 | N/A | 1.1127
LA MANCHA | Circuit | Distribution | 7.6342 |  | HFTD 3 | 0.014162 | 0.01415 | 1.1623e-05 | 0.0072103 | 0.0042814 | 0.0001582 | 0.0027707 | N/A | 0.013376 | 1.9625 | N/A | N/A | 1.0547 | 0.0008689 | N/A | 1.0547
LA RICA | Circuit | Distribution | 0.35089 |  | HFTD 2 | 0.0027649 | 0.0027636 | 1.365e-06 | 0.020774 | 0.013938 | 0.00021291 | 0.006623 | N/A | 0.0023618 | 0.13303 | N/A | N/A | 1.1404 | 0.00057796 | N/A | 1.1404
LA SIERRA | Circuit | Distribution | 5.1973 |  | HFTD 2 | 0.0055536 | 0.0055305 | 2.3113e-05 | 0.0011514 | 0.00020487 | 0.00023449 | 0.00071205 | N/A | 0.0079182 | 4.8033 | N/A | N/A | 1.1322 | 0.002919 | N/A | 1.1322
LA VACA | Circuit | Distribution | 0.88229 |  | HFTD 3 | 0.00413 | 0.0037973 | 0.00033273 | 0.030023 | 0.020817 | 0.0018926 | 0.0073139 | N/A | 0.015356 | 0.12648 | N/A | N/A | 1.0565 | 0.021668 | N/A | 1.0565
LACRESTA | Circuit | Distribution | 5.9113 |  | HFTD 3 | 0.0048174 | 0.0048174 | 4.0304e-08 | 0.0013 | 0.00054312 | 6.3261e-05 | 0.00069364 | N/A | 0.0079679 | 3.7056 | N/A | N/A | 1.0928 | 5.0584e-06 | N/A | 1.0928
LAKELAND | Circuit | Distribution | 7.9567 |  | HFTD 2 | 0.014024 | 0.014004 | 2.0631e-05 | 0.014431 | 0.0089848 | 0.0019004 | 0.0035457 | N/A | 0.00683 | 0.9704 | N/A | N/A | 1.0681 | 0.0030206 | N/A | 1.0681
LAMANDA | Circuit | Distribution | 6.0826 |  | HFTD 3 | 0.01936 | 0.019354 | 6.5723e-06 | 0.006828 | 0.0033901 | 0.00029806 | 0.0031398 | N/A | 0.0047328 | 2.8345 | N/A | N/A | 1.4818 | 0.0013887 | N/A | 1.4818
LAMBDA | Circuit | Distribution | 0.65931 |  | HFTD 2 | 0.00077363 | 0.00077363 | 0 | 0.004893 | 0.0026699 | 0.00045968 | 0.0017634 | N/A | 0 | 0.15811 | N/A | N/A | 1.0476 |  | N/A | 1.0476
LANE | Circuit | Distribution | 2.5596 |  | HFTD 2 | 0.025802 | 0.025798 | 4.511e-06 | 0.023836 | 0.015107 | 0.0050553 | 0.0036731 | N/A | 0.012364 | 1.0823 | N/A | N/A | 1.1751 | 0.00036485 | N/A | 1.1751
LANGER | Circuit | Distribution | 11.7144 |  | HFTD 3 | 0.0085627 | 0.008541 | 2.1719e-05 | 0.015578 | 0.0069345 | 0.0017435 | 0.0069001 | N/A | 0.022396 | 0.54826 | N/A | N/A | 1.071 | 0.00096975 | N/A | 1.071
LARCH | Circuit | Distribution | 4.3916 |  | HFTD 2 | 0.0006132 | 0.00061269 | 5.0651e-07 | 0.0015088 | 0.00082418 | 9.6691e-05 | 0.0005879 | N/A | 0.0051082 | 0.40609 | N/A | N/A | 1.4737 | 9.9156e-05 | N/A | 1.4737
LARK | Circuit | Distribution | 6.6989 |  | HFTD 3 | 0.032375 | 0.032374 | 1.1731e-06 | 0.012963 | 0.011301 | 4.8345e-05 | 0.0016134 | N/A | 0.026741 | 2.4973 | N/A | N/A | 1.1296 | 4.3871e-05 | N/A | 1.1296
LASKER | Circuit | Distribution | 19.467 | Top 5% Highest Risk | HFTD Tier 3 | 0.10629 | 0.10625 | 3.2392e-05 | 0.009741 | 0.0044517 | 1.4186e-05 | 0.005275 | N/A | 0.0022469 | 10.9079 | N/A | N/A | 1.3504 | 0.014416 | N/A | 1.3504
LAST | Circuit | Distribution | 1.0534 |  | HFTD 2 | 0.0039748 | 0.0038821 | 9.2636e-05 | 0.0034682 | 0.0011667 | 0.00029808 | 0.0020034 | N/A | 0.011433 | 1.1194 | N/A | N/A | 1.1139 | 0.0081029 | N/A | 1.1139
LAUDA | Circuit | Distribution | 8.6501 |  | HFTD 3 | 0.0039167 | 0.0039167 | 1.837e-08 | 0.0026917 | 0.001194 | 2.9637e-05 | 0.001468 | N/A | 0.016235 | 1.4551 | N/A | N/A | 1.5 | 1.1315e-06 | N/A | 1.5
LAURO | Circuit | Distribution | 5.2513 |  | HFTD 2 | 0.013146 | 0.013138 | 8.1646e-06 | 0.018768 | 0.011575 | 0.0034582 | 0.0037338 | N/A | 0.0035617 | 0.70002 | N/A | N/A | 1.0926 | 0.0022923 | N/A | 1.0926
LAWMAN | Circuit | Distribution | 6.7794 |  | HFTD 2 | 0.0016269 | 0.0016135 | 1.3456e-05 | 0.015831 | 0.0085566 | 0.00068948 | 0.0065851 | N/A | 0.0064226 | 0.10192 | N/A | N/A | 1.0667 | 0.0020951 | N/A | 1.0667
LAZARO | Circuit | Distribution | 0.7304 |  | HFTD 3 | 0.0084859 | 0.0084859 | 0 | 0.0086462 | 0.004272 | 0.00012469 | 0.0042495 | N/A | 0.010701 | 0.98145 | N/A | N/A | 1.0718 | 0 | N/A | 1.0718
LEMONADE | Circuit | Distribution | 5.8967 |  | HFTD 3 | 0.011868 | 0.011858 | 1.0138e-05 | 0.0099789 | 0.0048797 | 0.00033799 | 0.0047612 | N/A | 0.0052417 | 1.1883 | N/A | N/A | 1.3279 | 0.0019341 | N/A | 1.3279
LEON | Circuit | Distribution | 1.0904 |  | HFTD 2 | 0.01936 | 0.01936 | 0 | 0.0091939 | 0.0049652 | 0.00031905 | 0.0039096 | N/A | 0.0010894 | 2.1058 | N/A | N/A | 1.0474 | 0 | N/A | 1.0474
LEONA | Circuit | Distribution | 2.9529 |  | HFTD 2 | 0.0082013 | 0.0080288 | 0.00017242 | 0.002798 | 0.00094099 | 1.0479e-05 | 0.0018466 | N/A | 0.0091565 | 2.8695 | N/A | N/A | 1.1081 | 0.018831 | N/A | 1.1081
LESSER | Circuit | Distribution | 2.3491 |  | HFTD 3 | 0.0016371 | 0.001629 | 8.1484e-06 | 0.04604 | 0.025803 | 0.0030733 | 0.017163 | N/A | 0.0026753 | 0.035381 | N/A | N/A | 1.0073 | 0.0030458 | N/A | 1.0073
LEVECHE | Circuit | Distribution | 9.1708 |  | HFTD 2 | 0.014322 | 0.014266 | 5.5428e-05 | 0.0036201 | 0.0015508 | 4.2992e-05 | 0.0020263 | N/A | 0.018126 | 3.9408 | N/A | N/A | 1.1129 | 0.003058 | N/A | 1.1129
LEXINGTON | Circuit | Distribution | 1.7406 |  | HFTD 3 | 0.0060213 | 0.0060102 | 1.1121e-05 | 0.013689 | 0.0088403 | 0.00069893 | 0.0041496 | N/A | 0.0061643 | 0.43906 | N/A | N/A | 1.0337 | 0.0018041 | N/A | 1.0337
LILAC | Circuit | Distribution | 2.9488 |  | HFTD 2 | 0.012193 | 0.012193 | 0 | 0.033855 | 0.0075041 | 0.011554 | 0.014798 | N/A | 0 | 0.36014 | N/A | N/A | 1.4715 |  | N/A | 1.4715
LIMA | Circuit | Distribution | 1.0484 |  | HFTD 2 | 0.0012105 | 0.0012018 | 8.7472e-06 | 0.019024 | 0.0076522 | 0.0054729 | 0.0058992 | N/A | 0.006095 | 0.06317 | N/A | N/A | 1.0524 | 0.0014351 | N/A | 1.0524
LIMBER | Circuit | Distribution | 0.6868 |  | HFTD 2 | 0.00010319 | 9.2477e-05 | 1.0715e-05 | 0.011692 | 0.0012357 | 0.00029618 | 0.01016 | N/A | 0.0029156 | 0.0079092 | N/A | N/A | 1.1698 | 0.003675 | N/A | 1.1698
LIMITED | Circuit | Distribution | 1.5426 | Top 5% Highest Risk | HFTD Tier 2 | 0.068837 | 0.068815 | 2.1764e-05 | 0.054867 | 0.032156 | 0.0037593 | 0.018952 | N/A | 0.0013568 | 1.2542 | N/A | N/A | 1.1741 | 0.016041 | N/A | 1.1741
LIMONITE | Circuit | Distribution | 2.7654 |  | HFTD 2 | 0.0047776 | 0.0047773 | 3.3784e-07 | 0.006365 | 0.0010234 | 0.00020022 | 0.0051414 | N/A | 0.0052575 | 0.75055 | N/A | N/A | 1 | 6.4259e-05 | N/A | 1
LINDERO | Circuit | Distribution | 0.48455 |  | HFTD 3 | 0.0034744 | 0.0034202 | 5.4193e-05 | 0.023218 | 0.0087565 | 0.00090116 | 0.01356 | N/A | 0.0053506 | 0.14731 | N/A | N/A | 1.2911 | 0.010128 | N/A | 1.2911
LINEBACKER | Circuit | Distribution | 0.56383 |  | HFTD 2 | 0.0021172 | 0.0021041 | 1.3049e-05 | 0.012831 | 0.00775 | 0.00012357 | 0.0049573 | N/A | 0.0034548 | 0.16399 | N/A | N/A | 1.0341 | 0.0037771 | N/A | 1.0341
LINNET | Circuit | Distribution | 5.2131 |  | HFTD 3 | 0.034853 | 0.034849 | 3.557e-06 | 0.010507 | 0.0085718 | 0.0010874 | 0.00084828 | N/A | 0.010701 | 3.3166 | N/A | N/A | 1.2323 | 0.00033239 | N/A | 1.2323
LITTLE MOUNTAIN | Circuit | Distribution | 2.697 |  | HFTD 2 | 0.00036357 | 0.00036357 | 0 | 0.00074705 | 0.00011382 | 5.2451e-05 | 0.00058078 | N/A | 0.0090639 | 0.48668 | N/A | N/A |  | 0 | N/A
LIVERMORE | Circuit | Distribution | 3.0395 |  | HFTD 2 | 0.0061626 | 0.0061365 | 2.6055e-05 | 0.0034242 | 0.00067983 | 0.0010635 | 0.0016808 | N/A | 0.0074003 | 1.7921 | N/A | N/A | 1.0485 | 0.0035208 | N/A | 1.0485
LOCKNER | Circuit | Distribution | 1.0046 |  | HFTD 2 | 0.022274 | 0.022087 | 0.00018715 | 0.0081402 | 0.0046621 | 6.8293e-05 | 0.0034098 | N/A | 0.001974 | 2.7133 | N/A | N/A | 1.0586 | 0.094809 | N/A | 1.0586
LOPEZ | Circuit | Distribution | 18.9594 |  | HFTD 3 | 0.026971 | 0.026921 | 5.0011e-05 | 0.0067529 | 0.0048132 | 0.00026114 | 0.0016786 | N/A | 0.048512 | 3.9866 | N/A | N/A | 1.0676 | 0.0010309 | N/A | 1.0676
LOS CARNEROS | Circuit | Distribution | 0.31139 |  | HFTD 3 | 0.00073888 | 0.00073888 | 0 | 0.017612 | 0.009288 | 0.001332 | 0.006992 | N/A | 0 | 0.041953 | N/A | N/A | 1.0315 |  | N/A | 1.0315
LOTTO | Circuit | Distribution | 4.1342 | Top 5% Highest Risk | HFTD Tier 2 | 0.09959 | 0.09959 | 0 | 0.010903 | 0.0070634 | 3.301e-05 | 0.0038068 | N/A | 0 | 9.1339 | N/A | N/A | 1.4367 |  | N/A | 1.4367
LOUCKS | Circuit | Distribution | 5.3546 |  | HFTD 3 | 0.015229 | 0.015229 | 4.8027e-07 | 0.0008702 | 0.0005474 | 0.00015445 | 0.00016835 | N/A | 0.049493 | 17.5005 | N/A | N/A | 1.0931 | 9.7038e-06 | N/A | 1.0931
LOWELL | Circuit | Distribution | 4.6476 |  | HFTD 3 | 0.0075509 | 0.0075467 | 4.1828e-06 | 0.012916 | 0.0054285 | 0.0037761 | 0.0037119 | N/A | 0.010798 | 0.58427 | N/A | N/A | 1.1128 | 0.00038738 | N/A | 1.1128
LUISENO | Circuit | Distribution | 18.104 | Top 5% Highest Risk | HFTD Tier 3 | 0.044697 | 0.044697 | 1.9939e-08 | 0.0082176 | 0.0049491 | 0.0002017 | 0.0030667 | N/A | 0.0019868 | 5.4392 | N/A | N/A | 1.9702 | 1.0036e-05 | N/A | 1.9702
LURING | Circuit | Distribution | 2.5412 |  | HFTD 3 | 0.013927 | 0.013898 | 2.8477e-05 | 0.011402 | 0.0070279 | 0.0029898 | 0.0013842 | N/A | 0.03036 | 1.2189 | N/A | N/A | 1.1597 | 0.00093796 | N/A | 1.1597
LYONS | Circuit | Distribution | 6.4568 |  | HFTD 3 | 0.0078406 | 0.0077498 | 9.0806e-05 | 0.030508 | 0.0096772 | 0.00055444 | 0.020277 | N/A | 0.012328 | 0.25402 | N/A | N/A | 1.0769 | 0.0073658 | N/A | 1.0769
LYTLE | Circuit | Distribution | 0.76932 |  | HFTD 2 | 0.00017353 | 4.9474e-05 | 0.00012405 | 0.0075653 | 0.0041016 | 0.00017999 | 0.0032837 | N/A | 0.0037284 | 0.0065397 | N/A | N/A | 1.1396 | 0.033273 | N/A | 1.1396
MACIEL | Circuit | Distribution | 2.0709 |  | HFTD 3 | 0.011266 | 0.011256 | 1.0194e-05 | 0.0018552 | 0.00076203 | 5.9611e-05 | 0.0010336 | N/A | 0.010701 | 6.0672 | N/A | N/A | 1.1533 | 0.00095258 | N/A | 1.1533
MAGIC | Circuit | Distribution | 0.25275 |  | HFTD 3 | 0.0051725 | 0.0051609 | 1.1589e-05 | 0.019937 | 0.0060357 | 8.8586e-05 | 0.013813 | N/A | 0.0040129 | 0.25886 | N/A | N/A | 1.0068 | 0.0028878 | N/A | 1.0068
MAGUIRE | Circuit | Distribution | 49.0098 |  | HFTD 3 | 0.030895 | 0.030894 | 7.4608e-07 | 0.0061106 | 0.0040862 | 8.8634e-05 | 0.0019357 | N/A | 0.024384 | 5.0558 | N/A | N/A | 1.2514 | 3.0597e-05 | N/A | 1.2514
MAHOGANY | Circuit | Distribution | 17.5007 |  | HFTD 2 | 0.00068158 | 0.00068158 | 0 | 0.0052239 | 0.0020747 | 0.0017323 | 0.0014168 | N/A | 0 | 0.13047 | N/A | N/A | 1.3028 |  | N/A | 1.3028
MAIZE | Circuit | Distribution | 1.3804 |  | HFTD 3 | 0.014303 | 0.014298 | 4.9979e-06 | 0.0048133 | 0.0042048 | 4.8303e-05 | 0.00056011 | N/A | 0.0062897 | 2.9706 | N/A | N/A | 1.1284 | 0.00079461 | N/A | 1.1284
MAJOR | Circuit | Distribution | 1.8241 |  | HFTD 2 | 0.017655 | 0.017655 | 0 | 0.03301 | 0.014056 | 0.0080414 | 0.010912 | N/A | 0 | 0.53484 | N/A | N/A | 1.5381 |  | N/A | 1.5381
MALAGA COVE | Circuit | Distribution | 1.1002 |  | HFTD 2 | 0.017884 | 0.017884 | 0 | 0.031458 | 0.015384 | 0.0089023 | 0.0071719 | N/A | 0 | 0.56851 | N/A | N/A | 1.0364 |  | N/A | 1.0364
MALLET | Circuit | Distribution | 0.48838 |  | HFTD 2 | 0.0063932 | 0.0063776 | 1.5593e-05 | 0.0097319 | 0.0039282 | 0.0022939 | 0.0035098 | N/A | 8.5957e-05 | 0.65533 | N/A | N/A | 1.0727 | 0.18141 | N/A | 1.0727
MALOY | Circuit | Distribution | 2.1115 |  | HFTD 3 | 0.0055058 | 0.0054972 | 8.6612e-06 | 0.011455 | 0.0081073 | 0.0002494 | 0.0030985 | N/A | 0.0027659 | 0.47988 | N/A | N/A | 1.1386 | 0.0031314 | N/A | 1.1386
MAMBA | Circuit | Distribution | 10.4415 |  | HFTD 3 | 0.0080409 | 0.0079872 | 5.368e-05 | 0.0074318 | 0.0036416 | 0.00026158 | 0.0035286 | N/A | 0.03223 | 1.0747 | N/A | N/A | 1.0849 | 0.0016655 | N/A | 1.0849
MANDARIN | Circuit | Distribution | 2.4209 |  | HFTD 2 | 0.028879 | 0.028851 | 2.878e-05 | 0.017289 | 0.0092763 | 0.00035053 | 0.0076618 | N/A | 0.0041948 | 1.6688 | N/A | N/A | 1.105 | 0.006861 | N/A | 1.105
MANIFOLD | Circuit | Distribution | 0.51959 |  | HFTD 3 | 0.00046527 | 0.00046527 | 0 | 0.0030835 | 0.0028995 | 8.4753e-06 | 0.00017551 | N/A | 0.0035277 | 0.15089 | N/A | N/A |  | 0 | N/A
MARCUS | Circuit | Distribution | 5.7943 |  | HFTD 3 | 0.0021343 | 0.0021226 | 1.1698e-05 | 0.016109 | 0.011199 | 9.9492e-05 | 0.0048101 | N/A | 0.01176 | 0.13177 | N/A | N/A | 1.161 | 0.00099473 | N/A | 1.161
MATILIJA | Circuit | Distribution | 17.9225 |  | HFTD 3 | 0.019069 | 0.019068 | 9.426e-07 | 0.022984 | 0.016249 | 0.0019589 | 0.0047761 | N/A | 0.0038718 | 0.82962 | N/A | N/A | 1.1122 | 0.00024345 | N/A | 1.1122
MAXSON | Circuit | Distribution | 1.7351 |  | HFTD 2 | 0.00094794 | 0.00074617 | 0.00020177 | 0.0056572 | 0.0037648 | 0.00050321 | 0.0013892 | N/A | 0.0012522 | 0.1319 | N/A | N/A | 1.105 | 0.16113 | N/A | 1.105
MAYBELL | Circuit | Distribution | 9.1522 |  | HFTD 2 | 0.015488 | 0.015486 | 2.6055e-06 | 0.011963 | 0.0046641 | 0.0014328 | 0.0058659 | N/A | 0.0033234 | 1.2945 | N/A | N/A | 1.1337 | 0.00078397 | N/A | 1.1337
MAYER | Circuit | Distribution | 11.4975 |  | HFTD 2 | 0.0059504 | 0.0059504 | 2.8346e-09 | 0.0024439 | 0.00083196 | 0.00010561 | 0.0015064 | N/A | 0.0044174 | 2.4348 | N/A | N/A | 1 | 6.4169e-07 | N/A | 1
MC ALLISTER | Circuit | Distribution | 1.6417 |  | HFTD 2 | 0.0040498 | 0.0040012 | 4.8569e-05 | 0.0061086 | 0.0018227 | 0.00017669 | 0.0041092 | N/A | 0.0046116 | 0.65502 | N/A | N/A | 1.1699 | 0.010532 | N/A | 1.1699
MCBEAN | Circuit | Distribution | 4.8938 |  | HFTD 3 | 0.0037086 | 0.0036048 | 0.00010386 | 0.026478 | 0.01441 | 0.00042819 | 0.01164 | N/A | 0.02555 | 0.13614 | N/A | N/A | 1.1302 | 0.0040651 | N/A | 1.1302
MCCLENNY | Circuit | Distribution | 1.7069 |  | HFTD 2 | 0.010899 | 0.010898 | 5.5146e-07 | 0.042056 | 0.022441 | 0.01848 | 0.0011349 | N/A | 0.010263 | 0.25913 | N/A | N/A | 1.2709 | 5.3731e-05 | N/A | 1.2709
MCGEE | Circuit | Distribution | 15.9652 |  | HFTD 2 | 0.014957 | 0.014907 | 5.0295e-05 | 0.005745 | 0.0044912 | 0.00044065 | 0.00081317 | N/A | 0.043194 | 2.5948 | N/A | N/A | 1.1556 | 0.0011644 | N/A | 1.1556
MCLAUGHLIN | Circuit | Distribution | 0.79035 |  | HFTD 2 | 0.009828 | 0.009828 | 0 | 0.0032514 | 0.0019139 | 0.0002264 | 0.0011111 | N/A | 0 | 3.0227 | N/A | N/A | 1.0409 |  | N/A | 1.0409
MEANDER | Circuit | Distribution | 0.26795 |  | HFTD 2 | 0.00015823 | 0.00013048 | 2.7754e-05 | 0.017636 | 0.0037242 | 0.0020686 | 0.011843 | N/A | 0.00020921 | 0.0073984 | N/A | N/A | 1.0899 | 0.13266 | N/A | 1.0899
MEBANE | Circuit | Distribution | 4.6228 |  | HFTD 2 | 0.00041164 | 0.00041141 | 2.3119e-07 | 0.0015132 | 0.0010178 | 2.7796e-05 | 0.0004676 | N/A | 0.014714 | 0.27188 | N/A | N/A | 1.1667 | 1.5712e-05 | N/A | 1.1667
MEDAL | Circuit | Distribution | 10.7714 |  | HFTD 2 | 0.014853 | 0.014851 | 1.5269e-06 | 0.013023 | 0.004621 | 0.0018745 | 0.0065272 | N/A | 0.0010558 | 1.1404 | N/A | N/A | 1.1365 | 0.0014462 | N/A | 1.1365
MEDUSA | Circuit | Distribution | 1.9851 |  | HFTD 2 | 0.00042163 | 0.00039514 | 2.6488e-05 | 0.0076794 | 0.00088496 | 0.00027462 | 0.0065198 | N/A | 0.011106 | 0.051455 | N/A | N/A | 1.1751 | 0.0023849 | N/A | 1.1751
MEMPHIS | Circuit | Distribution | 15.6549 |  | HFTD 2 | 0.03925 | 0.039248 | 2.1321e-06 | 0.013687 | 0.0079978 | 0.0020026 | 0.0036863 | N/A | 0.0080859 | 2.8676 | N/A | N/A | 1.1194 | 0.00026368 | N/A | 1.1194
MENIFEE | Circuit | Distribution | 15.8184 |  | HFTD 2 | 0.041778 | 0.041778 | 0 | 0.0083992 | 0.0041944 | 0.00087888 | 0.003326 | N/A | 0 | 4.974 | N/A | N/A | 1.1359 |  | N/A | 1.1359
MENTRY | Circuit | Distribution | 1.2461 |  | HFTD 3 | 0.00427 | 0.0042274 | 4.2626e-05 | 0.0083422 | 0.0042542 | 9.8817e-05 | 0.0039892 | N/A | 0.0045765 | 0.50675 | N/A | N/A | 1.0805 | 0.0093141 | N/A | 1.0805
MERLIN | Circuit | Distribution | 16.2978 |  | HFTD 3 | 0.019277 | 0.019265 | 1.1761e-05 | 0.017712 | 0.012139 | 0.00069813 | 0.0048741 | N/A | 0.034936 | 1.0877 | N/A | N/A | 1.1399 | 0.00033664 | N/A | 1.1399
MESA GRANDE | Circuit | Distribution | 6.3028 |  | HFTD 3 | 0.035562 | 0.035557 | 5.1094e-06 | 0.0072565 | 0.0044683 | 0.00050012 | 0.0022882 | N/A | 0.0053244 | 4.8999 | N/A | N/A | 1.179 | 0.00095962 | N/A | 1.179
METTLER | Circuit | Distribution | 24.0056 |  | HFTD 3 | 0.014252 | 0.014251 | 1.7712e-06 | 0.0027141 | 0.0023077 | 0.0001938 | 0.00021267 | N/A | 0.086809 | 5.2506 | N/A | N/A | 1.2158 | 2.0403e-05 | N/A | 1.2158
MIDDLE ROAD | Circuit | Distribution | 16.5774 |  | HFTD 3 | 0.00094671 | 0.000945 | 1.7114e-06 | 0.0024097 | 0.0017238 | 0.00024841 | 0.00043748 | N/A | 0.010727 | 0.39217 | N/A | N/A | 1.0575 | 0.00015955 | N/A | 1.0575
MILO | Circuit | Distribution | 7.6475 |  | HFTD 3 | 0.0045309 | 0.0045018 | 2.9082e-05 | 0.012516 | 0.0061628 | 0.00043689 | 0.0059167 | N/A | 0.013316 | 0.35968 | N/A | N/A | 1.0494 | 0.0021841 | N/A | 1.0494
MILPAS | Circuit | Distribution | 0.8496 |  | HFTD 2 | 0.044223 | 0.044088 | 0.00013559 | 0.024893 | 0.011284 | 0.001036 | 0.012573 | N/A | 0.0011352 | 1.7711 | N/A | N/A | 1.0406 | 0.11944 | N/A | 1.0406
MINT CANYON | Circuit | Distribution | 1.671 |  | HFTD 3 | 0.02287 | 0.022821 | 4.9123e-05 | 0.022929 | 0.0045556 | 6.244e-05 | 0.018311 | N/A | 0.012024 | 0.99529 | N/A | N/A | 1.0487 | 0.0040855 | N/A | 1.0487
MIRAMAR | Circuit | Distribution | 2.1166 |  | HFTD 2 | 0.0057612 | 0.0057557 | 5.5447e-06 | 0.015195 | 0.0077703 | 0.0063966 | 0.0010278 | N/A | 0.0048999 | 0.3788 | N/A | N/A | 1.2779 | 0.0011316 | N/A | 1.2779
MIST | Circuit | Distribution | 40.1616 |  | HFTD 3 | 0.0015895 | 0.0015876 | 1.8766e-06 | 0.006224 | 0.0037051 | 0.00078702 | 0.0017319 | N/A | 0.060146 | 0.25508 | N/A | N/A | 1.2073 | 3.1201e-05 | N/A | 1.2073
MOAB | Circuit | Distribution | 0.51563 |  | HFTD 2 | 0.017962 | 0.01795 | 1.1993e-05 | 0.0083801 | 0.001651 | 0.00086835 | 0.0058608 | N/A | 0.021402 | 2.1419 | N/A | N/A | 1.0061 | 0.00056038 | N/A | 1.0061
MOCCASIN | Circuit | Distribution | 5.9113 |  | HFTD 3 | 0.0037998 | 0.0037832 | 1.6611e-05 | 0.016506 | 0.0064698 | 0.00010097 | 0.0099357 | N/A | 0.0069429 | 0.22919 | N/A | N/A | 1.089 | 0.0023926 | N/A | 1.089
MOCKINGBIRD | Circuit | Distribution | 6.4597 |  | HFTD 2 | 0.031374 | 0.031358 | 1.6273e-05 | 0.012695 | 0.0073914 | 0.0027277 | 0.002576 | N/A | 0.03876 | 2.4701 | N/A | N/A | 1.0761 | 0.00041983 | N/A | 1.0761
MODJESKA | Circuit | Distribution | 1.1898 |  | HFTD 2 | 0.024105 | 0.023877 | 0.00022791 | 0.0071654 | 0.0018352 | 0.0038714 | 0.0014588 | N/A | 0.02248 | 3.3323 | N/A | N/A | 1.1175 | 0.010138 | N/A | 1.1175
MONACHE | Circuit | Distribution | 0.66211 |  | HFTD 2 | 0.0024624 | 0.0024624 | 0 | 0.0045068 | 0.0029537 | 0.00014258 | 0.0014105 | N/A | 0.00011396 | 0.54638 | N/A | N/A | 1.1104 | 0 | N/A | 1.1104
MONARCH | Circuit | Distribution | 3.1102 |  | HFTD 3 | 0.00052923 | 0.00033687 | 0.00019236 | 0.027135 | 0.0086509 | 0.0012106 | 0.017273 | N/A | 0.015541 | 0.012415 | N/A | N/A | 1.0325 | 0.012377 | N/A | 1.0325
MONTGOMERY | Circuit | Distribution | 6.4862 |  | HFTD 3 | 0.00043968 | 0.00030254 | 0.00013713 | 0.018687 | 0.010174 | 0.00077381 | 0.0077389 | N/A | 0.023291 | 0.01619 | N/A | N/A | 1.1303 | 0.0058878 | N/A | 1.1303
MONTREAL | Circuit | Distribution | 11.7722 |  | HFTD 3 | 0.0099383 | 0.0099067 | 3.1624e-05 | 0.011093 | 0.0066031 | 0.00084119 | 0.0036486 | N/A | 0.014679 | 0.89307 | N/A | N/A | 1.493 | 0.0021544 | N/A | 1.493
MORELAND | Circuit | Distribution | 7.527 |  | HFTD 3 | 0.0054093 | 0.005365 | 4.4347e-05 | 0.018917 | 0.0098313 | 0.0018121 | 0.0072736 | N/A | 0.022315 | 0.28361 | N/A | N/A | 1.0741 | 0.0019873 | N/A | 1.0741
MORELLO | Circuit | Distribution | 6.3664 |  | HFTD 2 | 0.017486 | 0.017485 | 1.0382e-06 | 0.0039266 | 0.0020729 | 0.00014623 | 0.0017075 | N/A | 0.023289 | 4.4528 | N/A | N/A | 1.1682 | 4.458e-05 | N/A | 1.1682
MORGANSTEIN | Circuit | Distribution | 18.8783 |  | HFTD 3 | 0.028857 | 0.02884 | 1.6994e-05 | 0.013976 | 0.0057892 | 0.00026717 | 0.0079197 | N/A | 0.027733 | 2.0635 | N/A | N/A | 1.1542 | 0.00061277 | N/A | 1.1542
MORITZ | Circuit | Distribution | 19.5269 |  | HFTD 3 | 0.011715 | 0.011602 | 0.00011374 | 0.008899 | 0.0065039 | 0.00083415 | 0.001561 | N/A | 0.11051 | 1.3037 | N/A | N/A | 1.1241 | 0.0010292 | N/A | 1.1241
MORONGO | Circuit | Distribution | 32.9784 |  | HFTD 2 | 0.011518 | 0.011504 | 1.3343e-05 | 0.0036171 | 0.0025662 | 0.00034852 | 0.00070236 | N/A | 0.062035 | 3.1805 | N/A | N/A | 1.2597 | 0.00021509 | N/A | 1.2597
MORRIE | Circuit | Distribution | 0.47697 |  | HFTD 3 | 0.0041053 | 0.0040871 | 1.8134e-05 | 0.010885 | 0.0054422 | 4.8624e-05 | 0.0053945 | N/A | 0.0093635 | 0.37547 | N/A | N/A | 1.0312 | 0.0019366 | N/A | 1.0312
MORRIS | Circuit | Distribution | 1.4011 |  | HFTD 2 | 0.0072151 | 0.0072129 | 2.2217e-06 | 0.0014301 | 0.00037413 | 4.5442e-05 | 0.0010106 | N/A | 0.00055884 | 5.0435 | N/A | N/A | 1.1998 | 0.0039756 | N/A | 1.1998
MOSQUITO | Circuit | Distribution | 0.60208 |  | HFTD 2 | 0.0018886 | 0.0018814 | 7.2189e-06 | 0.0032419 | 0.0010856 | 0.00013862 | 0.0020176 | N/A | 0.0020782 | 0.58034 | N/A | N/A | 1.2 | 0.0034737 | N/A | 1.2
MT. GIVENS | Circuit | Distribution | 8.0814 |  | HFTD 3 | 4.0437e-05 | 4.037e-05 | 6.6668e-08 | 0.0011335 | 0.00052639 | 0.00037428 | 0.00023283 | N/A | 0.014714 | 0.035615 | N/A | N/A | 1.2719 | 4.5309e-06 | N/A | 1.2719
MUDDY | Circuit | Distribution | 3.8197 |  | HFTD 2 | 0.011304 | 0.011293 | 1.0397e-05 | 0.013308 | 0.0031774 | 0.0014915 | 0.0086394 | N/A | 0.0016136 | 0.84858 | N/A | N/A | 1.0794 | 0.0064432 | N/A | 1.0794
MULHOLLAND | Circuit | Distribution | 23.9801 | Top 5% Highest Risk | HFTD Tier 3 | 0.061761 | 0.061759 | 1.6902e-06 | 0.0080989 | 0.0045466 | 0.00062914 | 0.0029231 | N/A | 0.0091236 | 7.6257 | N/A | N/A | 1.2742 | 0.00018525 | N/A | 1.2742
MUNICH | Circuit | Distribution | 0.33662 |  | HFTD 2 | 0.0014523 | 0.00093788 | 0.00051446 | 0.0018887 | 0.00061738 | 0.00022199 | 0.0010494 | N/A | 0.017153 | 0.49657 | N/A | N/A | 1.1073 | 0.029992 | N/A | 1.1073
MUSTANG | Circuit | Distribution | 44.9938 | Top 5% Highest Risk | HFTD Tier 3 | 0.045159 | 0.045139 | 2.0155e-05 | 0.013065 | 0.0096436 | 0.00037877 | 0.0030428 | N/A | 0.039406 | 3.4549 | N/A | N/A | 1.2286 | 0.00051147 | N/A | 1.2286
MUTUAL | Circuit | Distribution | 4.9166 | Top 5% Highest Risk | HFTD Tier 3 | 0.04444 | 0.044104 | 0.00033573 | 0.013775 | 0.0044834 | 0.0037017 | 0.0055898 | N/A | 0.035833 | 3.2018 | N/A | N/A | 1.0574 | 0.0093694 | N/A | 1.0574
MYRTLE | Circuit | Distribution | 0.39085 |  | HFTD 3 | 0.0055208 | 0.0054798 | 4.099e-05 | 0.0098599 | 0.0081704 | 0.00037258 | 0.0013169 | N/A | 0.0018843 | 0.55577 | N/A | N/A | 1.0439 | 0.021754 | N/A | 1.0439
NAPA | Circuit | Distribution | 6.897 |  | HFTD 2 | 0.0093565 | 0.0093491 | 7.3864e-06 | 0.0043063 | 0.0017972 | 8.8817e-05 | 0.0024203 | N/A | 0.0024153 | 2.171 | N/A | N/A | 1.2559 | 0.0030581 | N/A | 1.2559
NAPOLEON | Circuit | Distribution | 3.9541 |  | HFTD 2 | 0.018925 | 0.018851 | 7.345e-05 | 0.0027788 | 0.0020652 | 0.00011659 | 0.00059703 | N/A | 0.0082231 | 6.784 | N/A | N/A | 1.1165 | 0.0089322 | N/A | 1.1165
NASHVILLE | Circuit | Distribution | 4.8476 |  | HFTD 2 | 0.013398 | 0.013388 | 9.7388e-06 | 0.0083281 | 0.001581 | 0.0017589 | 0.0049882 | N/A | 0.0044537 | 1.6076 | N/A | N/A | 1.058 | 0.0021867 | N/A | 1.058
NATIONS | Circuit | Distribution | 11.5433 |  | HFTD 2 | 0.042927 | 0.042926 | 1.102e-06 | 0.0056636 | 0.0034244 | 9.7347e-05 | 0.0021418 | N/A | 0.0040007 | 7.5794 | N/A | N/A | 1.3306 | 0.00027545 | N/A | 1.3306
NAVEL | Circuit | Distribution | 0.25046 |  | HFTD 2 | 0.00076413 | 0.00029497 | 0.00046916 | 0.00081625 | 0.00019291 | 7.2133e-06 | 0.00061613 | N/A | 0.0011333 | 0.36137 | N/A | N/A | 1.0481 | 0.41396 | N/A | 1.0481
NEAPOLITAN | Circuit | Distribution | 2.1659 |  | HFTD 2 | 0.0096018 | 0.009595 | 6.7444e-06 | 0.012463 | 0.007783 | 0.0008086 | 0.0038713 | N/A | 0.0023249 | 0.76989 | N/A | N/A | 1.1958 | 0.002901 | N/A | 1.1958
NEARGATE | Circuit | Distribution | 9.8181 |  | HFTD 3 | 0.018965 | 0.018929 | 3.6046e-05 | 0.02718 | 0.016058 | 0.00062397 | 0.010498 | N/A | 0.015959 | 0.69644 | N/A | N/A | 1.074 | 0.0022587 | N/A | 1.074
NEPAL | Circuit | Distribution | 3.1241 |  | HFTD 3 | 0.03245 | 0.032414 | 3.5969e-05 | 0.026175 | 0.0089797 | 0.0017704 | 0.015425 | N/A | 0.0071567 | 1.2384 | N/A | N/A | 1.1389 | 0.0050259 | N/A | 1.1389
NERO | Circuit | Distribution | 6.8522 |  | HFTD 3 | 0.0033895 | 0.0033743 | 1.5235e-05 | 0.026045 | 0.013679 | 0.00085877 | 0.011507 | N/A | 0.01694 | 0.12956 | N/A | N/A | 1.1649 | 0.00089934 | N/A | 1.1649
NIGHTHAWK | Circuit | Distribution | 2.9642 |  | HFTD 3 | 0.0091474 | 0.0091413 | 6.0346e-06 | 0.010305 | 0.0045344 | 0.00011132 | 0.0056596 | N/A | 0.0054327 | 0.88705 | N/A | N/A | 1.032 | 0.0011108 | N/A | 1.032
NORTH BAY | Circuit | Distribution | 2.3747 |  | HFTD 3 | 0.014261 | 0.014245 | 1.628e-05 | 0.017647 | 0.013174 | 0.0022069 | 0.0022656 | N/A | 0.011975 | 0.80722 | N/A | N/A | 1.0037 | 0.0013595 | N/A | 1.0037
NORTH SHORE | Circuit | Distribution | 7.3691 |  | HFTD 3 | 0.013745 | 0.013694 | 5.1661e-05 | 0.0085044 | 0.0052784 | 0.0012675 | 0.0019585 | N/A | 0.056346 | 1.6102 | N/A | N/A | 1.0931 | 0.00091685 | N/A | 1.0931
NORTHPARK | Circuit | Distribution | 26.2106 |  | HFTD 2 | 0.014512 | 0.01445 | 6.2078e-05 | 0.0071635 | 0.0049486 | 8.4003e-05 | 0.0021309 | N/A | 0.11759 | 2.0172 | N/A | N/A | 1.1628 | 0.00052791 | N/A | 1.1628
NORTHRIDGE | Circuit | Distribution | 0.33651 |  | HFTD 2 | 0.00011353 | 0.00011353 | 0 | 0.010426 | 0.0020032 | 0.0034815 | 0.0049414 | N/A | 0 | 0.010889 | N/A | N/A | 1.5149 |  | N/A | 1.5149
NOVA | Circuit | Distribution | 3.0384 |  | HFTD 2 | 0.0031725 | 0.0031505 | 2.1993e-05 | 0.0041034 | 0.0012193 | 0.00015774 | 0.0027263 | N/A | 0.0010989 | 0.76778 | N/A | N/A | 1.1317 | 0.020014 | N/A | 1.1317
NUBIA | Circuit | Distribution | 0.59462 |  | HFTD 2 | 0.00091127 | 0.00085703 | 5.424e-05 | 0.012508 | 0.0090299 | 0.00038577 | 0.003092 | N/A | 0.00094267 | 0.06852 | N/A | N/A | 1.0721 | 0.057539 | N/A | 1.0721
NUTMEG | Circuit | Distribution | 6.9535 |  | HFTD 3 | 0.020191 | 0.020191 | 5.2586e-07 | 0.0060954 | 0.0036215 | 9.4881e-05 | 0.0023791 | N/A | 0.00093268 | 3.3125 | N/A | N/A | 1.1731 | 0.00056381 | N/A | 1.1731
O'TOOLE | Circuit | Distribution | 4.3571 |  | HFTD 2 | 0.0031267 | 0.0031236 | 3.0952e-06 | 0.0094375 | 0.0051089 | 0.00045523 | 0.0038734 | N/A | 0.0029827 | 0.33098 | N/A | N/A | 1.0719 | 0.0010377 | N/A | 1.0719
OAK GLEN | Circuit | Distribution | 20.8976 |  | HFTD 3 | 0.014793 | 0.014787 | 6.1498e-06 | 0.010768 | 0.0054908 | 0.00043673 | 0.0048407 | N/A | 0.016726 | 1.3732 | N/A | N/A | 1.1109 | 0.00036767 | N/A | 1.1109
OAK KNOLL | Circuit | Distribution | 3.7166 |  | HFTD 3 | 0.0023302 | 0.002318 | 1.2216e-05 | 0.011934 | 0.0057888 | 0.0029479 | 0.0031976 | N/A | 0.03876 | 0.19423 | N/A | N/A | 1.339 | 0.00031517 | N/A | 1.339
OAKDALE | Circuit | Distribution | 12.163 |  | HFTD 2 | 0.032813 | 0.032811 | 1.8708e-06 | 0.012587 | 0.007861 | 0.0001795 | 0.0045468 | N/A | 0.00095862 | 2.6067 | N/A | N/A | 1.2336 | 0.0019516 | N/A | 1.2336
OAKWOOD | Circuit | Distribution | 4.2112 |  | HFTD 2 | 0.0005024 | 0.00050099 | 1.4126e-06 | 0.013221 | 0.0071435 | 0.0019982 | 0.004079 | N/A | 0.0075014 | 0.037894 | N/A | N/A | 1.0718 | 0.00018831 | N/A | 1.0718
OLIVER | Circuit | Distribution | 14.7074 |  | HFTD 2 | 0.0021243 | 0.0021243 | 1.6491e-08 | 0.001405 | 0.00037247 | 5.1566e-05 | 0.00098093 | N/A | 0.0059053 | 1.512 | N/A | N/A | 1 | 2.7926e-06 | N/A | 1
OLYMPIAD | Circuit | Distribution | 0.42 |  | HFTD 2 | 0.02536 | 0.025002 | 0.00035771 | 0.034834 | 0.00061407 | 0.026242 | 0.0079783 | N/A | 0.020065 | 0.71774 | N/A | N/A | 1.1808 | 0.017828 | N/A | 1.1808
OMEGA | Circuit | Distribution | 13.1863 |  | HFTD 3 | 0.028319 | 0.028319 | 0 | 0.012328 | 0.0052335 | 0.0012887 | 0.0058058 | N/A | 0 | 2.2971 | N/A | N/A | 1.1705 |  | N/A | 1.1705
ONAGA | Circuit | Distribution | 7.1373 |  | HFTD 2 | 0.011884 | 0.011805 | 7.8732e-05 | 0.0046874 | 0.0033621 | 9.8963e-05 | 0.0012263 | N/A | 0.014848 | 2.5184 | N/A | N/A | 1.0882 | 0.0053027 | N/A | 1.0882
ONBORD | Circuit | Distribution | 6.2127 |  | HFTD 3 | 0.022067 | 0.022014 | 5.266e-05 | 0.010926 | 0.0060662 | 0.00075001 | 0.0041099 | N/A | 0.023595 | 2.0148 | N/A | N/A | 1.1881 | 0.0022318 | N/A | 1.1881
ORION | Circuit | Distribution | 3.4612 |  | HFTD 3 | 0.010937 | 0.0107 | 0.00023666 | 0.0092602 | 0.0046351 | 5.203e-05 | 0.0045731 | N/A | 0.027535 | 1.1555 | N/A | N/A | 1.0536 | 0.008595 | N/A | 1.0536
OSLO | Circuit | Distribution | 1.215 |  | HFTD 3 | 0.0040129 | 0.0038719 | 0.00014105 | 0.00092752 | 0.00052591 | 1.0399e-05 | 0.00039121 | N/A | 0.011211 | 4.1744 | N/A | N/A | 1.0498 | 0.012582 | N/A | 1.0498
OVERHILL | Circuit | Distribution | 0.35914 |  | HFTD 2 | 0.00010638 | 0.00010638 | 0 | 0.0097693 | 0.001877 | 0.0032622 | 0.0046301 | N/A | 0 | 0.010889 | N/A | N/A | 1.1189 |  | N/A | 1.1189
OVERLOOK | Circuit | Distribution | 2.6012 |  | HFTD 2 | 0.00078537 | 0.00074185 | 4.3523e-05 | 0.019265 | 0.0062559 | 0.0021681 | 0.010841 | N/A | 0.0057157 | 0.038508 | N/A | N/A | 1.0079 | 0.0076146 | N/A | 1.0079
OWENS | Circuit | Distribution | 5.5076 |  | HFTD 2 | 0.0037218 | 0.0037214 | 4.0523e-07 | 0.0086725 | 0.0033961 | 0.00014299 | 0.0051334 | N/A | 0.0065475 | 0.42911 | N/A | N/A | 1.2018 | 6.189e-05 | N/A | 1.2018
PADOVA | Circuit | Distribution | 0.48284 |  | HFTD 2 | 0.019094 | 0.018995 | 9.8641e-05 | 0.021257 | 0.0098722 | 0.00052243 | 0.010863 | N/A | 0.0019499 | 0.89358 | N/A | N/A | 1.2073 | 0.050587 | N/A | 1.2073
PAINTED CAVE | Circuit | Distribution | 1.9247 |  | HFTD 3 | 0.0060052 | 0.0060048 | 3.3375e-07 | 0.0094895 | 0.0050506 | 0.0010169 | 0.003422 | N/A | 0.0013185 | 0.63279 | N/A | N/A | 1.0068 | 0.00025314 | N/A | 1.0068
PALACE | Circuit | Distribution | 0.77248 |  | HFTD 2 | 0.002258 | 0.0021208 | 0.00013717 | 0.0085005 | 0.0018683 | 0.00050775 | 0.0061244 | N/A | 0.0033995 | 0.2495 | N/A | N/A | 1.062 | 0.040349 | N/A | 1.062
PALMER | Circuit | Distribution | 6.3665 |  | HFTD 2 | 0.0064858 | 0.0064845 | 1.2636e-06 | 0.011314 | 0.0041464 | 0.0015723 | 0.0055954 | N/A | 0.0065005 | 0.57314 | N/A | N/A | 1.3182 | 0.00019438 | N/A | 1.3182
PALOMA | Circuit | Distribution | 1.7546 |  | HFTD 3 | 0.013163 | 0.013088 | 7.5304e-05 | 0.0091994 | 0.0034194 | 0.00027842 | 0.0055016 | N/A | 0.0057893 | 1.4227 | N/A | N/A | 1.1 | 0.013007 | N/A | 1.1
PALOMINO | Circuit | Distribution | 6.7799 |  | HFTD 2 | 0.015618 | 0.015618 | 0 | 0.0063741 | 0.0047697 | 0.00011265 | 0.0014917 | N/A | 0.0012857 | 2.4503 | N/A | N/A | 1.0584 | 0 | N/A | 1.0584
PANCAKE | Circuit | Distribution | 1.4131 |  | HFTD 2 | 0.0030654 | 0.0030654 | 0 | 0.0093781 | 0.0036756 | 0.0030317 | 0.0026708 | N/A | 0 | 0.32687 | N/A | N/A | 1.2397 |  | N/A | 1.2397
PANCHO | Circuit | Distribution | 0.84103 |  | HFTD 2 | 0.00028461 | 0.00024841 | 3.6203e-05 | 0.0049587 | 0.0016043 | 0.00069122 | 0.0026632 | N/A | 0.00041045 | 0.050096 | N/A | N/A | 1.0942 | 0.088203 | N/A | 1.0942
PAR | Circuit | Distribution | 0.29316 |  | HFTD 3 | 0.018175 | 0.018175 | 0 | 0.049417 | 0.024121 | 0.013787 | 0.011509 | N/A | 0 | 0.36779 | N/A | N/A | 1.0129 |  | N/A | 1.0129
PARADISE | Circuit | Distribution | 13.3843 |  | HFTD 3 | 0.034538 | 0.034536 | 2.6537e-06 | 0.013953 | 0.0097701 | 0.0010081 | 0.0031747 | N/A | 0.012802 | 2.4752 | N/A | N/A | 1.2349 | 0.00020729 | N/A | 1.2349
PARCO | Circuit | Distribution | 0.37859 | Top 5% Highest Risk | HFTD Tier 2 | 0.045834 | 0.045148 | 0.00068536 | 0.01308 | 0.0089796 | 0.00013384 | 0.0039663 | N/A | 0.0013551 | 3.4517 | N/A | N/A | 1.1143 | 0.50577 | N/A | 1.1143
PARINA | Circuit | Distribution | 0.56765 |  | HFTD 2 | 0.0011784 | 0.0011373 | 4.1106e-05 | 0.0063373 | 0.0027262 | 0.00015193 | 0.0034592 | N/A | 0.00081263 | 0.17946 | N/A | N/A | 1.0588 | 0.050584 | N/A | 1.0588
PARSONS | Circuit | Distribution | 0.46292 |  | HFTD 2 | 0.021127 | 0.020784 | 0.000343 | 0.0057115 | 0.0015486 | 0.00038586 | 0.0037771 | N/A | 0.00066699 | 3.639 | N/A | N/A | 1.1522 | 0.51425 | N/A | 1.1522
PASCAL | Circuit | Distribution | 9.8184 | Top 5% Highest Risk | HFTD Tier 3 | 0.075647 | 0.075643 | 4.2297e-06 | 0.0090393 | 0.0051734 | 3.0839e-05 | 0.0038351 | N/A | 0.0051563 | 8.3682 | N/A | N/A | 1.2032 | 0.00082029 | N/A | 1.2032
PASCOE | Circuit | Distribution | 7.0127 |  | HFTD 3 | 0.0053014 | 0.0052981 | 3.3222e-06 | 0.02578 | 0.017164 | 0.0033515 | 0.0052649 | N/A | 0.039015 | 0.20551 | N/A | N/A | 1.449 | 8.5151e-05 | N/A | 1.449
PATHE | Circuit | Distribution | 0.41962 |  | HFTD 2 | 0.0087499 | 0.0087499 | 0 | 0.012438 | 0.0077908 | 0.0012212 | 0.0034258 | N/A | 0 | 0.70349 | N/A | N/A | 1.0801 |  | N/A | 1.0801
PATRICIA | Circuit | Distribution | 36.4383 |  | HFTD 3 | 0.008838 | 0.0088366 | 1.3648e-06 | 0.0057312 | 0.0041386 | 0.00036395 | 0.0012287 | N/A | 0.015054 | 1.5418 | N/A | N/A | 1.0875 | 9.0664e-05 | N/A | 1.0875
PATRIOT | Circuit | Distribution | 5.821 |  | HFTD 3 | 0.0073843 | 0.0073486 | 3.5659e-05 | 0.022763 | 0.01633 | 0.0004353 | 0.0059973 | N/A | 0.014446 | 0.32283 | N/A | N/A | 1.0588 | 0.0024684 | N/A | 1.0588
PAWLEY | Circuit | Distribution | 54.4708 |  | HFTD 2 | 0.0045523 | 0.0045518 | 4.8195e-07 | 0.0061791 | 0.0044389 | 0.00082725 | 0.00091293 | N/A | 0.010342 | 0.73665 | N/A | N/A | 1.0983 | 4.6603e-05 | N/A | 1.0983
PAWNEE | Circuit | Distribution | 48.7884 |  | HFTD 3 | 0.023473 | 0.023472 | 1.0501e-06 | 0.0030628 | 0.0024192 | 0.0001052 | 0.0005384 | N/A | 0.0083144 | 7.6636 | N/A | N/A | 1.2358 | 0.0001263 | N/A | 1.2358
PAYNE | Circuit | Distribution | 9.0474 |  | HFTD 2 | 0.0081707 | 0.0081611 | 9.5294e-06 | 0.017883 | 0.0064273 | 0.0023329 | 0.0091233 | N/A | 0.0051941 | 0.45635 | N/A | N/A | 1.0884 | 0.0018346 | N/A | 1.0884
PEACOCK | Circuit | Distribution | 1.0193 |  | HFTD 2 | 0.035252 | 0.035252 | 0 | 0.032395 | 0.02365 | 0.0054241 | 0.0033206 | N/A | 0 | 1.0882 | N/A | N/A | 1.7588 |  | N/A | 1.7588
PEAR | Circuit | Distribution | 2.0457 |  | HFTD 2 | 0.0064503 | 0.0064375 | 1.2849e-05 | 0.0069321 | 0.0017262 | 0.00041945 | 0.0047864 | N/A | 0.0044563 | 0.92864 | N/A | N/A | 1.0801 | 0.0028833 | N/A | 1.0801
PEARCE | Circuit | Distribution | 2.7514 |  | HFTD 3 | 0.0019424 | 0.0019361 | 6.2481e-06 | 0.010291 | 0.0074283 | 0.00040886 | 0.0024542 | N/A | 0.0044908 | 0.18813 | N/A | N/A | 1.0901 | 0.0013913 | N/A | 1.0901
PELONA | Circuit | Distribution | 1.5643 | Both >1% and Top 5% | HFTD Tier 3 | 0.13247 | 0.13247 | 0 | 0.015045 | 0.0037262 | 5.0619e-05 | 0.011269 | N/A | 0.046818 | 8.8048 | N/A | N/A | 1.1395 | 0 | N/A | 1.1395
PENDLETON | Circuit | Distribution | 1.0978 |  | HFTD 2 | 0.023017 | 0.022925 | 9.2105e-05 | 0.0076542 | 0.0034292 | 0.00019054 | 0.0040344 | N/A | 0.0028732 | 2.995 | N/A | N/A | 1.0549 | 0.032056 | N/A | 1.0549
PENINSULA | Circuit | Distribution | 0.50119 |  | HFTD 3 | 0.021714 | 0.021582 | 0.00013137 | 0.0033866 | 0.00062903 | 0.00024309 | 0.0025145 | N/A | 0.0016681 | 6.3728 | N/A | N/A | 1.158 | 0.078755 | N/A | 1.158
PENSTOCK | Circuit | Distribution | 45.2612 |  | HFTD 3 | 0.014001 | 0.013935 | 6.5468e-05 | 0.0047558 | 0.002659 | 5.5192e-05 | 0.0020417 | N/A | 0.078504 | 2.9302 | N/A | N/A | 1.3524 | 0.00083394 | N/A | 1.3524
PERIMETER | Circuit | Distribution | 20.0393 |  | HFTD 3 | 0.00097481 | 0.00097411 | 7.0138e-07 | 0.00411 | 0.0027231 | 0.00089086 | 0.00049604 | N/A | 0.011812 | 0.23701 | N/A | N/A | 1.2552 | 5.9378e-05 | N/A | 1.2552
PERRIS | Circuit | Distribution | 3.0676 | Top 5% Highest Risk | HFTD Tier 2 | 0.052765 | 0.052757 | 7.3789e-06 | 0.0076409 | 0.0037352 | 0.0010156 | 0.00289 | N/A | 0.0013471 | 6.9046 | N/A | N/A | 1.1393 | 0.0054776 | N/A | 1.1393
PETIT | Circuit | Distribution | 11.2285 |  | HFTD 3 | 0.0042647 | 0.0042425 | 2.228e-05 | 0.0083207 | 0.0054584 | 0.00020011 | 0.0026622 | N/A | 0.011911 | 0.50987 | N/A | N/A | 1.3147 | 0.0018706 | N/A | 1.3147
PHEASANT | Circuit | Distribution | 4.6219 | Top 5% Highest Risk | HFTD Tier 3 | 0.048791 | 0.048791 | 3.9717e-07 | 0.0023759 | 0.001393 | 0.00020642 | 0.0007765 | N/A | 0.0066805 | 20.5355 | N/A | N/A | 1.5232 | 5.9452e-05 | N/A | 1.5232
PHOTON | Circuit | Distribution | 11.8398 |  | HFTD 2 | 0.0068831 | 0.0068831 | 0 | 0.0033791 | 0.0017342 | 8.3109e-05 | 0.0015617 | N/A | 0.001154 | 2.037 | N/A | N/A | 1.0837 | 0 | N/A | 1.0837
PICK | Circuit | Distribution | 40.0216 |  | HFTD 3 | 0.030977 | 0.030976 | 6.9659e-07 | 0.0047836 | 0.0036649 | 0.0001755 | 0.00094323 | N/A | 0.042346 | 6.4756 | N/A | N/A | 1.0903 | 1.645e-05 | N/A | 1.0903
PICKENS | Circuit | Distribution | 0.8193 |  | HFTD 2 | 0.0051985 | 0.004899 | 0.00029948 | 0.018787 | 0.009276 | 0.0031343 | 0.0063764 | N/A | 0.0028832 | 0.26077 | N/A | N/A | 1.0495 | 0.10387 | N/A | 1.0495
PICKLE MEADOWS | Circuit | Distribution | 22.5182 |  | HFTD 2 | 0.0027234 | 0.0027209 | 2.4496e-06 | 0.002218 | 0.00099663 | 3.5721e-05 | 0.0011856 | N/A | 0.07058 | 1.2268 | N/A | N/A | 1.5546 | 3.4707e-05 | N/A | 1.5546
PICONI | Circuit | Distribution | 18.7025 | Top 5% Highest Risk | HFTD Tier 3 | 0.04677 | 0.04677 | 7.3109e-08 | 0.008115 | 0.0032759 | 0.00034442 | 0.0044947 | N/A | 0.0038034 | 5.7634 | N/A | N/A | 1.1739 | 1.9222e-05 | N/A | 1.1739
PIEDMONT | Circuit | Distribution | 0.38723 |  | HFTD 2 | 0.00033072 | 0.00022556 | 0.00010516 | 0.023843 | 0.017112 | 0.0024689 | 0.0042624 | N/A | 0.0024117 | 0.0094602 | N/A | N/A | 1.4964 | 0.043603 | N/A | 1.4964
PIEDRA | Circuit | Distribution | 1.5648 |  | HFTD 2 | 0.00087151 | 0.00086829 | 3.2218e-06 | 0.0020467 | 0.0007422 | 4.3057e-05 | 0.0012614 | N/A | 0.00038299 | 0.42425 | N/A | N/A | 1.0832 | 0.0084122 | N/A | 1.0832
PIMA | Circuit | Distribution | 1.5232 |  | HFTD 2 | 0.0029201 | 0.0029201 | 0 | 0.017689 | 0.0095858 | 0.0014066 | 0.0066962 | N/A | 0.0013376 | 0.16508 | N/A | N/A | 1.1605 | 0 | N/A | 1.1605
PINE COVE | Circuit | Distribution | 19.8209 |  | HFTD 3 | 0.0015308 | 0.0015241 | 6.7003e-06 | 0.0039238 | 0.0033385 | 0.00010018 | 0.00048509 | N/A | 0.031263 | 0.38843 | N/A | N/A | 1.2584 | 0.00021432 | N/A | 1.2584
PINEWOOD | Circuit | Distribution | 1.1943 | Top 5% Highest Risk | HFTD Tier 2 | 0.077016 | 0.076902 | 0.00011472 | 0.0037339 | 0.0032129 | 7.048e-05 | 0.00045056 | N/A | 0.00040579 | 20.5953 | N/A | N/A | 1.18 | 0.28271 | N/A | 1.18
PINTO | Circuit | Distribution | 12.7381 |  | HFTD 2 | 0.019367 | 0.019367 | 1.467e-07 | 0.0030518 | 0.0016569 | 0.00028955 | 0.0011054 | N/A | 0.040803 | 6.3459 | N/A | N/A | 2 | 3.5952e-06 | N/A | 2
PINWHEEL | Circuit | Distribution | 1.3552 |  | HFTD 2 | 0.015341 | 0.01534 | 1.0312e-06 | 0.011643 | 0.0058916 | 3.5324e-05 | 0.0057164 | N/A | 0.0059544 | 1.3175 | N/A | N/A | 1.8158 | 0.00017318 | N/A | 1.8158
PINZON | Circuit | Distribution | 2.4795 |  | HFTD 2 | 0.011696 | 0.011696 | 0 | 0.025848 | 0.0065446 | 0.0044737 | 0.01483 | N/A | 0 | 0.4525 | N/A | N/A | 1.0331 |  | N/A | 1.0331
PIONEERTOWN | Circuit | Distribution | 55.6487 | Top 5% Highest Risk | HFTD Tier 3 | 0.046819 | 0.046812 | 7.2179e-06 | 0.0075794 | 0.0057102 | 0.00017898 | 0.0016902 | N/A | 0.065902 | 6.1762 | N/A | N/A | 1.1383 | 0.00010952 | N/A | 1.1383
PLACID | Circuit | Distribution | 26.0674 |  | HFTD 3 | 0.031702 | 0.031691 | 1.1685e-05 | 0.0089141 | 0.0043147 | 0.0002481 | 0.0043513 | N/A | 0.014389 | 3.5551 | N/A | N/A | 1.0997 | 0.00081205 | N/A | 1.0997
PLATEAU | Circuit | Distribution | 21.8371 |  | HFTD 3 | 0.020632 | 0.020609 | 2.2582e-05 | 0.0098872 | 0.0048454 | 0.0012938 | 0.0037481 | N/A | 0.029832 | 2.0844 | N/A | N/A | 1.2256 | 0.00075698 | N/A | 1.2256
PLAYBOY | Circuit | Distribution | 0.3316 |  | HFTD 2 | 0.00040699 | 0.00025923 | 0.00014777 | 0.03246 | 0.005976 | 0.0031614 | 0.023322 | N/A | 0.00061623 | 0.0079861 | N/A | N/A | 1.0916 | 0.23979 | N/A | 1.0916
PLAYER | Circuit | Distribution | 1.0616 |  | HFTD 2 | 0.00015655 | 0.00015364 | 2.9105e-06 | 0.009408 | 0.0016572 | 0.001082 | 0.0066688 | N/A | 0.0059522 | 0.01633 | N/A | N/A | 2 | 0.00048897 | N/A | 2
PLUTO | Circuit | Distribution | 5.5754 |  | HFTD 2 | 0.0010644 | 0.0010644 | 0 | 0.028041 | 0.022435 | 0.00032597 | 0.0052793 | N/A | 0.0013297 | 0.037961 | N/A | N/A | 1.5151 | 0 | N/A | 1.5151
POLYMER | Circuit | Distribution | 1.2362 |  | HFTD 3 | 0.0033596 | 0.0033575 | 2.0999e-06 | 0.0098352 | 0.0039194 | 0.00013136 | 0.0057844 | N/A | 0.012039 | 0.34137 | N/A | N/A | 1.3296 | 0.00017443 | N/A | 1.3296
POPPET FLATS | Circuit | Distribution | 28.513 | Top 5% Highest Risk | HFTD Tier 2 | 0.056838 | 0.056838 | 0 | 0.010597 | 0.0088267 | 5.9357e-05 | 0.0017108 | N/A | 0.25966 | 5.3637 | N/A | N/A | 1.3515 | 0 | N/A | 1.3515
PORCELAIN | Circuit | Distribution | 4.627 |  | HFTD 2 | 0.0046107 | 0.00461 | 7.0611e-07 | 0.0045139 | 0.0038749 | 9.9887e-05 | 0.00053911 | N/A | 0.0051719 | 1.0213 | N/A | N/A | 1.012 | 0.00013653 | N/A | 1.012
PORPHYRY | Circuit | Distribution | 3.3898 |  | HFTD 3 | 0.0034754 | 0.0034751 | 3.5222e-07 | 0.0043801 | 0.0017662 | 0.00017502 | 0.0024389 | N/A | 0.0090149 | 0.79337 | N/A | N/A | 1 | 3.9071e-05 | N/A | 1
POSO PARK | Circuit | Distribution | 0.61918 |  | HFTD 2 | 0.006023 | 0.006023 | 0 | 0.007505 | 0.0032082 | 0.0028648 | 0.001432 | N/A | 0.013376 | 0.80253 | N/A | N/A | 1.6713 | 0 | N/A | 1.6713
POTATO | Circuit | Distribution | 2.0914 |  | HFTD 2 | 0.0067446 | 0.0061219 | 0.00062267 | 0.016077 | 0.0045951 | 0.0038504 | 0.0076314 | N/A | 0.0026985 | 0.38079 | N/A | N/A | 1.1077 | 0.23074 | N/A | 1.1077
POTTERY | Circuit | Distribution | 6.3457 |  | HFTD 2 | 0.0030209 | 0.0030187 | 2.2584e-06 | 0.010168 | 0.0041261 | 0.0020509 | 0.0039913 | N/A | 0.0034877 | 0.29687 | N/A | N/A | 1.1008 | 0.00064753 | N/A | 1.1008
POULTRY | Circuit | Distribution | 18.7779 |  | HFTD 3 | 0.014374 | 0.014369 | 5.1404e-06 | 0.009081 | 0.0057439 | 0.00092396 | 0.0024132 | N/A | 0.011187 | 1.5823 | N/A | N/A | 1.1821 | 0.00045949 | N/A | 1.1821
POWELL | Circuit | Distribution | 8.8964 |  | HFTD 3 | 0.011425 | 0.011379 | 4.5983e-05 | 0.026015 | 0.011298 | 0.00095265 | 0.013765 | N/A | 0.038103 | 0.43741 | N/A | N/A | 1.0945 | 0.0012068 | N/A | 1.0945
POWER | Circuit | Distribution | 1.7512 |  | HFTD 2 | 0.0085837 | 0.0080604 | 0.00052332 | 0.0069882 | 0.0027317 | 0.00022067 | 0.0040358 | N/A | 0.0067653 | 1.1534 | N/A | N/A | 1.5066 | 0.077354 | N/A | 1.5066
PRADO | Circuit | Distribution | 0.29419 |  | HFTD 3 | 0.00027512 | 0.00021103 | 6.4083e-05 | 0.026815 | 0.014229 | 0.00099207 | 0.011595 | N/A | 0.0040129 | 0.0078699 | N/A | N/A | 1.0235 | 0.015969 | N/A | 1.0235
PREDATOR | Circuit | Distribution | 2.4115 |  | HFTD 2 | 0.0040473 | 0.0040377 | 9.6391e-06 | 0.0057072 | 0.001934 | 0.00026523 | 0.003508 | N/A | 0.0019978 | 0.70747 | N/A | N/A | 1.134 | 0.0048249 | N/A | 1.134
PRESTON | Circuit | Distribution | 2.2142 |  | HFTD 3 | 0.011797 | 0.011604 | 0.0001932 | 0.0088376 | 0.0018259 | 0.00041118 | 0.0066005 | N/A | 0.0030556 | 1.313 | N/A | N/A | 1.1053 | 0.063229 | N/A | 1.1053
PRIMROSE | Circuit | Distribution | 9.8323 |  | HFTD 3 | 0.011502 | 0.011487 | 1.5219e-05 | 0.013452 | 0.0070157 | 0.0011362 | 0.0052998 | N/A | 0.010853 | 0.85396 | N/A | N/A | 1.0983 | 0.0014023 | N/A | 1.0983
PRONGHORN | Circuit | Distribution | 19.0646 |  | HFTD 3 | 0.018202 | 0.018191 | 1.1569e-05 | 0.0048949 | 0.0035633 | 3.1445e-05 | 0.0013002 | N/A | 0.021069 | 3.7162 | N/A | N/A | 1.2852 | 0.0005491 | N/A | 1.2852
PUESTA | Circuit | Distribution | 7.8926 |  | HFTD 3 | 0.027012 | 0.027002 | 9.5651e-06 | 0.020477 | 0.016095 | 0.0010405 | 0.0033421 | N/A | 0.011588 | 1.3186 | N/A | N/A | 1.1624 | 0.00082544 | N/A | 1.1624
PUFF | Circuit | Distribution | 6.6402 |  | HFTD 2 | 0.013965 | 0.013961 | 4.313e-06 | 0.012083 | 0.0078483 | 3.0373e-05 | 0.0042041 | N/A | 0.015648 | 1.1554 | N/A | N/A | 1.3753 | 0.00027562 | N/A | 1.3753
PURCHASE | Circuit | Distribution | 3.0183 | Top 5% Highest Risk | HFTD Tier 3 | 0.07278 | 0.072778 | 1.2109e-06 | 0.021593 | 0.014012 | 0.00010228 | 0.0074782 | N/A | 0.031448 | 3.3705 | N/A | N/A | 1.2309 | 3.8504e-05 | N/A | 1.2309
PYLE | Circuit | Distribution | 1.3253 |  | HFTD 3 | 0.0010022 | 0.0009671 | 3.5102e-05 | 0.003523 | 0.0022508 | 4.5781e-05 | 0.0012264 | N/A | 0.0024067 | 0.27451 | N/A | N/A | 1.0747 | 0.014585 | N/A | 1.0747
PYTHON | Circuit | Distribution | 20.7639 |  | HFTD 3 | 0.031495 | 0.031468 | 2.6817e-05 | 0.017061 | 0.0085304 | 0.00035457 | 0.008176 | N/A | 0.063266 | 1.8444 | N/A | N/A | 1.1347 | 0.00042387 | N/A | 1.1347
QUARRY | Circuit | Distribution | 3.7789 |  | HFTD 2 | 0.010913 | 0.010871 | 4.2512e-05 | 0.01571 | 0.010361 | 0.0003782 | 0.0049707 | N/A | 0.0027317 | 0.69198 | N/A | N/A | 1.1933 | 0.015562 | N/A | 1.1933
QUICKSILVER | Circuit | Distribution | 13.5697 |  | HFTD 2 | 0.0077903 | 0.0077903 | 0 | 0.017376 | 0.0070614 | 0.0011359 | 0.0091785 | N/A | 0.0026501 | 0.44834 | N/A | N/A | 1.2946 | 0 | N/A | 1.2946
QUINBY | Circuit | Distribution | 2.269 | Top 5% Highest Risk | HFTD Tier 2 | 0.06205 | 0.062004 | 4.522e-05 | 0.010879 | 0.0023546 | 0.00016514 | 0.0083597 | N/A | 0.0026985 | 5.6992 | N/A | N/A | 1.0889 | 0.016757 | N/A | 1.0889
QUIXOTE | Circuit | Distribution | 0.46646 |  | HFTD 2 | 0.0034403 | 0.0034397 | 6.0837e-07 | 0.0089092 | 0.0019496 | 5.2012e-05 | 0.0069076 | N/A | 0.0059578 | 0.38608 | N/A | N/A | 1.6316 | 0.00010211 | N/A | 1.6316
RACER | Circuit | Distribution | 1.3554 |  | HFTD 3 | 0.00074441 | 0.0006708 | 7.3607e-05 | 0.017905 | 0.0036154 | 0.00011423 | 0.014175 | N/A | 0.0079565 | 0.037466 | N/A | N/A | 1.1887 | 0.0092512 | N/A | 1.1887
RAINBOW | Circuit | Distribution | 9.4507 |  | HFTD 3 | 0.0022202 | 0.0022108 | 9.3512e-06 | 0.0045207 | 0.0034648 | 0.00027741 | 0.00077849 | N/A | 0.012298 | 0.48905 | N/A | N/A | 1.1642 | 0.00076038 | N/A | 1.1642
RAISIN | Circuit | Distribution | 2.5822 |  | HFTD 2 | 0.0040103 | 0.0035206 | 0.0004897 | 0.010204 | 0.002332 | 0.00027571 | 0.0075959 | N/A | 0.0036075 | 0.34504 | N/A | N/A | 1.1316 | 0.13575 | N/A | 1.1316
RAMAC | Circuit | Distribution | 5.7507 |  | HFTD 2 | 0.00032051 | 0.00030892 | 1.1588e-05 | 0.0019928 | 0.0011236 | 0.00054012 | 0.00032912 | N/A | 0.0019494 | 0.15502 | N/A | N/A | 1.1092 | 0.005944 | N/A | 1.1092
RAMSGATE | Circuit | Distribution | 0.90627 |  | HFTD 3 | 0.0036093 | 0.003457 | 0.00015234 | 0.0041655 | 0.0024157 | 0.00017897 | 0.0015708 | N/A | 0.0074001 | 0.82991 | N/A | N/A | 1.0712 | 0.020586 | N/A | 1.0712
RANGER | Circuit | Distribution | 3.792 |  | HFTD 3 | 0.025633 | 0.025588 | 4.547e-05 | 0.015621 | 0.0081496 | 0.0041426 | 0.0033284 | N/A | 0.0394 | 1.6381 | N/A | N/A | 1.1101 | 0.001154 | N/A | 1.1101
RANIER | Circuit | Distribution | 2.2314 |  | HFTD 2 | 0.0093578 | 0.009353 | 4.7396e-06 | 0.0016572 | 0.0013125 | 0.00013499 | 0.00020972 | N/A | 0.004927 | 5.6439 | N/A | N/A | 1.1074 | 0.00096197 | N/A | 1.1074
RANKIN | Circuit | Distribution | 13.1821 |  | HFTD 2 | 0.009395 | 0.0093947 | 3.3844e-07 | 0.0051044 | 0.003466 | 3.7844e-05 | 0.0016006 | N/A | 0.020753 | 1.8405 | N/A | N/A | 1.0133 | 1.6308e-05 | N/A | 1.0133
RAVINE | Circuit | Distribution | 11.5292 |  | HFTD 2 | 0.0041088 | 0.0041074 | 1.4738e-06 | 0.012243 | 0.0065046 | 0.0020679 | 0.0036703 | N/A | 0.0088692 | 0.33549 | N/A | N/A | 1.0494 | 0.00016617 | N/A | 1.0494
RAYBURN | Circuit | Distribution | 10.4027 | Top 5% Highest Risk | HFTD Tier 3 | 0.093218 | 0.0932 | 1.7483e-05 | 0.010494 | 0.0057848 | 7.6178e-06 | 0.0047015 | N/A | 0.049097 | 8.8814 | N/A | N/A | 1.1122 | 0.00035609 | N/A | 1.1122
READY | Circuit | Distribution | 1.8401 |  | HFTD 2 | 0.0038804 | 0.0038211 | 5.9262e-05 | 0.010019 | 0.0064627 | 0.0011023 | 0.0024536 | N/A | 0.0029061 | 0.38141 | N/A | N/A | 1.0476 | 0.020392 | N/A | 1.0476
RED BOX | Circuit | Distribution | 17.6731 |  | HFTD 3 | 0.0018991 | 0.0018984 | 7.8349e-07 | 0.005853 | 0.002193 | 0.00069779 | 0.0029622 | N/A | 0.031407 | 0.32434 | N/A | N/A | 1.261 | 2.4947e-05 | N/A | 1.261
RED MOUNTAIN | Circuit | Distribution | 14.9151 |  | HFTD 3 | 0.0011989 | 0.0011982 | 7.4978e-07 | 0.0068263 | 0.0037929 | 0.00063816 | 0.0023953 | N/A | 0 | 0.17552 | N/A | N/A | 1.5519 | inf | N/A | 1.5519
REDBALL | Circuit | Distribution | 0.86218 |  | HFTD 2 | 0.024797 | 0.024547 | 0.00025012 | 0.010228 | 0.00092423 | 0.0016714 | 0.0076326 | N/A | 0.0078408 | 2.3999 | N/A | N/A | 1.0348 | 0.0319 | N/A | 1.0348
REDBANKS | Circuit | Distribution | 0.47531 |  | HFTD 2 | 0.00042832 | 0.00042832 | 0 | 0.0016987 | 0.0007354 | 1.2797e-05 | 0.00095055 | N/A | 0 | 0.25214 | N/A | N/A | 1.1087 |  | N/A | 1.1087
REED | Circuit | Distribution | 1.5804 |  | HFTD 2 | 0.026701 | 0.026677 | 2.3982e-05 | 0.0063333 | 0.0030364 | 0.00045257 | 0.0028444 | N/A | 0.00355 | 4.2121 | N/A | N/A | 1.0863 | 0.0067556 | N/A | 1.0863
REEDER | Circuit | Distribution | 0.34556 |  | HFTD 2 | 0.016233 | 0.016164 | 6.9623e-05 | 0.019437 | 0.014199 | 0.0010068 | 0.0042305 | N/A | 0.00016368 | 0.8316 | N/A | N/A | 1.1872 | 0.42536 | N/A | 1.1872
REJADA | Circuit | Distribution | 3.4134 |  | HFTD 3 | 0.015094 | 0.015048 | 4.5767e-05 | 0.020606 | 0.0097723 | 0.00095063 | 0.0098831 | N/A | 0.025197 | 0.73028 | N/A | N/A | 1.0589 | 0.0018163 | N/A | 1.0589
RESORT | Circuit | Distribution | 14.9474 |  | HFTD 3 | 0.0021122 | 0.0021121 | 9.0174e-08 | 0.0038677 | 0.0020787 | 0.00021607 | 0.001573 | N/A | 0.01532 | 0.54609 | N/A | N/A | 1.9386 | 5.8859e-06 | N/A | 1.9386
REVERSE PEAK | Circuit | Distribution | 19.8102 |  | HFTD 2 | 0.0043182 | 0.0042029 | 0.00011535 | 0.0040826 | 0.0026619 | 0.00031574 | 0.001105 | N/A | 0.13229 | 1.0295 | N/A | N/A | 1.1481 | 0.00087194 | N/A | 1.1481
RHINEDOLLAR | Circuit | Distribution | 1.5636 |  | HFTD 2 | 0.00054464 | 0.00047804 | 6.6604e-05 | 0.0041748 | 0.0027461 | 0.00010422 | 0.0013245 | N/A | 0.093635 | 0.11451 | N/A | N/A | 1.2069 | 0.00071131 | N/A | 1.2069
RHODA | Circuit | Distribution | 3.4839 | Top 5% Highest Risk | HFTD Tier 3 | 0.066731 | 0.066711 | 2.0465e-05 | 0.02204 | 0.0039744 | 0.0014592 | 0.016607 | N/A | 0.012826 | 3.0267 | N/A | N/A | 1.0932 | 0.0015956 | N/A | 1.0932
RICARDO | Circuit | Distribution | 2.7868 |  | HFTD 3 | 0.0084084 | 0.0083923 | 1.609e-05 | 0.023189 | 0.012422 | 0.0020484 | 0.0087189 | N/A | 0.0025406 | 0.36191 | N/A | N/A | 1.0516 | 0.0063334 | N/A | 1.0516
RIDGE | Circuit | Distribution | 17.5426 |  | HFTD 2 | 0.013777 | 0.013775 | 2.0078e-06 | 0.0084161 | 0.0035882 | 6.4396e-05 | 0.0047635 | N/A | 0.024235 | 1.6367 | N/A | N/A | 1.1819 | 8.2849e-05 | N/A | 1.1819
RIDGEMOOR | Circuit | Distribution | 0.53779 |  | HFTD 2 | 0.0012749 | 0.0011935 | 8.1352e-05 | 0.010504 | 0.0010829 | 0.00017942 | 0.0092416 | N/A | 0.00018229 | 0.11363 | N/A | N/A | 1.1147 | 0.44627 | N/A | 1.1147
RIM | Circuit | Distribution | 18.9527 |  | HFTD 3 | 0.015416 | 0.015373 | 4.3305e-05 | 0.01438 | 0.0084405 | 0.0023952 | 0.0035439 | N/A | 0.063569 | 1.069 | N/A | N/A | 1.2379 | 0.00068123 | N/A | 1.2379
RINCON | Circuit | Distribution | 1.8683 |  | HFTD 2 | 0.015262 | 0.015262 | 0 | 0.011653 | 0.007547 | 0.00098552 | 0.0031204 | N/A | 0 | 1.3097 | N/A | N/A | 1.0723 |  | N/A | 1.0723
RITTER | Circuit | Distribution | 0.95344 |  | HFTD 2 | 0.012961 | 0.012845 | 0.00011625 | 0.0062779 | 0.00095239 | 1.2617e-05 | 0.0053129 | N/A | 0.021148 | 2.046 | N/A | N/A | 1.1477 | 0.0054968 | N/A | 1.1477
RIVA | Circuit | Distribution | 26.6789 |  | HFTD 3 | 0.0087391 | 0.0087391 | 0 | 0.017621 | 0.010388 | 0.0010262 | 0.0062061 | N/A | 0 | 0.49596 | N/A | N/A | 1.1008 |  | N/A | 1.1008
RIVIERA | Circuit | Distribution | 3.8523 |  | HFTD 2 | 0.022844 | 0.022842 | 2.0039e-06 | 0.017025 | 0.014231 | 0.0018335 | 0.00096113 | N/A | 0.0038764 | 1.3416 | N/A | N/A | 1.248 | 0.00051695 | N/A | 1.248
RMV 1243 | Circuit | Distribution | 1.5212 |  | HFTD 2 | 0.0029756 | 0.0029709 | 4.774e-06 | 0.0081353 | 0.00063772 | 0.0053778 | 0.0021198 | N/A | 0.0020592 | 0.36518 | N/A | N/A | 1.7885 | 0.0023184 | N/A | 1.7885
ROADRUNNER | Circuit | Distribution | 7.0498 |  | HFTD 2 | 0.013882 | 0.013867 | 1.5175e-05 | 0.0048007 | 0.0026 | 0.00025372 | 0.001947 | N/A | 0.0078301 | 2.8886 | N/A | N/A | 1.5112 | 0.001938 | N/A | 1.5112
ROBIN | Circuit | Distribution | 11.5491 |  | HFTD 3 | 0.018767 | 0.018766 | 9.6709e-07 | 0.012475 | 0.007665 | 0.00025955 | 0.0045503 | N/A | 0.058645 | 1.5043 | N/A | N/A | 1.1875 | 1.649e-05 | N/A | 1.1875
ROBINSON CREEK | Circuit | Distribution | 14.692 |  | HFTD 2 | 0.0052551 | 0.0052152 | 3.9903e-05 | 0.0086412 | 0.0075757 | 4.1338e-05 | 0.0010242 | N/A | 0.046818 | 0.60352 | N/A | N/A | 1.5047 | 0.00085231 | N/A | 1.5047
ROCKCREEK | Circuit | Distribution | 11.4706 |  | HFTD 2 | 0.018781 | 0.018757 | 2.424e-05 | 0.0059972 | 0.00369 | 2.3893e-05 | 0.0022833 | N/A | 0.067566 | 3.1275 | N/A | N/A | 1.8321 | 0.00035876 | N/A | 1.8321
ROCKHILL | Circuit | Distribution | 13.0051 |  | HFTD 2 | 0.0118 | 0.0118 | 3.4656e-07 | 0.016351 | 0.0069126 | 0.0041146 | 0.0053238 | N/A | 0 | 0.72164 | N/A | N/A | 1.3133 | inf | N/A | 1.3133
ROCKRIDGE | Circuit | Distribution | 1.9285 |  | HFTD 2 | 0.0050848 | 0.0050739 | 1.0882e-05 | 0.0050513 | 0.00091815 | 0.00014837 | 0.0039848 | N/A | 0.0039757 | 1.0045 | N/A | N/A | 1.0771 | 0.0027371 | N/A | 1.0771
ROCKWELL | Circuit | Distribution | 6.3427 |  | HFTD 2 | 0.028523 | 0.028523 | 0 | 0.012474 | 0.0090649 | 0.0011032 | 0.0023061 | N/A | 0 | 2.2865 | N/A | N/A | 1.1831 |  | N/A | 1.1831
ROI-TAN | Circuit | Distribution | 0.73632 |  | HFTD 2 | 0.009482 | 0.0052708 | 0.0042112 | 0.0092392 | 0.0032863 | 0.00066157 | 0.0052913 | N/A | 0.0018385 | 0.57048 | N/A | N/A | 1.158 | 2.2905 | N/A | 1.158
ROMANUS | Circuit | Distribution | 4.2752 |  | HFTD 3 | 0.0041288 | 0.0040043 | 0.00012454 | 0.0022087 | 0.0013055 | 0.00010842 | 0.00079474 | N/A | 0.011899 | 1.813 | N/A | N/A | 1.087 | 0.010467 | N/A | 1.087
ROMERO | Circuit | Distribution | 0.96526 | Top 5% Highest Risk | HFTD Tier 3 | 0.074548 | 0.074519 | 2.9177e-05 | 0.016436 | 0.0072808 | 5.6613e-05 | 0.0090981 | N/A | 0.0064621 | 4.534 | N/A | N/A | 1.0622 | 0.0045151 | N/A | 1.0622
ROS | Circuit | Distribution | 19.1782 |  | HFTD 2 | 0.0063693 | 0.0063637 | 5.5894e-06 | 0.0028859 | 0.0016613 | 7.132e-05 | 0.0011533 | N/A | 0.0099613 | 2.2052 | N/A | N/A | 1.1285 | 0.00056111 | N/A | 1.1285
ROSA | Circuit | Distribution | 3.1549 |  | HFTD 3 | 0.0070325 | 0.0070277 | 4.7637e-06 | 0.014192 | 0.0081604 | 0.00042454 | 0.005607 | N/A | 0 | 0.49519 | N/A | N/A | 1.0887 | inf | N/A | 1.0887
ROSEBUD | Circuit | Distribution | 18.9723 |  | HFTD 3 | 0.0014879 | 0.0014877 | 1.1299e-07 | 0.0075348 | 0.0042912 | 0.0015456 | 0.001698 | N/A | 0.0077165 | 0.19745 | N/A | N/A | 1.2942 | 1.4642e-05 | N/A | 1.2942
ROSEMONT | Circuit | Distribution | 11.2801 |  | HFTD 2 | 0.0090466 | 0.0090241 | 2.2437e-05 | 0.018464 | 0.0095016 | 0.0046947 | 0.0042675 | N/A | 0.024785 | 0.48875 | N/A | N/A | 1.1079 | 0.00090525 | N/A | 1.1079
ROTEC | Circuit | Distribution | 3.4006 | Top 5% Highest Risk | HFTD Tier 2 | 0.056804 | 0.056789 | 1.447e-05 | 0.005236 | 0.0025204 | 0.00014203 | 0.0025736 | N/A | 0.00071642 | 10.8459 | N/A | N/A | 1.0681 | 0.020198 | N/A | 1.0681
ROUNDEL | Circuit | Distribution | 4.8998 |  | HFTD 2 | 0.029837 | 0.029801 | 3.5772e-05 | 0.007408 | 0.0032565 | 0.00014393 | 0.0040075 | N/A | 0.020289 | 4.0228 | N/A | N/A | 1.1329 | 0.0017631 | N/A | 1.1329
ROWCO | Circuit | Distribution | 14.8277 |  | HFTD 3 | 0.014101 | 0.013672 | 0.00042826 | 0.01244 | 0.0081854 | 0.00092048 | 0.0033341 | N/A | 0.24025 | 1.0991 | N/A | N/A | 1.4196 | 0.0017825 | N/A | 1.4196
ROXBURY | Circuit | Distribution | 0.36175 |  | HFTD 2 | 0.00081834 | 0.00081834 | 0 | 0.027682 | 0.0074514 | 0.013221 | 0.0070096 | N/A | 0.00037493 | 0.029562 | N/A | N/A | 1.0988 | 0 | N/A | 1.0988
ROYCE | Circuit | Distribution | 0.38299 |  | HFTD 2 | 0.0011356 | 0.0011356 | 0 | 0.0063506 | 0.00195 | 0.00087844 | 0.0035221 | N/A | 0.0076906 | 0.17881 | N/A | N/A |  | 0 | N/A
RUBIN | Circuit | Distribution | 5.9385 |  | HFTD 3 | 0.011689 | 0.011682 | 6.7382e-06 | 0.0052367 | 0.0019455 | 0.00073404 | 0.0025572 | N/A | 0.0051662 | 2.2308 | N/A | N/A | 1.1607 | 0.0013043 | N/A | 1.1607
RUGGLES | Circuit | Distribution | 0.42817 |  | HFTD 2 | 0.032079 | 0.032072 | 6.7947e-06 | 0.0088108 | 0.005074 | 0.0008759 | 0.0028609 | N/A | 0.0010354 | 3.6401 | N/A | N/A | 1.0113 | 0.0065624 | N/A | 1.0113
RUIZ | Circuit | Distribution | 9.0269 |  | HFTD 2 | 0.010277 | 0.010275 | 2.1018e-06 | 0.005279 | 0.0010019 | 0.00019107 | 0.004086 | N/A | 0.0045318 | 1.9463 | N/A | N/A | 1.0893 | 0.00046378 | N/A | 1.0893
RUSTIC | Circuit | Distribution | 16.3522 |  | HFTD 3 | 0.020526 | 0.020473 | 5.3224e-05 | 0.009453 | 0.0046439 | 0.00099593 | 0.0038132 | N/A | 0.044517 | 2.1657 | N/A | N/A | 1.207 | 0.0011956 | N/A | 1.207
RYE | Circuit | Distribution | 1.4926 |  | HFTD 2 | 0.0022038 | 0.0017887 | 0.00041508 | 0.0063869 | 0.0034204 | 0.00043981 | 0.0025267 | N/A | 0.002403 | 0.28006 | N/A | N/A | 1.1053 | 0.17273 | N/A | 1.1053
SABRINA | Circuit | Distribution | 6.1575 |  | HFTD 2 | 0.01114 | 0.011043 | 9.6523e-05 | 0.0069707 | 0.0023101 | 0.00035926 | 0.0043013 | N/A | 0.10938 | 1.5842 | N/A | N/A | 1.3572 | 0.00088244 | N/A | 1.3572
SADDLEBACK | Circuit | Distribution | 4.4809 |  | HFTD 2 | 0.0061411 | 0.0061411 | 3.7883e-08 | 0.0007921 | 0.0005407 | 1.3501e-05 | 0.0002379 | N/A | 0.020016 | 7.7529 | N/A | N/A | 1.0182 | 1.8927e-06 | N/A | 1.0182
SAGEHEN | Circuit | Distribution | 29.0724 |  | HFTD 2 | 0.0035802 | 0.0035685 | 1.1671e-05 | 0.0027026 | 0.0018746 | 9.3021e-06 | 0.00081869 | N/A | 0.03222 | 1.3204 | N/A | N/A | 1.1423 | 0.00036222 | N/A | 1.1423
SAGINAW | Circuit | Distribution | 8.9163 |  | HFTD 3 | 0.00043801 | 0.00043669 | 1.3162e-06 | 0.0020579 | 0.00030483 | 6.5506e-05 | 0.0016876 | N/A | 0.13303 | 0.2122 | N/A | N/A | 1.4737 | 9.894e-06 | N/A | 1.4737
SAINT JO | Circuit | Distribution | 1.9761 |  | HFTD 2 | 0.0015738 | 0.0015276 | 4.6193e-05 | 0.016469 | 0.0047723 | 0.0028269 | 0.0088696 | N/A | 0.0031222 | 0.092757 | N/A | N/A | 1.0864 | 0.014795 | N/A | 1.0864
SALT CREEK | Circuit | Distribution | 23.3483 |  | HFTD 2 | 0.010041 | 0.01004 | 1.2269e-06 | 0.0074773 | 0.0058193 | 9.5454e-05 | 0.0015625 | N/A | 0.019567 | 1.3427 | N/A | N/A | 1.222 | 6.2702e-05 | N/A | 1.222
SAN NICHOLAS | Circuit | Distribution | 5.6139 |  | HFTD 3 | 0.0033697 | 0.0033321 | 3.7616e-05 | 0.018616 | 0.0082581 | 0.00028176 | 0.010076 | N/A | 0.011814 | 0.17899 | N/A | N/A | 1.0912 | 0.0031839 | N/A | 1.0912
SANCHO | Circuit | Distribution | 1.4453 |  | HFTD 2 | 0.0037956 | 0.0037953 | 3.1705e-07 | 0.0057411 | 0.0018065 | 2.4814e-05 | 0.0039098 | N/A | 0.017389 | 0.66107 | N/A | N/A | 1 | 1.8232e-05 | N/A | 1
SAND CANYON | Circuit | Distribution | 18.5796 |  | HFTD 3 | 0.02334 | 0.023282 | 5.8065e-05 | 0.0071554 | 0.0044969 | 0.00025105 | 0.0024074 | N/A | 0.054912 | 3.2538 | N/A | N/A | 1.1495 | 0.0010574 | N/A | 1.1495
SANTORINI | Circuit | Distribution | 2.6436 |  | HFTD 2 | 0.035533 | 0.035475 | 5.8762e-05 | 0.010797 | 0.0070664 | 0.00035305 | 0.0033779 | N/A | 0.0066995 | 3.2855 | N/A | N/A | 1.3539 | 0.0087711 | N/A | 1.3539
SAUNDERS | Circuit | Distribution | 33.4037 |  | HFTD 3 | 0.012068 | 0.012066 | 1.8146e-06 | 0.0035133 | 0.0027554 | 0.00019418 | 0.00056377 | N/A | 0.039456 | 3.4344 | N/A | N/A | 1.1338 | 4.5991e-05 | N/A | 1.1338
SAUTERNE | Circuit | Distribution | 0.39186 |  | HFTD 2 | 0.0081591 | 0.0059902 | 0.0021689 | 0.010562 | 0.0068381 | 0.00041264 | 0.0033115 | N/A | 0 | 0.56713 | N/A | N/A | 1.1213 | inf | N/A | 1.1213
SAVORY | Circuit | Distribution | 7.9307 |  | HFTD 2 | 0.010773 | 0.01076 | 1.3131e-05 | 0.0035565 | 0.0014371 | 4.1283e-05 | 0.0020781 | N/A | 0.0054872 | 3.0253 | N/A | N/A | 1.2016 | 0.0023931 | N/A | 1.2016
SAWPIT | Circuit | Distribution | 4.4061 |  | HFTD 3 | 0.0028152 | 0.0028152 | 0 | 0.0020492 | 0.0017131 | 7.6646e-05 | 0.00025944 | N/A | 0.047628 | 1.3738 | N/A | N/A |  | 0 | N/A
SCALP | Circuit | Distribution | 0.68046 |  | HFTD 2 | 0.036432 | 0.036414 | 1.8771e-05 | 0.0074586 | 0.0012263 | 0.0004631 | 0.0057692 | N/A | 0.0016983 | 4.8821 | N/A | N/A | 1.5856 | 0.011053 | N/A | 1.5856
SCHMIDT | Circuit | Distribution | 15.5471 | Top 5% Highest Risk | HFTD Tier 2 | 0.068757 | 0.068748 | 9.5903e-06 | 0.0095956 | 0.0059488 | 0.00027689 | 0.0033699 | N/A | 0.017453 | 7.1645 | N/A | N/A | 1.114 | 0.00054949 | N/A | 1.114
SCIURBA | Circuit | Distribution | 10.7235 |  | HFTD 2 | 0.0010467 | 0.0010467 | 0 | 0.0069868 | 0.0017716 | 0.00043417 | 0.004781 | N/A | 0 | 0.14982 | N/A | N/A | 1.0953 |  | N/A | 1.0953
SDGE 520 | Circuit | Distribution | 2.0892 |  | HFTD 3 | 0.013789 | 0.013789 | 2.0304e-07 | 0.0039339 | 0.0018416 | 0.00013352 | 0.0019588 | N/A | 0.0026112 | 3.5052 | N/A | N/A | 1.0094 | 7.7755e-05 | N/A | 1.0094
SDGE 521 | Circuit | Distribution | 2.8653 |  | HFTD 3 | 0.0031777 | 0.0031777 | 4.5689e-08 | 0.001029 | 0.00026446 | 1.7489e-05 | 0.00074709 | N/A | 0.0010594 | 3.088 | N/A | N/A | 1.6376 | 4.3127e-05 | N/A | 1.6376
SEACLIFF | Circuit | Distribution | 33.9304 |  | HFTD 2 | 0.0049827 | 0.0049813 | 1.3661e-06 | 0.010232 | 0.0048984 | 0.0016366 | 0.0036971 | N/A | 0.0083826 | 0.48683 | N/A | N/A | 1.1305 | 0.00016297 | N/A | 1.1305
SEAFORTH | Circuit | Distribution | 3.65 |  | HFTD 2 | 0.034617 | 0.03432 | 0.00029626 | 0.013439 | 0.0038966 | 2.8663e-05 | 0.0095138 | N/A | 0.00087049 | 2.5538 | N/A | N/A | 1.2317 | 0.34033 | N/A | 1.2317
SEAWOLF | Circuit | Distribution | 1.0917 |  | HFTD 2 | 0.017311 | 0.017307 | 4.2506e-06 | 0.0078562 | 0.0025509 | 0.00036466 | 0.0049406 | N/A | 0.00047263 | 2.2029 | N/A | N/A | 1.1073 | 0.0089936 | N/A | 1.1073
SEBASTIAN | Circuit | Distribution | 0.96162 |  | HFTD 2 | 0.0030395 | 0.0029233 | 0.00011625 | 0.0065945 | 0.0039231 | 0.000196 | 0.0024754 | N/A | 0.0025123 | 0.44328 | N/A | N/A | 1.3059 | 0.046272 | N/A | 1.3059
SECO | Circuit | Distribution | 0.80874 |  | HFTD 2 | 0.0090586 | 0.0089077 | 0.00015092 | 0.015279 | 0.0077757 | 0.0020864 | 0.0054167 | N/A | 0.0022272 | 0.58301 | N/A | N/A | 1.1238 | 0.06776 | N/A | 1.1238
SEELEY | Circuit | Distribution | 5.2796 |  | HFTD 3 | 0.026273 | 0.026223 | 5.0015e-05 | 0.023104 | 0.014833 | 0.0057641 | 0.0025072 | N/A | 0.050372 | 1.135 | N/A | N/A | 1.2326 | 0.00099292 | N/A | 1.2326
SEMINARY | Circuit | Distribution | 4.6358 |  | HFTD 2 | 0.0061942 | 0.0061676 | 2.6581e-05 | 0.009214 | 0.0048698 | 0.0015033 | 0.0028409 | N/A | 0.0041487 | 0.66938 | N/A | N/A | 1.0848 | 0.006407 | N/A | 1.0848
SERNA | Circuit | Distribution | 0.3381 |  | HFTD 3 | 0.013529 | 0.013444 | 8.4644e-05 | 0.008124 | 0.00095849 | 0.00015802 | 0.0070075 | N/A | 0.00070522 | 1.6549 | N/A | N/A | 1.04 | 0.12002 | N/A | 1.04
SERRA | Circuit | Distribution | 15.2675 |  | HFTD 3 | 0.01011 | 0.010107 | 2.5536e-06 | 0.0071724 | 0.0040168 | 0.00047659 | 0.0026789 | N/A | 0.018887 | 1.4092 | N/A | N/A | 1.2687 | 0.0001352 | N/A | 1.2687
SESPE | Circuit | Distribution | 0.33041 |  | HFTD 3 | 8.6396e-05 | 8.3042e-05 | 3.354e-06 | 0.01433 | 0.008248 | 0.0014589 | 0.0046227 | N/A | 0.00091335 | 0.0057952 | N/A | N/A | 1.0088 | 0.0036722 | N/A | 1.0088
SEXTON | Circuit | Distribution | 10.5097 |  | HFTD 3 | 0.014191 | 0.014149 | 4.1791e-05 | 0.013124 | 0.0088636 | 0.0010247 | 0.0032356 | N/A | 0.013059 | 1.0781 | N/A | N/A | 1.1285 | 0.0032001 | N/A | 1.1285
SEYMOUR | Circuit | Distribution | 10.8214 |  | HFTD 3 | 0.00066609 | 0.00066599 | 1.0501e-07 | 0.0026177 | 0.001831 | 0.00015742 | 0.00062931 | N/A | 0.029428 | 0.25442 | N/A | N/A | 1 | 3.5682e-06 | N/A | 1
SHAKE | Circuit | Distribution | 5.7243 |  | HFTD 3 | 0.0048831 | 0.0048831 | 0 | 0.0020129 | 0.0014066 | 0.00022013 | 0.00038619 | N/A | 0.11236 | 2.4259 | N/A | N/A |  | 0 | N/A
SHAMROCK | Circuit | Distribution | 0.82267 |  | HFTD 3 | 0.0021121 | 0.0020807 | 3.1373e-05 | 0.011855 | 0.0062716 | 0.0012979 | 0.0042851 | N/A | 0.0094529 | 0.17552 | N/A | N/A | 1.0093 | 0.0033189 | N/A | 1.0093
SHASTA | Circuit | Distribution | 7.2807 |  | HFTD 2 | 0.024508 | 0.024504 | 3.272e-06 | 0.0089738 | 0.0034165 | 0.00064683 | 0.0049105 | N/A | 0.0051741 | 2.7307 | N/A | N/A | 1.1591 | 0.00063238 | N/A | 1.1591
SHEFFIELD | Circuit | Distribution | 26.9054 |  | HFTD 3 | 0.018849 | 0.018841 | 7.6775e-06 | 0.014818 | 0.0083252 | 0.00091612 | 0.0055769 | N/A | 0.031196 | 1.2715 | N/A | N/A | 1.1241 | 0.00024611 | N/A | 1.1241
SHERBOURNE | Circuit | Distribution | 4.0792 |  | HFTD 2 | 0.0021065 | 0.0021065 | 0 | 0.0056503 | 0.0018374 | 0.0010552 | 0.0027577 | N/A | 0 | 0.37282 | N/A | N/A | 1.1303 |  | N/A | 1.1303
SHETLAND | Circuit | Distribution | 1.0442 |  | HFTD 2 | 0.019311 | 0.019311 | 0 | 0.0054539 | 0.0023438 | 0.00012362 | 0.0029865 | N/A | 0 | 3.5407 | N/A | N/A | 1.0975 |  | N/A | 1.0975
SHINE | Circuit | Distribution | 1.3163 |  | HFTD 2 | 0.0053355 | 0.0036528 | 0.0016827 | 0.0044381 | 0.0011975 | 8.0933e-05 | 0.0031597 | N/A | 0.0048432 | 0.82306 | N/A | N/A | 1.1218 | 0.34743 | N/A | 1.1218
SHIRAZ | Circuit | Distribution | 3.4912 |  | HFTD 2 | 0.0015099 | 0.0010393 | 0.00047065 | 0.003006 | 0.0012011 | 0.00021739 | 0.0015875 | N/A | 0.0026026 | 0.34574 | N/A | N/A | 1.1482 | 0.18084 | N/A | 1.1482
SHOPPER | Circuit | Distribution | 2.14 |  | HFTD 2 | 0.00041399 | 0.00041293 | 1.0602e-06 | 0.003235 | 0.0020317 | 0.00020861 | 0.00099469 | N/A | 0.00042013 | 0.12765 | N/A | N/A | 1.0661 | 0.0025235 | N/A | 1.0661
SHOPPING | Circuit | Distribution | 0.28326 |  | HFTD 3 | 0.0014308 | 0.00094865 | 0.00048215 | 0.031529 | 0.0098084 | 0.0011372 | 0.020583 | N/A | 0.0078417 | 0.030088 | N/A | N/A | 1.0585 | 0.061485 | N/A | 1.0585
SHORELINE | Circuit | Distribution | 11.0099 |  | HFTD 2 | 0.0099319 | 0.0099319 | 0 | 0.010933 | 0.0049966 | 0.0031538 | 0.002783 | N/A | 0 | 0.90841 | N/A | N/A | 1.334 |  | N/A | 1.334
SHOVEL | Circuit | Distribution | 40.3449 | Top 5% Highest Risk | HFTD Tier 3 | 0.091808 | 0.091808 | 0 | 0.008222 | 0.0045248 | 0.0001419 | 0.0035553 | N/A | 0.1042 | 11.1662 | N/A | N/A | 1.1263 | 0 | N/A | 1.1263
SHOWDOWN | Circuit | Distribution | 3.9317 |  | HFTD 3 | 0.025157 | 0.025062 | 9.4488e-05 | 0.0056681 | 0.0025706 | 2.4074e-05 | 0.0030735 | N/A | 0.018956 | 4.4216 | N/A | N/A | 1.3722 | 0.0049847 | N/A | 1.3722
SIAM | Circuit | Distribution | 1.1961 |  | HFTD 2 | 0.028477 | 0.028365 | 0.00011174 | 0.015455 | 0.0059681 | 0.0074911 | 0.0019958 | N/A | 0.0099193 | 1.8354 | N/A | N/A | 1.0942 | 0.011265 | N/A | 1.0942
SIENNA | Circuit | Distribution | 5.5976 |  | HFTD 3 | 0.0081699 | 0.0081403 | 2.9668e-05 | 0.014193 | 0.006792 | 0.00078446 | 0.0066164 | N/A | 0.013484 | 0.57355 | N/A | N/A | 1.1473 | 0.0022002 | N/A | 1.1473
SILICONE | Circuit | Distribution | 7.8508 |  | HFTD 2 | 0.0075935 | 0.0075935 | 0 | 0.012426 | 0.0049973 | 0.0027178 | 0.0047106 | N/A | 0.0011447 | 0.61111 | N/A | N/A | 1.1565 | 0 | N/A | 1.1565
SILVA | Circuit | Distribution | 0.44599 | Top 5% Highest Risk | HFTD Tier 2 | 0.046797 | 0.044198 | 0.0025993 | 0.013521 | 0.0018842 | 0.00050857 | 0.011129 | N/A | 0.020395 | 3.2688 | N/A | N/A | 1.0841 | 0.12745 | N/A | 1.0841
SIMS | Circuit | Distribution | 1.4834 |  | HFTD 2 | 0.01977 | 0.01957 | 0.0001999 | 0.0058743 | 0.0023069 | 4.4398e-05 | 0.0035231 | N/A | 0.0010262 | 3.3314 | N/A | N/A | 1.1816 | 0.1948 | N/A | 1.1816
SINALOA | Circuit | Distribution | 4.1644 |  | HFTD 3 | 0.0019907 | 0.0018893 | 0.00010135 | 0.015811 | 0.01206 | 0.00054893 | 0.0032016 | N/A | 0.0025964 | 0.11949 | N/A | N/A | 1.1843 | 0.039034 | N/A | 1.1843
SINKER | Circuit | Distribution | 1.2985 |  | HFTD 2 | 0.0022144 | 0.0022116 | 2.7662e-06 | 0.0020051 | 0.00083813 | 0.00019459 | 0.00097235 | N/A | 0.05083 | 1.103 | N/A | N/A | 1.4101 | 5.442e-05 | N/A | 1.4101
SITZMARK | Circuit | Distribution | 2.4331 |  | HFTD 2 | 0.0038979 | 0.001968 | 0.0019298 | 0.019822 | 0.0081272 | 0.0010285 | 0.010666 | N/A | 0.036345 | 0.099288 | N/A | N/A | 1.0908 | 0.053097 | N/A | 1.0908
SKI | Circuit | Distribution | 6.7326 |  | HFTD 2 | 0.0029381 | 0.0029381 | 0 | 0.0047582 | 0.0017208 | 0.00033984 | 0.0026976 | N/A | 0.021402 | 0.61749 | N/A | N/A |  | 0 | N/A
SKINKLE | Circuit | Distribution | 8.6388 |  | HFTD 2 | 0.00083065 | 0.00082727 | 3.3756e-06 | 0.0029566 | 0.001566 | 6.2812e-05 | 0.0013277 | N/A | 0.0013472 | 0.27981 | N/A | N/A | 1.0724 | 0.0025056 | N/A | 1.0724
SKINNER | Circuit | Distribution | 7.5398 |  | HFTD 2 | 0.0043024 | 0.0043024 | 3.095e-09 | 0.0013043 | 0.0007018 | 4.0701e-05 | 0.00056184 | N/A | 0.0067481 | 3.2985 | N/A | N/A | 2 | 4.5865e-07 | N/A | 2
SKY HI | Circuit | Distribution | 7.5173 |  | HFTD 2 | 0.010985 | 0.010601 | 0.00038407 | 0.0042405 | 0.0037625 | 3.7687e-05 | 0.00044033 | N/A | 0.010991 | 2.4999 | N/A | N/A | 1.2042 | 0.034944 | N/A | 1.2042
SKYBORNE | Circuit | Distribution | 2.872 |  | HFTD 2 | 0.0024324 | 0.0020673 | 0.00036514 | 0.0028466 | 0.0023611 | 2.5411e-05 | 0.0004601 | N/A | 0.023237 | 0.72621 | N/A | N/A | 1.1837 | 0.015714 | N/A | 1.1837
SKYLAND | Circuit | Distribution | 6.139 |  | HFTD 3 | 0.016826 | 0.01676 | 6.5272e-05 | 0.017917 | 0.014874 | 0.0012715 | 0.0017724 | N/A | 0.05044 | 0.93543 | N/A | N/A | 1.1578 | 0.0012941 | N/A | 1.1578
SLALOM | Circuit | Distribution | 0.96546 |  | HFTD 2 | 0.0070924 | 0.0019524 | 0.00514 | 0.034772 | 0.011318 | 0.0018722 | 0.021582 | N/A | 0.040629 | 0.056148 | N/A | N/A | 1.0087 | 0.12651 | N/A | 1.0087
SLOPE | Circuit | Distribution | 1.8883 |  | HFTD 2 | 0.030407 | 0.027885 | 0.0025213 | 0.01153 | 0.0050146 | 0.0016461 | 0.0048693 | N/A | 0.050317 | 2.4185 | N/A | N/A | 1.0323 | 0.050109 | N/A | 1.0323
SNO CAT | Circuit | Distribution | 1.8084 |  | HFTD 3 | 0.00034091 | 0.00034091 | 4.7869e-09 | 0.0075264 | 0.0029764 | 0.00059827 | 0.0039518 | N/A | 0.0047069 | 0.045295 | N/A | N/A | 1.6316 | 1.017e-06 | N/A | 1.6316
SNOW VALLEY | Circuit | Distribution | 16.7512 |  | HFTD 3 | 0.0039866 | 0.0039643 | 2.2289e-05 | 0.012563 | 0.0098019 | 0.00073979 | 0.0020208 | N/A | 0.072981 | 0.31556 | N/A | N/A | 1.1856 | 0.0003054 | N/A | 1.1856
SNOWCREEK | Circuit | Distribution | 1.4746 |  | HFTD 2 | 0.034131 | 0.033965 | 0.00016634 | 0.0070763 | 0.0043998 | 9.8505e-05 | 0.002578 | N/A | 0.061536 | 4.7998 | N/A | N/A | 1.5202 | 0.0027032 | N/A | 1.5202
SNOWDRIFT | Circuit | Distribution | 1.8195 |  | HFTD 2 | 0.009752 | 0.0091008 | 0.0006512 | 0.0067062 | 0.0015317 | 0.00079785 | 0.0043767 | N/A | 0.018727 | 1.3571 | N/A | N/A | 1.0333 | 0.034773 | N/A | 1.0333
SOCRATES | Circuit | Distribution | 3.2226 |  | HFTD 3 | 0.0138 | 0.0138 | 0 | 0.015941 | 0.0058966 | 0.0012253 | 0.0088193 | N/A | 0 | 0.86567 | N/A | N/A | 1.1064 |  | N/A | 1.1064
SODA SPRINGS | Circuit | Distribution | 81.303 |  | HFTD 2 | 0.00090767 | 0.00090766 | 1.6577e-08 | 0.0023439 | 0.0018835 | 0.0001758 | 0.00028456 | N/A | 0.012018 | 0.38725 | N/A | N/A | 1.1537 | 1.3793e-06 | N/A | 1.1537
SOGGY | Circuit | Distribution | 7.4566 |  | HFTD 2 | 0.013473 | 0.013466 | 7.4848e-06 | 0.0059222 | 0.0049013 | 3.6777e-05 | 0.0009841 | N/A | 0.002484 | 2.2738 | N/A | N/A | 1.1926 | 0.0030132 | N/A | 1.1926
SONOMA | Circuit | Distribution | 30.6315 |  | HFTD 2 | 0.030829 | 0.030827 | 1.9617e-06 | 0.0052949 | 0.0037333 | 0.00017677 | 0.0013849 | N/A | 0.0038953 | 5.8221 | N/A | N/A | 1.1984 | 0.00050361 | N/A | 1.1984
SOPHIE | Circuit | Distribution | 22.1385 |  | HFTD 3 | 0.013462 | 0.013461 | 6.3204e-07 | 0.0023447 | 0.0017942 | 3.3598e-05 | 0.0005169 | N/A | 0.0046871 | 5.7412 | N/A | N/A | 1.1642 | 0.00013485 | N/A | 1.1642
SORRENTO | Circuit | Distribution | 0.40982 |  | HFTD 2 | 0.00079978 | 0.00064749 | 0.00015229 | 0.014811 | 0.005917 | 0.0020463 | 0.0068475 | N/A | 0.014101 | 0.043717 | N/A | N/A | 1.0387 | 0.0108 | N/A | 1.0387
SOUTHRIDGE | Circuit | Distribution | 0.4115 |  | HFTD 2 | 0.006654 | 0.0065626 | 9.1395e-05 | 0.045781 | 0.02397 | 0.016597 | 0.0052143 | N/A | 0.0034541 | 0.14335 | N/A | N/A | 1.0894 | 0.02646 | N/A | 1.0894
SPANADA | Circuit | Distribution | 4.558 |  | HFTD 3 | 0.024195 | 0.02419 | 5.4133e-06 | 0.016717 | 0.0067438 | 0.00039203 | 0.0095808 | N/A | 0.0047145 | 1.4471 | N/A | N/A | 1.4964 | 0.0011482 | N/A | 1.4964
SPARKS | Circuit | Distribution | 0.52647 |  | HFTD 2 | 0.0042165 | 0.0041492 | 6.738e-05 | 0.011823 | 0.0022074 | 0.00083995 | 0.0087754 | N/A | 0.00043765 | 0.35095 | N/A | N/A | 1.0889 | 0.15396 | N/A | 1.0889
SPARLING | Circuit | Distribution | 4.6257 |  | HFTD 2 | 0.013962 | 0.01396 | 1.4936e-06 | 0.0085351 | 0.0038163 | 0.00095841 | 0.0037604 | N/A | 0.0015046 | 1.6356 | N/A | N/A | 1.1087 | 0.00099267 | N/A | 1.1087
SPICE | Circuit | Distribution | 4.1257 |  | HFTD 2 | 0.015411 | 0.015404 | 6.4376e-06 | 0.0053914 | 0.0010568 | 0.00017052 | 0.0041641 | N/A | 0.0082125 | 2.8572 | N/A | N/A | 1.1344 | 0.00078387 | N/A | 1.1344
SPIKE | Circuit | Distribution | 0.81153 |  | HFTD 2 | 0.035522 | 0.034586 | 0.00093665 | 0.017286 | 0.0049062 | 0.00089158 | 0.011488 | N/A | 0.0022105 | 2.0008 | N/A | N/A | 1.1452 | 0.42373 | N/A | 1.1452
SPINKS | Circuit | Distribution | 1.4019 |  | HFTD 2 | 0.0077507 | 0.0077391 | 1.1618e-05 | 0.017804 | 0.0085839 | 0.0025631 | 0.006657 | N/A | 0.0057034 | 0.43469 | N/A | N/A | 1.0924 | 0.002037 | N/A | 1.0924
SPLENDOR | Circuit | Distribution | 0.97389 |  | HFTD 3 | 0.001238 | 0.00062205 | 0.00061596 | 0.020994 | 0.0086326 | 0.00064813 | 0.011713 | N/A | 0.02425 | 0.02963 | N/A | N/A | 1.0355 | 0.025401 | N/A | 1.0355
SPRAGUE | Circuit | Distribution | 23.7144 |  | HFTD 3 | 0.00511 | 0.0051074 | 2.6483e-06 | 0.010601 | 0.0074013 | 0.0007433 | 0.0024559 | N/A | 0.0067709 | 0.4818 | N/A | N/A | 1.2064 | 0.00039113 | N/A | 1.2064
SQUINT | Circuit | Distribution | 10.1507 |  | HFTD 3 | 0.0159 | 0.015883 | 1.6909e-05 | 0.012016 | 0.0084383 | 0.00060527 | 0.002972 | N/A | 0.032569 | 1.3219 | N/A | N/A | 1.4358 | 0.00051917 | N/A | 1.4358
STACK | Circuit | Distribution | 0.91561 |  | HFTD 2 | 0.0011766 | 0.00064328 | 0.00053331 | 0.012835 | 0.0026697 | 0.0016223 | 0.0085425 | N/A | 0.0023631 | 0.050121 | N/A | N/A | 1.0181 | 0.22569 | N/A | 1.0181
STAGELINE | Circuit | Distribution | 6.4567 |  | HFTD 3 | 0.0083032 | 0.0082966 | 6.5856e-06 | 0.0094458 | 0.0045455 | 0.00015806 | 0.0047422 | N/A | 0.003844 | 0.87834 | N/A | N/A | 1.1898 | 0.0017132 | N/A | 1.1898
STAGHORN | Circuit | Distribution | 2.0276 |  | HFTD 2 | 0.0069113 | 0.0067614 | 0.00014988 | 0.016524 | 0.007816 | 0.00022466 | 0.0084829 | N/A | 0.0024587 | 0.4092 | N/A | N/A | 1.1159 | 0.060961 | N/A | 1.1159
STANFORD | Circuit | Distribution | 0.52014 |  | HFTD 2 | 0.0042707 | 0.004141 | 0.00012967 | 0.0066076 | 0.0027214 | 0.00052354 | 0.0033626 | N/A | 0.00061602 | 0.62671 | N/A | N/A | 1.1615 | 0.21049 | N/A | 1.1615
STANWOOD | Circuit | Distribution | 28.8063 |  | HFTD 3 | 0.030365 | 0.030356 | 9.4374e-06 | 0.0075455 | 0.0046297 | 0.0014038 | 0.0015121 | N/A | 0.049073 | 4.023 | N/A | N/A | 1.1216 | 0.00019231 | N/A | 1.1216
STAR ROCK | Circuit | Distribution | 2.2097 |  | HFTD 3 | 0.02573 | 0.025688 | 4.191e-05 | 0.0087104 | 0.0035429 | 0.00029973 | 0.0048678 | N/A | 0.020728 | 2.9492 | N/A | N/A | 1.0993 | 0.0020219 | N/A | 1.0993
STARGLOW | Circuit | Distribution | 31.852 |  | HFTD 2 | 0.017909 | 0.017906 | 3.0279e-06 | 0.0020076 | 0.0014921 | 3.5295e-05 | 0.00048022 | N/A | 0.0074942 | 8.9192 | N/A | N/A | 1.2217 | 0.00040403 | N/A | 1.2217
STATLER | Circuit | Distribution | 22.5499 |  | HFTD 2 | 0.0081928 | 0.0081917 | 1.0671e-06 | 0.0099232 | 0.0050641 | 0.0016402 | 0.0032189 | N/A | 0.001266 | 0.82551 | N/A | N/A | 1.3292 | 0.00084291 | N/A | 1.3292
STEARNS | Circuit | Distribution | 6.7032 |  | HFTD 3 | 0.00091935 | 0.0007233 | 0.00019605 | 0.019863 | 0.013454 | 0.0015183 | 0.0048901 | N/A | 0.038781 | 0.036415 | N/A | N/A | 1.098 | 0.0050553 | N/A | 1.098
STEEL | Circuit | Distribution | 9.2604 |  | HFTD 2 | 0.0015514 | 0.0015509 | 4.4251e-07 | 0.0036844 | 0.0016119 | 6.7185e-05 | 0.0020053 | N/A | 0.01482 | 0.42094 | N/A | N/A | 1.2774 | 2.9859e-05 | N/A | 1.2774
STEVENSON | Circuit | Distribution | 12.6987 |  | HFTD 2 | 0.00062851 | 0.00062832 | 1.873e-07 | 0.0047878 | 0.0015713 | 0.00055847 | 0.0026579 | N/A | 0.012833 | 0.13124 | N/A | N/A | 1.4641 | 1.4595e-05 | N/A | 1.4641
STOCKER | Circuit | Distribution | 1.5066 |  | HFTD 2 | 0.00022156 | 0.00022156 | 0 | 0.0093318 | 0.0024635 | 0.0018544 | 0.0050139 | N/A | 0 | 0.023743 | N/A | N/A | 1.1277 |  | N/A | 1.1277
STONEMAN | Circuit | Distribution | 25.329 | Top 5% Highest Risk | HFTD Tier 3 | 0.045793 | 0.045793 | 7.7419e-07 | 0.01525 | 0.0099625 | 0.00085345 | 0.0044341 | N/A | 0.0038033 | 3.0028 | N/A | N/A | 1.2094 | 0.00020356 | N/A | 1.2094
STONEWOOD | Circuit | Distribution | 5.1204 |  | HFTD 3 | 0.014693 | 0.014681 | 1.2028e-05 | 0.0061948 | 0.0030674 | 0.00039479 | 0.0027326 | N/A | 0.0080135 | 2.3699 | N/A | N/A | 1.0848 | 0.001501 | N/A | 1.0848
STORES | Circuit | Distribution | 20.129 | Top 5% Highest Risk | HFTD Tier 3 | 0.090221 | 0.090219 | 2.3797e-06 | 0.0084898 | 0.0047291 | 0.00027852 | 0.0034821 | N/A | 0.047175 | 10.6267 | N/A | N/A | 1.0687 | 5.0445e-05 | N/A | 1.0687
STRATHERN | Circuit | Distribution | 7.4581 |  | HFTD 3 | 0.0042686 | 0.0041686 | 9.9991e-05 | 0.017552 | 0.0089196 | 0.0010567 | 0.0075758 | N/A | 0.026246 | 0.2375 | N/A | N/A | 1.1173 | 0.0038097 | N/A | 1.1173
STRIPER | Circuit | Distribution | 1.0308 |  | HFTD 2 | 0.012283 | 0.012283 | 0 | 0.0019611 | 0.001182 | 2.7063e-05 | 0.00075209 | N/A | 0 | 6.2631 | N/A | N/A | 2 |  | N/A | 2
STROH | Circuit | Distribution | 0.85272 |  | HFTD 2 | 0.0094409 | 0.00943 | 1.0918e-05 | 0.011676 | 0.0084699 | 0.00075254 | 0.0024532 | N/A | 0.0014119 | 0.80767 | N/A | N/A | 1.0318 | 0.0077325 | N/A | 1.0318
STROSNIDER | Circuit | Distribution | 12.4528 |  | HFTD 2 | 0.012708 | 0.012692 | 1.6286e-05 | 0.0081404 | 0.0041477 | 0.00010172 | 0.003891 | N/A | 0.066306 | 1.5591 | N/A | N/A | 1.1393 | 0.00024561 | N/A | 1.1393
STUBBY | Circuit | Distribution | 13.3235 |  | HFTD 3 | 0.014419 | 0.014419 | 2.8386e-08 | 0.0047105 | 0.0023456 | 6.0637e-05 | 0.0023042 | N/A | 0.03633 | 3.0611 | N/A | N/A | 1.375 | 7.8134e-07 | N/A | 1.375
STUTZ | Circuit | Distribution | 7.7144 |  | HFTD 2 | 0.001766 | 0.001766 | 0 | 0.012047 | 0.0041031 | 0.00035198 | 0.0075916 | N/A | 0 | 0.1466 | N/A | N/A | 1.0608 |  | N/A | 1.0608
SUBIDA | Circuit | Distribution | 1.009 |  | HFTD 2 | 0.041333 | 0.040948 | 0.00038578 | 0.012032 | 0.002181 | 3.4939e-05 | 0.0098159 | N/A | 0.0033433 | 3.4033 | N/A | N/A | 1.1055 | 0.11539 | N/A | 1.1055
SUCCESS | Circuit | Distribution | 33.2136 |  | HFTD 2 | 0.0044856 | 0.0044836 | 2.0015e-06 | 0.0049081 | 0.0025329 | 9.9055e-05 | 0.0022762 | N/A | 0.00085361 | 0.91351 | N/A | N/A | 1.184 | 0.0023447 | N/A | 1.184
SUGARLOAF | Circuit | Distribution | 4.4702 |  | HFTD 2 | 0.0011452 | 0.001144 | 1.1763e-06 | 0.016304 | 0.0099236 | 0.0049029 | 0.001477 | N/A | 0.018589 | 0.070172 | N/A | N/A | 1.505 | 6.3282e-05 | N/A | 1.505
SUNDANCE | Circuit | Distribution | 6.9104 |  | HFTD 2 | 0.0048085 | 0.0048077 | 8.0579e-07 | 0.004343 | 0.0019058 | 0.00032359 | 0.0021136 | N/A | 0.004103 | 1.107 | N/A | N/A | 1.0941 | 0.00019639 | N/A | 1.0941
SURREY | Circuit | Distribution | 2.5236 |  | HFTD 2 | 0.017875 | 0.017875 | 0 | 0.014462 | 0.0082856 | 0.0026557 | 0.0035211 | N/A | 0 | 1.236 | N/A | N/A | 1.0034 |  | N/A | 1.0034
SUSAN | Circuit | Distribution | 1.536 |  | HFTD 2 | 0.0014169 | 0.00091249 | 0.00050444 | 0.021746 | 0.0095913 | 0.00011762 | 0.012038 | N/A | 0.010108 | 0.04196 | N/A | N/A | 1.3267 | 0.049906 | N/A | 1.3267
SUTT | Circuit | Distribution | 16.3224 |  | HFTD 3 | 0.0064897 | 0.006338 | 0.00015168 | 0.011806 | 0.0077073 | 0.0011278 | 0.0029712 | N/A | 0.052054 | 0.53683 | N/A | N/A | 1.1413 | 0.002914 | N/A | 1.1413
SWEETWATER | Circuit | Distribution | 1.98 |  | HFTD 2 | 0.0034078 | 0.0023786 | 0.0010292 | 0.0027783 | 0.0019894 | 0.00024698 | 0.00054198 | N/A | 0.025163 | 0.85613 | N/A | N/A | 1.0495 | 0.0409 | N/A | 1.0495
SWIFT | Circuit | Distribution | 2.6809 |  | HFTD 3 | 0.017856 | 0.017848 | 8.4623e-06 | 0.0268 | 0.015912 | 0.0030843 | 0.0078038 | N/A | 0.029182 | 0.66597 | N/A | N/A | 1.0457 | 0.00028999 | N/A | 1.0457
TACKLE | Circuit | Distribution | 1.3372 |  | HFTD 3 | 0.0053541 | 0.0053526 | 1.5496e-06 | 0.0043447 | 0.0026556 | 5.7384e-05 | 0.0016317 | N/A | 0 | 1.232 | N/A | N/A | 1.0739 | inf | N/A | 1.0739
TAGGERT | Circuit | Distribution | 10.5543 |  | HFTD 3 | 0.0026296 | 0.0026118 | 1.7787e-05 | 0.0096335 | 0.0058127 | 0.0005944 | 0.0032264 | N/A | 0.038831 | 0.27111 | N/A | N/A | 1.278 | 0.00045806 | N/A | 1.278
TAHQUITZ | Circuit | Distribution | 9.5767 |  | HFTD 3 | 0.0050398 | 0.0050386 | 1.1756e-06 | 0.0059093 | 0.0029614 | 0.00044373 | 0.0025042 | N/A | 0.020894 | 0.85266 | N/A | N/A | 1.1422 | 5.6267e-05 | N/A | 1.1422
TAIWAN | Circuit | Distribution | 11.2323 |  | HFTD 3 | 0.014939 | 0.014923 | 1.6445e-05 | 0.0033356 | 0.00094893 | 0.00017525 | 0.0022114 | N/A | 0.038 | 4.4739 | N/A | N/A | 1.3453 | 0.00043277 | N/A | 1.3453
TALLEY | Circuit | Distribution | 3.3913 |  | HFTD 3 | 0.00096135 | 0.00085558 | 0.00010577 | 0.020865 | 0.0063768 | 0.0039979 | 0.010491 | N/A | 0.016781 | 0.041005 | N/A | N/A | 1.1121 | 0.0063031 | N/A | 1.1121
TAMBOURINE | Circuit | Distribution | 0.63496 |  | HFTD 3 | 0.023583 | 0.023093 | 0.0004898 | 0.022393 | 0.011603 | 0.00017994 | 0.01061 | N/A | 0.022205 | 1.0313 | N/A | N/A | 1.1133 | 0.022059 | N/A | 1.1133
TANAGER | Circuit | Distribution | 54.4035 |  | HFTD 3 | 0.0060159 | 0.0060155 | 4.3622e-07 | 0.0007698 | 0.00071319 | 8.4299e-06 | 4.8174e-05 | N/A | 0.023805 | 7.8144 | N/A | N/A | 1.2721 | 1.8325e-05 | N/A | 1.2721
TANDEM | Circuit | Distribution | 10.7395 |  | HFTD 2 | 0.004142 | 0.004142 | 0 | 0.010003 | 0.0042362 | 0.0020738 | 0.0036928 | N/A | 0 | 0.41408 | N/A | N/A | 1.1671 |  | N/A | 1.1671
TAPO | Circuit | Distribution | 12.0037 |  | HFTD 3 | 0.0068614 | 0.006807 | 5.4418e-05 | 0.0080926 | 0.0051065 | 0.00039308 | 0.0025931 | N/A | 0.030901 | 0.84114 | N/A | N/A | 1.1025 | 0.0017611 | N/A | 1.1025
TATANKA | Circuit | Distribution | 3.3618 |  | HFTD 3 | 0.040595 | 0.040585 | 9.3988e-06 | 0.023869 | 0.015185 | 0.0049184 | 0.0037658 | N/A | 0.013231 | 1.7003 | N/A | N/A | 1.0559 | 0.00071038 | N/A | 1.0559
TAVA | Circuit | Distribution | 2.1515 |  | HFTD 2 | 0.03 | 0.029937 | 6.3139e-05 | 0.0089261 | 0.0060653 | 0.0018712 | 0.00098954 | N/A | 0.0014351 | 3.3539 | N/A | N/A | 1.2603 | 0.043996 | N/A | 1.2603
TECOLOTE | Circuit | Distribution | 10.2353 |  | HFTD 3 | 0.0088113 | 0.0088113 | 0 | 0.0086438 | 0.0044273 | 0.00073488 | 0.0034817 | N/A | 0.0024084 | 1.0194 | N/A | N/A | 1.093 | 0 | N/A | 1.093
TEE VEE | Circuit | Distribution | 4.775 |  | HFTD 3 | 0.0020558 | 0.0020558 | 1.5717e-08 | 0.0030007 | 0.0016811 | 1.7426e-05 | 0.0013022 | N/A | 0.0051078 | 0.68512 | N/A | N/A | 1.8333 | 3.077e-06 | N/A | 1.8333
TEJON | Circuit | Distribution | 51.5002 |  | HFTD 2 | 0.010361 | 0.010361 | 0 | 0.0027547 | 0.0016236 | 8.8721e-05 | 0.0010423 | N/A | 0.062835 | 3.7612 | N/A | N/A | 1.2932 | 0 | N/A | 1.2932
TEMPEST | Circuit | Distribution | 1.5903 |  | HFTD 2 | 0.011993 | 0.011993 | 2.842e-07 | 0.010079 | 0.0058567 | 2.6215e-05 | 0.0041957 | N/A | 0.0066882 | 1.1899 | N/A | N/A |  | 4.2493e-05 | N/A
TENDER | Circuit | Distribution | 3.1523 |  | HFTD 2 | 0.0087548 | 0.0085222 | 0.00023262 | 0.0056668 | 0.001482 | 0.0014223 | 0.0027625 | N/A | 0.0034694 | 1.5039 | N/A | N/A | 1.2076 | 0.067049 | N/A | 1.2076
TENNECO | Circuit | Distribution | 86.2989 |  | HFTD 3 | 0.0064333 | 0.0064321 | 1.2278e-06 | 0.0023609 | 0.0018441 | 2.6129e-05 | 0.0004907 | N/A | 0.050129 | 2.7244 | N/A | N/A | 1.2068 | 2.4492e-05 | N/A | 1.2068
TERMINUS | Circuit | Distribution | 11.0592 |  | HFTD 2 | 0.00056019 | 0.00056011 | 7.7742e-08 | 0.0020303 | 0.0009456 | 0.0003022 | 0.00078251 | N/A | 0.0005664 | 0.27587 | N/A | N/A | 1.0997 | 0.00013726 | N/A | 1.0997
TERRA COTTA | Circuit | Distribution | 9.7889 |  | HFTD 2 | 0.0064898 | 0.0064897 | 2.3345e-08 | 0.0047488 | 0.0017801 | 0.00018208 | 0.0027866 | N/A | 0.0064701 | 1.3666 | N/A | N/A | 1.1667 | 3.6081e-06 | N/A | 1.1667
TEST | Circuit | Distribution | 4.6903 |  | HFTD 2 | 0.008827 | 0.0088228 | 4.2175e-06 | 0.014974 | 0.0045073 | 0.0041199 | 0.0063471 | N/A | 0.00048293 | 0.58919 | N/A | N/A | 1.1103 | 0.0087332 | N/A | 1.1103
TETLEY | Circuit | Distribution | 10.4414 |  | HFTD 3 | 0.012893 | 0.012802 | 9.1196e-05 | 0.013585 | 0.0094591 | 0.0013716 | 0.0027539 | N/A | 0.082184 | 0.94238 | N/A | N/A | 1.3371 | 0.0011097 | N/A | 1.3371
TEXFI | Circuit | Distribution | 1.9027 |  | HFTD 2 | 0.0193 | 0.018832 | 0.0004677 | 0.0071316 | 0.0018723 | 0.00015993 | 0.0050993 | N/A | 0.002194 | 2.6407 | N/A | N/A | 1.125 | 0.21317 | N/A | 1.125
THACHER | Circuit | Distribution | 64.3574 |  | HFTD 3 | 0.0043484 | 0.0043479 | 4.5027e-07 | 0.0056215 | 0.0042511 | 0.00032925 | 0.0010412 | N/A | 0.013989 | 0.77344 | N/A | N/A | 1.1431 | 3.2187e-05 | N/A | 1.1431
THOMPSEN | Circuit | Distribution | 1.0424 |  | HFTD 2 | 0.001124 | 0.001097 | 2.7035e-05 | 0.0043292 | 0.00044645 | 0.0021544 | 0.0017283 | N/A | 0.0060128 | 0.25339 | N/A | N/A | 1.0445 | 0.0044963 | N/A | 1.0445
THORNTON | Circuit | Distribution | 0.50767 |  | HFTD 2 | 0.0036148 | 0.0033992 | 0.00021561 | 0.010126 | 0.0013763 | 0.0070827 | 0.0016674 | N/A | 8.7891e-05 | 0.33568 | N/A | N/A | 1.227 | 2.4531 | N/A | 1.227
THRUSH | Circuit | Distribution | 4.7192 |  | HFTD 3 | 0.025227 | 0.025223 | 3.2025e-06 | 0.012608 | 0.007856 | 0.00016351 | 0.0045888 | N/A | 0.0080259 | 2.0005 | N/A | N/A | 1.5668 | 0.00039902 | N/A | 1.5668
TICO | Circuit | Distribution | 34.3303 |  | HFTD 3 | 0.011838 | 0.011834 | 4.172e-06 | 0.011263 | 0.0047983 | 0.0010053 | 0.0054589 | N/A | 0.010406 | 1.0507 | N/A | N/A | 1.2523 | 0.0004009 | N/A | 1.2523
TIMBER CANYON | Circuit | Distribution | 22.4352 |  | HFTD 3 | 0.0013465 | 0.0013448 | 1.7014e-06 | 0.00474 | 0.0035178 | 0.00012536 | 0.0010969 | N/A | 0.0084666 | 0.28372 | N/A | N/A | 1.1145 | 0.00020095 | N/A | 1.1145
TIN MINE | Circuit | Distribution | 17.0787 |  | HFTD 2 | 0.0054813 | 0.0054771 | 4.2381e-06 | 0.0036535 | 0.0024817 | 7.624e-05 | 0.0010955 | N/A | 0.0042167 | 1.4991 | N/A | N/A | 1.2968 | 0.0010051 | N/A | 1.2968
TIPS | Circuit | Distribution | 0.94485 |  | HFTD 3 | 0.0062068 | 0.0061496 | 5.7182e-05 | 0.022691 | 0.0040232 | 0.00016283 | 0.018505 | N/A | 0.0097376 | 0.27101 | N/A | N/A | 1.0487 | 0.0058723 | N/A | 1.0487
TITAN | Circuit | Distribution | 61.3687 |  | HFTD 3 | 0.010951 | 0.010935 | 1.6039e-05 | 0.003919 | 0.0024568 | 8.7042e-05 | 0.0013751 | N/A | 0.05699 | 2.7903 | N/A | N/A | 1.1919 | 0.00028143 | N/A | 1.1919
TOGA | Circuit | Distribution | 2.8804 |  | HFTD 3 | 0.0033962 | 0.0033513 | 4.4946e-05 | 0.02781 | 0.0094155 | 0.00017402 | 0.01822 | N/A | 0.010028 | 0.12051 | N/A | N/A | 1.1717 | 0.0044822 | N/A | 1.1717
TOLA | Circuit | Distribution | 1.1572 |  | HFTD 2 | 0.0081867 | 0.0081266 | 6.009e-05 | 0.0090953 | 0.0038684 | 0.0010031 | 0.0042238 | N/A | 0.00088226 | 0.89349 | N/A | N/A | 1.1598 | 0.06811 | N/A | 1.1598
TOLL | Circuit | Distribution | 6.2137 |  | HFTD 2 | 0.020659 | 0.020659 | 0 | 0.0065913 | 0.0046577 | 5.6213e-05 | 0.0018773 | N/A | 0.15729 | 3.1344 | N/A | N/A | 1.5277 | 0 | N/A | 1.5277
TOLLHOUSE | Circuit | Distribution | 1.4273 |  | HFTD 3 | 0.0027233 | 0.0027232 | 1.2677e-07 | 0.015171 | 0.008602 | 0.00069979 | 0.005869 | N/A | 0.004294 | 0.1795 | N/A | N/A | 1.3101 | 2.9523e-05 | N/A | 1.3101
TOMAHAWK | Circuit | Distribution | 5.9896 |  | HFTD 2 | 0.021525 | 0.021497 | 2.8137e-05 | 0.0058742 | 0.0036251 | 3.7214e-05 | 0.0022119 | N/A | 0.0056737 | 3.6595 | N/A | N/A | 1.1441 | 0.0049592 | N/A | 1.1441
TONNER | Circuit | Distribution | 4.6724 |  | HFTD 3 | 0.0070405 | 0.0070405 | 0 | 0.011695 | 0.0039586 | 0.00036356 | 0.0073731 | N/A | 0 | 0.602 | N/A | N/A | 1.0972 |  | N/A | 1.0972
TONTO | Circuit | Distribution | 1.1624 | Top 5% Highest Risk | HFTD Tier 2 | 0.05897 | 0.058068 | 0.00090172 | 0.0076917 | 0.0033249 | 1.4757e-05 | 0.004352 | N/A | 0.0010236 | 7.5495 | N/A | N/A | 1.1541 | 0.88096 | N/A | 1.1541
TORONTO | Circuit | Distribution | 14.799 |  | HFTD 3 | 0.0085431 | 0.0085256 | 1.7515e-05 | 0.010505 | 0.0071851 | 0.0013028 | 0.0020171 | N/A | 0.056008 | 0.81157 | N/A | N/A | 1.2173 | 0.00031272 | N/A | 1.2173
TOWNHALL | Circuit | Distribution | 11.8537 |  | HFTD 2 | 0.032186 | 0.032162 | 2.4338e-05 | 0.006326 | 0.0041291 | 4.142e-05 | 0.0021555 | N/A | 0.050517 | 5.0841 | N/A | N/A | 1.0965 | 0.00048177 | N/A | 1.0965
TOWNSHIP | Circuit | Distribution | 15.7206 |  | HFTD 3 | 0.00028322 | 0.0002343 | 4.8921e-05 | 0.016605 | 0.010362 | 0.00097462 | 0.0052684 | N/A | 0.017054 | 0.01411 | N/A | N/A | 1.1411 | 0.0028687 | N/A | 1.1411
TRAM | Circuit | Distribution | 3.5659 |  | HFTD 2 | 0.001921 | 0.0019081 | 1.291e-05 | 0.0025678 | 0.001829 | 0.00021176 | 0.00052702 | N/A | 0.088094 | 0.7431 | N/A | N/A | 1.3158 | 0.00014654 | N/A | 1.3158
TRAUTWEIN | Circuit | Distribution | 7.5342 |  | HFTD 2 | 0.015635 | 0.015621 | 1.4325e-05 | 0.0048908 | 0.0024269 | 0.0002444 | 0.0022195 | N/A | 0.0063032 | 3.1939 | N/A | N/A | 1.0962 | 0.0022726 | N/A | 1.0962
TREMAINE | Circuit | Distribution | 4.9422 |  | HFTD 3 | 0.025609 | 0.025601 | 8.7702e-06 | 0.022304 | 0.013213 | 0.0054591 | 0.0036328 | N/A | 0.03091 | 1.1478 | N/A | N/A | 1.0223 | 0.00028374 | N/A | 1.0223
TRESTLE | Circuit | Distribution | 2.2124 |  | HFTD 2 | 0.0010382 | 0.0010328 | 5.4487e-06 | 0.0077557 | 0.0058374 | 0.00027313 | 0.0016451 | N/A | 0.0005611 | 0.13316 | N/A | N/A | 1.1877 | 0.0097108 | N/A | 1.1877
TREVINO | Circuit | Distribution | 0.96051 |  | HFTD 2 | 0.00017147 | 0.00017147 | 0 | 0.004319 | 0.0026691 | 0.00018436 | 0.0014656 | N/A | 0.014198 | 0.039701 | N/A | N/A |  | 0 | N/A
TRI CITY | Circuit | Distribution | 0.2929 |  | HFTD 2 | 0.0033368 | 0.00065063 | 0.0026862 | 0.0077659 | 0.0040437 | 0.0017763 | 0.0019458 | N/A | 0.0012376 | 0.083781 | N/A | N/A | 1.0637 | 2.1704 | N/A | 1.0637
TRIUNFO | Circuit | Distribution | 3.1089 | Top 5% Highest Risk | HFTD Tier 3 | 0.045841 | 0.045836 | 4.8029e-06 | 0.014341 | 0.0073442 | 0.00029696 | 0.0066997 | N/A | 0.0063818 | 3.1962 | N/A | N/A | 1.0234 | 0.00075259 | N/A | 1.0234
TROUT | Circuit | Distribution | 3.4417 |  | HFTD 2 | 0.0023115 | 0.0023115 | 0 | 0.006296 | 0.0023461 | 0.00023525 | 0.0037146 | N/A | 0.024104 | 0.36715 | N/A | N/A |  | 0 | N/A
TRUMBLE | Circuit | Distribution | 5.8131 |  | HFTD 2 | 0.0097673 | 0.0097649 | 2.3539e-06 | 0.0027017 | 0.00091021 | 5.8643e-05 | 0.0017328 | N/A | 0.0020133 | 3.6144 | N/A | N/A | 1.0881 | 0.0011691 | N/A | 1.0881
TRUMP | Circuit | Distribution | 15.7357 |  | HFTD 3 | 0.0046435 | 0.0046429 | 5.9124e-07 | 0.010023 | 0.0060756 | 0.00069078 | 0.0032569 | N/A | 0 | 0.46321 | N/A | N/A | 1.0974 | inf | N/A | 1.0974
TRUMPET | Circuit | Distribution | 24.949 |  | HFTD 3 | 0.019108 | 0.0191 | 7.4917e-06 | 0.0058751 | 0.0037536 | 0.00021787 | 0.0019036 | N/A | 0.033723 | 3.2511 | N/A | N/A | 1.2056 | 0.00022216 | N/A | 1.2056
TUBA | Circuit | Distribution | 7.8807 |  | HFTD 3 | 0.0079324 | 0.0078952 | 3.7238e-05 | 0.007242 | 0.0037288 | 4.3817e-05 | 0.0034695 | N/A | 0.021054 | 1.0902 | N/A | N/A | 1.2079 | 0.0017687 | N/A | 1.2079
TUDOR | Circuit | Distribution | 10.7487 | Top 5% Highest Risk | HFTD Tier 2 | 0.049128 | 0.049127 | 1.1692e-06 | 0.013117 | 0.0061461 | 0.001447 | 0.0055242 | N/A | 0.0032385 | 3.7452 | N/A | N/A | 1.2535 | 0.00036102 | N/A | 1.2535
TUFA | Circuit | Distribution | 22.1819 |  | HFTD 2 | 0.0036174 | 0.0035756 | 4.1854e-05 | 0.0034347 | 0.0025687 | 2.1398e-05 | 0.00084456 | N/A | 0.27111 | 1.041 | N/A | N/A | 1.4486 | 0.00015438 | N/A | 1.4486
TULLY | Circuit | Distribution | 4.4442 |  | HFTD 2 | 0.0051178 | 0.0051119 | 5.8291e-06 | 0.0084527 | 0.0036873 | 0.00032282 | 0.0044426 | N/A | 0.0031325 | 0.60477 | N/A | N/A | 1.3146 | 0.0018608 | N/A | 1.3146
TUNGSTEN | Circuit | Distribution | 0.54979 |  | HFTD 3 | 0.025879 | 0.025879 | 0 | 0.0062147 | 0.0049724 | 4.1229e-05 | 0.0012011 | N/A | 0.024078 | 4.1641 | N/A | N/A |  | 0 | N/A
TURNPIKE | Circuit | Distribution | 1.5899 |  | HFTD 2 | 0.0066409 | 0.0064097 | 0.00023122 | 0.017951 | 0.0059767 | 0.0040678 | 0.0079069 | N/A | 0.0016122 | 0.35706 | N/A | N/A | 1.0666 | 0.14341 | N/A | 1.0666
TWIN LAKES | Circuit | Distribution | 3.6655 |  | HFTD 3 | 0.00096356 | 0.00067168 | 0.00029187 | 0.026371 | 0.015365 | 0.00025608 | 0.010749 | N/A | 0.04243 | 0.025471 | N/A | N/A | 1.0931 | 0.006879 | N/A | 1.0931
TWIN PEAKS | Circuit | Distribution | 3.6827 |  | HFTD 3 | 0.031902 | 0.0319 | 2.4091e-06 | 0.027879 | 0.018557 | 0.0041546 | 0.0051674 | N/A | 0.066278 | 1.1442 | N/A | N/A | 2 | 3.6349e-05 | N/A | 2
TWISTER | Circuit | Distribution | 0.99433 |  | HFTD 2 | 0.0023531 | 0.0023531 | 0 | 0.01517 | 0.0040312 | 0.0043443 | 0.0067941 | N/A | 0 | 0.15512 | N/A | N/A | 1.0534 |  | N/A | 1.0534
UNDERWOOD | Circuit | Distribution | 15.9483 |  | HFTD 2 | 0.0064921 | 0.0063067 | 0.00018539 | 0.0030274 | 0.0017592 | 0.0002663 | 0.0010019 | N/A | 0.093886 | 2.0832 | N/A | N/A | 1.2127 | 0.0019746 | N/A | 1.2127
UNIVERSITY | Circuit | Distribution | 0.38564 |  | HFTD 2 | 0.014759 | 0.014758 | 4.2499e-07 | 0.007555 | 0.0030028 | 0.00033711 | 0.0042151 | N/A | 0.0093635 | 1.9534 | N/A | N/A | 1.0018 | 4.5388e-05 | N/A | 1.0018
URBITA | Circuit | Distribution | 7.6782 |  | HFTD 2 | 0.014362 | 0.014308 | 5.3462e-05 | 0.0094242 | 0.0041456 | 0.00062274 | 0.0046558 | N/A | 0.014825 | 1.5183 | N/A | N/A | 1.233 | 0.0036062 | N/A | 1.233
UTE | Circuit | Distribution | 0.91717 |  | HFTD 2 | 0.023482 | 0.023482 | 0 | 0.01176 | 0.004384 | 0.00027395 | 0.0071017 | N/A | 0.0077105 | 1.9969 | N/A | N/A |  | 0 | N/A
VAL VERDE | Circuit | Distribution | 2.5981 |  | HFTD 3 | 0.0010887 | 0.001084 | 4.6888e-06 | 0.0095335 | 0.0037941 | 4.1449e-05 | 0.0056979 | N/A | 0.012892 | 0.1137 | N/A | N/A | 1.0448 | 0.00036371 | N/A | 1.0448
VALLECITO | Circuit | Distribution | 13.3918 |  | HFTD 2 | 0.0060222 | 0.0060022 | 1.9934e-05 | 0.008093 | 0.0044554 | 0.001717 | 0.0019205 | N/A | 0.0027871 | 0.74166 | N/A | N/A | 1.0911 | 0.0071522 | N/A | 1.0911
VALLEY OF THE MOON | Circuit | Distribution | 5.9166 |  | HFTD 3 | 0.010024 | 0.009995 | 2.9241e-05 | 0.017143 | 0.010605 | 0.004658 | 0.0018795 | N/A | 0.045512 | 0.58304 | N/A | N/A | 1.1509 | 0.00064249 | N/A | 1.1509
VALMONTE | Circuit | Distribution | 2.6623 |  | HFTD 2 | 0.0046345 | 0.0046345 | 0 | 0.016351 | 0.0055682 | 0.0060547 | 0.0047279 | N/A | 0 | 0.28345 | N/A | N/A | 1.2924 |  | N/A | 1.2924
VANDERLIP | Circuit | Distribution | 1.3884 |  | HFTD 2 | 0.016032 | 0.016032 | 3.935e-07 | 0.0069807 | 0.0046571 | 0.00080898 | 0.0015147 | N/A | 0.0012739 | 2.2966 | N/A | N/A | 1.8441 | 0.00030889 | N/A | 1.8441
VARGAS | Circuit | Distribution | 0.99944 |  | HFTD 2 | 0.0034116 | 0.0010664 | 0.0023452 | 0.018925 | 0.015648 | 0.0015411 | 0.0017365 | N/A | 0.011141 | 0.056348 | N/A | N/A | 1.114 | 0.21051 | N/A | 1.114
VASQUEZ | Circuit | Distribution | 0.59674 |  | HFTD 3 | 0.0075233 | 0.0064875 | 0.0010358 | 0.012823 | 0.0083218 | 0.00012288 | 0.0043781 | N/A | 0.010315 | 0.50594 | N/A | N/A | 1.097 | 0.10042 | N/A | 1.097
VENGEANCE | Circuit | Distribution | 0.93855 |  | HFTD 2 | 0.015808 | 0.015746 | 6.2597e-05 | 0.0040124 | 0.00055414 | 0.00039752 | 0.0030608 | N/A | 0.005089 | 3.9242 | N/A | N/A | 1.0887 | 0.012301 | N/A | 1.0887
VENUS | Circuit | Distribution | 8.1516 |  | HFTD 2 | 0.0061719 | 0.0061719 | 0 | 0.031564 | 0.023257 | 0.0039724 | 0.0043352 | N/A | 0.0013359 | 0.19554 | N/A | N/A | 1.4674 | 0 | N/A | 1.4674
VENWIND 1 | Circuit | Distribution | 0.54942 |  | HFTD 2 | 0.015876 | 0.015876 | 0 | 0.011213 | 0.007027 | 0.0001842 | 0.0040022 | N/A | 0.066882 | 1.4158 | N/A | N/A |  | 0 | N/A
VENWIND 4 | Circuit | Distribution | 1.4035 |  | HFTD 2 | 0.0039195 | 0.0039195 | 0 | 0.0032073 | 0.0018087 | 8.557e-05 | 0.0013131 | N/A | 0.081596 | 1.222 | N/A | N/A |  | 0 | N/A
VERA CRUZ | Circuit | Distribution | 7.1343 |  | HFTD 3 | 0.016796 | 0.016793 | 2.8903e-06 | 0.011036 | 0.0061153 | 0.00070319 | 0.0042179 | N/A | 0.0091841 | 1.5216 | N/A | N/A | 1.1334 | 0.00031471 | N/A | 1.1334
VERDEMONT | Circuit | Distribution | 15.6908 |  | HFTD 2 | 0.0091942 | 0.0091925 | 1.6888e-06 | 0.0065352 | 0.0030571 | 6.4415e-05 | 0.0034137 | N/A | 0.015831 | 1.4066 | N/A | N/A | 1.5263 | 0.00010667 | N/A | 1.5263
VERDUGO | Circuit | Distribution | 20.9247 |  | HFTD 3 | 0.013502 | 0.013452 | 4.9871e-05 | 0.0043498 | 0.002489 | 0.00045474 | 0.001406 | N/A | 0.03726 | 3.0925 | N/A | N/A | 1.1072 | 0.0013384 | N/A | 1.1072
VERDUN | Circuit | Distribution | 0.42917 |  | HFTD 2 | 0.0015953 | 0.0015953 | 0 | 0.02206 | 0.0048745 | 0.0065153 | 0.01067 | N/A | 0 | 0.072315 | N/A | N/A | 1.287 |  | N/A | 1.287
VETERANS | Circuit | Distribution | 3.3694 |  | HFTD 3 | 0.011433 | 0.011166 | 0.0002676 | 0.0058462 | 0.0043502 | 0.00030117 | 0.0011948 | N/A | 0.0065369 | 1.9099 | N/A | N/A | 1.0804 | 0.040937 | N/A | 1.0804
VIAVERDE | Circuit | Distribution | 1.6425 |  | HFTD 2 | 0.0047903 | 0.0047712 | 1.9071e-05 | 0.010568 | 0.0025183 | 0.0015155 | 0.0065342 | N/A | 0.0021135 | 0.45148 | N/A | N/A | 1.099 | 0.0090237 | N/A | 1.099
VICASA | Circuit | Distribution | 42.0532 |  | HFTD 3 | 0.020092 | 0.020081 | 1.1173e-05 | 0.015644 | 0.010036 | 0.0011031 | 0.004505 | N/A | 0.02354 | 1.2836 | N/A | N/A | 1.3144 | 0.00047462 | N/A | 1.3144
VIDEO | Circuit | Distribution | 11.6346 |  | HFTD 2 | 0.0076623 | 0.0076613 | 1.0325e-06 | 0.010498 | 0.0037638 | 0.0026864 | 0.0040472 | N/A | 0.011787 | 0.72982 | N/A | N/A | 1.6321 | 8.7602e-05 | N/A | 1.6321
VIENTO | Circuit | Distribution | 77.8568 |  | HFTD 3 | 0.017169 | 0.017159 | 9.9349e-06 | 0.0050919 | 0.0032016 | 6.9827e-05 | 0.0018205 | N/A | 0.059944 | 3.3698 | N/A | N/A | 1.2054 | 0.00016574 | N/A | 1.2054
VIOLET | Circuit | Distribution | 4.2728 |  | HFTD 2 | 0.0065627 | 0.0065627 | 0 | 0.022856 | 0.010226 | 0.0068779 | 0.0057525 | N/A | 0 | 0.28713 | N/A | N/A | 1.2576 |  | N/A | 1.2576
VULCAN | Circuit | Distribution | 0.2839 |  | HFTD 2 | 0.003023 | 0.003022 | 1.0404e-06 | 0.018188 | 0.015604 | 0.00016882 | 0.0024154 | N/A | 0.028442 | 0.16616 | N/A | N/A | 1.6316 | 3.6581e-05 | N/A | 1.6316
WAHOO | Circuit | Distribution | 2.5292 |  | HFTD 2 | 0.0010911 | 0.0010698 | 2.1352e-05 | 0.012385 | 0.0051841 | 0.0020844 | 0.0051168 | N/A | 0.0016067 | 0.086374 | N/A | N/A | 1.0917 | 0.013289 | N/A | 1.0917
WAITE | Circuit | Distribution | 2.85 | Top 5% Highest Risk | HFTD Tier 2 | 0.05799 | 0.057977 | 1.2626e-05 | 0.012168 | 0.0078498 | 0.00027507 | 0.004043 | N/A | 0.0022383 | 4.7648 | N/A | N/A | 1.2554 | 0.0056408 | N/A | 1.2554
WAPELLO | Circuit | Distribution | 4.5992 |  | HFTD 3 | 0.025643 | 0.025639 | 4.2519e-06 | 0.010483 | 0.0072905 | 0.00041791 | 0.0027743 | N/A | 0.0077552 | 2.4458 | N/A | N/A | 1.5171 | 0.00054826 | N/A | 1.5171
WARDELL | Circuit | Distribution | 0.87527 |  | HFTD 2 | 0.0016145 | 0.0015523 | 6.2208e-05 | 0.0073615 | 0.0036126 | 0.00165 | 0.0020989 | N/A | 0.00040536 | 0.21086 | N/A | N/A | 1.081 | 0.15347 | N/A | 1.081
WARHAWK | Circuit | Distribution | 3.7964 |  | HFTD 2 | 0.013541 | 0.013489 | 5.17e-05 | 0.0041562 | 0.0024794 | 0.0001293 | 0.0015475 | N/A | 0.0098393 | 3.2455 | N/A | N/A | 1.1232 | 0.0052544 | N/A | 1.1232
WEESHA | Circuit | Distribution | 2.6883 |  | HFTD 3 | 0.00034006 | 0.0003379 | 2.1572e-06 | 0.0061371 | 0.0040058 | 0.00036298 | 0.0017683 | N/A | 0.025271 | 0.055059 | N/A | N/A | 1.0021 | 8.5364e-05 | N/A | 1.0021
WEIRICK | Circuit | Distribution | 0.67826 |  | HFTD 2 | 0.0031207 | 0.0029313 | 0.00018939 | 0.0076085 | 0.0053705 | 0.00020077 | 0.0020373 | N/A | 0.00086722 | 0.38527 | N/A | N/A | 1.1243 | 0.21839 | N/A | 1.1243
WELCH | Circuit | Distribution | 9.3673 |  | HFTD 2 | 0.00061767 | 0.00061726 | 4.1808e-07 | 0.0029355 | 0.0019558 | 0.00013183 | 0.0008479 | N/A | 0.00088771 | 0.21027 | N/A | N/A | 1.1004 | 0.00047097 | N/A | 1.1004
WESTBLUFF | Circuit | Distribution | 14.8664 |  | HFTD 3 | 0.011559 | 0.011554 | 4.9931e-06 | 0.0057876 | 0.0027919 | 6.3619e-05 | 0.0029321 | N/A | 0.016389 | 1.9963 | N/A | N/A | 1.2989 | 0.00030466 | N/A | 1.2989
WESTBROOK | Circuit | Distribution | 3.6159 |  | HFTD 3 | 0.033513 | 0.033513 | 0 | 0.0074861 | 0.0048381 | 9.2957e-05 | 0.0025551 | N/A | 0 | 4.4767 | N/A | N/A | 1.0822 |  | N/A | 1.0822
WESTFALL | Circuit | Distribution | 3.7801 |  | HFTD 3 | 0.0090742 | 0.0090703 | 3.8903e-06 | 0.011863 | 0.0065412 | 0.0037738 | 0.0015475 | N/A | 0.002158 | 0.76462 | N/A | N/A | 1.1974 | 0.0018027 | N/A | 1.1974
WHIP | Circuit | Distribution | 2.8873 |  | HFTD 3 | 0.021658 | 0.021435 | 0.00022327 | 0.0031712 | 0.0018509 | 4.0846e-05 | 0.0012795 | N/A | 0.012412 | 6.7591 | N/A | N/A | 1.1864 | 0.017989 | N/A | 1.1864
WHIPSTOCK | Circuit | Distribution | 17.1896 |  | HFTD 3 | 0.02836 | 0.02836 | 0 | 0.01551 | 0.0082477 | 0.00084728 | 0.0064151 | N/A | 0 | 1.8285 | N/A | N/A | 1.225 |  | N/A | 1.225
WHISPER | Circuit | Distribution | 0.41488 |  | HFTD 2 | 0.0033865 | 0.0033479 | 3.8607e-05 | 0.0068631 | 0.00094798 | 0.002226 | 0.0036891 | N/A | 0.001675 | 0.48782 | N/A | N/A | 1.0777 | 0.02305 | N/A | 1.0777
WHITECLIFF | Circuit | Distribution | 6.2819 |  | HFTD 3 | 0.004122 | 0.0040325 | 8.9403e-05 | 0.010791 | 0.0057172 | 0.00046281 | 0.0046111 | N/A | 0.016052 | 0.37369 | N/A | N/A | 1.1458 | 0.0055697 | N/A | 1.1458
WHITEHORN | Circuit | Distribution | 2.864 |  | HFTD 2 | 0.019687 | 0.019583 | 0.00010336 | 0.007992 | 0.0072118 | 1.5258e-05 | 0.00076504 | N/A | 0.0044443 | 2.4504 | N/A | N/A | 1.1025 | 0.023256 | N/A | 1.1025
WHIZZIN | Circuit | Distribution | 1.9334 |  | HFTD 3 | 0.0018062 | 0.0016572 | 0.00014899 | 0.020616 | 0.005464 | 0.0014057 | 0.013746 | N/A | 0.016052 | 0.080385 | N/A | N/A | 1.0616 | 0.0092818 | N/A | 1.0616
WIGWAG | Circuit | Distribution | 0.78842 |  | HFTD 2 | 0.031304 | 0.029373 | 0.0019312 | 0.012115 | 0.0011492 | 0.0019734 | 0.0089922 | N/A | 0.0041876 | 2.4245 | N/A | N/A | 1.2809 | 0.46117 | N/A | 1.2809
WILDOMAR | Circuit | Distribution | 14.5778 |  | HFTD 3 | 0.0093435 | 0.0093434 | 2.9959e-09 | 0.0030233 | 0.0011962 | 6.659e-05 | 0.0017605 | N/A | 0.008257 | 3.0905 | N/A | N/A | 1 | 3.6283e-07 | N/A | 1
WILSON CREEK | Circuit | Distribution | 3.6044 |  | HFTD 3 | 0.013593 | 0.013574 | 1.8948e-05 | 0.010651 | 0.0036105 | 0.0037268 | 0.0033141 | N/A | 0.0048712 | 1.2744 | N/A | N/A | 1.1411 | 0.0038899 | N/A | 1.1411
WINERY | Circuit | Distribution | 42.6396 |  | HFTD 3 | 0.016523 | 0.016523 | 1.5732e-07 | 0.0045034 | 0.0032508 | 0.00023986 | 0.0010127 | N/A | 0.0069697 | 3.669 | N/A | N/A | 1.1408 | 2.2573e-05 | N/A | 1.1408
WINNEBAGO | Circuit | Distribution | 0.68862 |  | HFTD 2 | 0.0038084 | 0.0026212 | 0.0011872 | 0.004433 | 0.0011016 | 0.00011285 | 0.0032186 | N/A | 0.0014212 | 0.59129 | N/A | N/A | 1.1447 | 0.83533 | N/A | 1.1447
WINTHROP | Circuit | Distribution | 0.28283 |  | HFTD 2 | 0.0065041 | 0.0064781 | 2.5997e-05 | 0.0066141 | 0.002722 | 0.00038899 | 0.003503 | N/A | 6.492e-05 | 0.97945 | N/A | N/A | 1.072 | 0.40045 | N/A | 1.072
WOBEGONE | Circuit | Distribution | 27.5743 |  | HFTD 2 | 0.029021 | 0.029019 | 2.3186e-06 | 0.0022661 | 0.0015298 | 4.0078e-05 | 0.00069621 | N/A | 0.012058 | 12.8056 | N/A | N/A | 1.3143 | 0.00019228 | N/A | 1.3143
WRIGLEY | Circuit | Distribution | 0.95522 |  | HFTD 3 | 0.0084085 | 0.0084085 | 0 | 0.0072621 | 0.001527 | 0.00013014 | 0.0056049 | N/A | 0 | 1.1579 | N/A | N/A | 1.0537 |  | N/A | 1.0537
WYLE | Circuit | Distribution | 1.0843 |  | HFTD 2 | 0.0036547 | 0.003348 | 0.00030671 | 0.0094185 | 0.0018475 | 0.003731 | 0.00384 | N/A | 0.0017083 | 0.35547 | N/A | N/A | 1.0888 | 0.17954 | N/A | 1.0888
YARBOROUGH | Circuit | Distribution | 0.28183 |  | HFTD 2 | 0.001045 | 0.00082059 | 0.00022439 | 0.0028915 | 0.00059672 | 0.00021516 | 0.0020796 | N/A | 0.010644 | 0.28379 | N/A | N/A | 1.035 | 0.021081 | N/A | 1.035
YORKTOWN | Circuit | Distribution | 2.1411 |  | HFTD 2 | 0.0010033 | 0.0010033 | 0 | 0.0167 | 0.0090874 | 0.00024982 | 0.0073628 | N/A | 0 | 0.060075 | N/A | N/A | 1.0663 |  | N/A | 1.0663
YOSEMITE | Circuit | Distribution | 3.0072 |  | HFTD 3 | 0.0037744 | 0.0035546 | 0.0002198 | 0.026649 | 0.011059 | 0.00098527 | 0.014605 | N/A | 0.016277 | 0.13339 | N/A | N/A | 1.2107 | 0.013504 | N/A | 1.2107
YUCATAN | Circuit | Distribution | 1.9654 |  | HFTD 3 | 0.014656 | 0.014656 | 0 | 0.016366 | 0.0053606 | 0.00049291 | 0.010512 | N/A | 0.0026753 | 0.89553 | N/A | N/A | 1.1626 | 0 | N/A | 1.1626
ZENDA | Circuit | Distribution | 40.9946 |  | HFTD 2 | 0.0045935 | 0.0045922 | 1.3041e-06 | 0.0027522 | 0.0018538 | 0.00036205 | 0.00053636 | N/A | 0.048409 | 1.6686 | N/A | N/A | 1.1539 | 2.694e-05 | N/A | 1.1539
ZINC | Circuit | Distribution | 3.042 |  | HFTD 2 | 0.0011967 | 0.0011967 | 0 | 0.016647 | 0.010409 | 0.0027422 | 0.003495 | N/A | 0.0013265 | 0.071891 | N/A | N/A | 1.1881 | 0 | N/A | 1.1881
ZIRCON | Circuit | Distribution | 0.3236 |  | HFTD 2 | 0.0082122 | 0.0082122 | 0 | 0.028579 | 0.0015037 | 0.0010298 | 0.026046 | N/A | 0.0013376 | 0.28735 | N/A | N/A | 1.0298 | 0 | N/A | 1.0298
ZONE | Circuit | Distribution | 25.4849 |  | HFTD 3 | 0.0035988 | 0.0035948 | 3.997e-06 | 0.0063507 | 0.0041956 | 0.00041449 | 0.0017406 | N/A | 0.025967 | 0.56604 | N/A | N/A | 1.173 | 0.00015393 | N/A | 1.173
ZUMA | Circuit | Distribution | 17.3091 |  | HFTD 3 | 0.0039618 | 0.0039618 | 0 | 0.0080705 | 0.0068675 | 7.1485e-05 | 0.0011315 | N/A | 0 | 0.4909 | N/A | N/A | 1.2509 |  | N/A | 1.2509