## Quarterly Submission Guide
| Yes | No | <-- for dropdowns
Office of Energy Infrastructure Safety Attachment 3
Wildifire Mitigation Plan Quarterly report - non-spatial data template
Instructions for use
1 | Fill out the tan cells (color represented here) starting with the cell below (D17: Utility). The Utility name will populate the Table tabs to follow. Date modified will vary by table.
2 | Cells will only accept valid entries. For most cells, this is positive numbers
3 | For each Table tab, after a modification is made, denote the date of the change in cell C4 for each Table tab.
4 | Some columns have an additional header in row 5 to serve as clarification for several columns. With the exception of projected data, row 5 will be highlighted in blue (color represented here)
5 | Some required metrics are future projections. For these, row 5, above the projections will be highlighted light green (color represented here)
In future submissions, report updated projected numbers if / when projections have changed, and report actuals once the quarter / year has passed.
6 | For data required annually rather than quarterly (see Tables 7.2 - 10, 12), report for entire year even if part of the year is projected. Once year has passed, update cell with actuals
7 | Some tables will have additional instructions provided in a Notes box located in cells D2 - D4
Notes will explain terms, signal where projections are required, and provide other useful information.
8 | For the initial quarterly submission, utilities are required to submit data on annual metrics for 2015 - 2020, which should represent the most updated data from the 2020 WMP for years 2015-2019
* | Do not add or manipulate the template for any of the tabs
Update the below table to establish which year, quarter of the WMP cycle this submission this represents.
Utility |  | Southern California Edison Company
First year of 3-year WMP cycle |  | 2020
Submission year |  | 2022
Submission quarter |  | Q4
Date Modified |  | 2022-02-11

## Table 1
Utility | Southern California Edison Company | Notes:
Table No. | 1 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.
Date Modified | 2022-02-11
Note: These columns are placeholders for future QR submissions.
Table 1: Recent performance on progress metrics | [7 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Progress metric name | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
1. Grid condition findings from inspection - Distribution lines in HFTD | 1.a. | Number of circuit miles inspected from patrol inspections in HFTD - Distribution lines | 9718 | 9723 | 9724 | 9729 | 9730 | 1594 | 6934 | 1235 | 235 | 3707 | 5895 | 955 | 1 |  |  |  |  | # circuit miles | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected.
| 1.b. | Number of circuit miles inspected from detailed inspections in HFTD - Distribution lines | 1869 | 2324 | 1984 | 2425 | 14349 | 4137 | 4537 | 4232 | 3495 | 3831 | 5471 | 2762 | 97 |  |  |  |  | # circuit miles | This row is the sum of the four detailed inspection programs found in the submetrics at the bottom of this table. 2021 year-end data is going through final quality assurance review and if any changes are needed, they will be updated in the next quarterly submission.
| 1.c. | Number of circuit miles inspected from other inspections (list types of "other" inspections in comments) in HFTD - Distribution lines | NA | NA | NA | 12605 | 5663 | 1382 | 1382 | 1382 | 1382 | 2548 | 2183 | 258 | 339 |  |  |  |  | # circuit miles | This row is the sum of the two programs below that are considered as "other" and found in the submetrics at the bottom of this table
| 1.d. | Level 1 findings in HFTD for patrol inspections - Distribution lines | 0 | 0 | 3 | 1 | 17 | 0 | 18 | 0 | 1 | 5 | 3 | 0 | 0 |  |  |  |  | # findings
| 1.e. | Level 1 findings in HFTD for detailed inspections - Distribution lines | 2167 | 3152 | 3111 | 2827 | 4147 | 792 | 717 | 710 | 735 | 772 | 647 | 577 | 689 |  |  |  |  | # findings
| 1.f. | Level 1 findings in HFTD for other inspections (list types of "other" inspections in comments) - Distribution lines | 246 | 770 | 326 | 168 | 616 | 90 | 115 | 306 | 261 | 87 | 53 | 41 | 56 |  |  |  |  | # findings
| 1.g. | Level 2 findings in HFTD for patrol inspections - Distribution lines | 6348 | 5106 | 3753 | 3704 | 6491 | 1024 | 1470 | 1222 | 1054 | 1517 | 994 | 853 | 636 |  |  |  |  | # findings
| 1.h. | Level 2 findings in HFTD for detailed inspections - Distribution lines | 7541 | 8113 | 6281 | 16458 | 58595 | 10006 | 9073 | 5645 | 3774 | 8965 | 13959 | 4375 | 1197 |  |  |  |  | # findings
| 1.i. | Level 2 findings in HFTD for other inspections (list types of "other" inspections in comments) - Distribution lines | 4432 | 4145 | 3798 | 3507 | 18212 | 1448 | 1744 | 530 | 1866 | 1169 | 665 | 592 | 803 |  |  |  |  | # findings
| 1.j. | Level 3 findings in HFTD for patrol inspections - Distribution lines | 40 | 10 | 29 | 51 | 227 | 119 | 6 | 0 | 2 | 26 | 90 | 28 | 0 |  |  |  |  | # findings
| 1.k. | Level 3 findings in HFTD for detailed inspections - Distribution lines | 14086 | 17813 | 12548 | 12865 | 31820 | 8767 | 9240 | 7008 | 804 | 13857 | 8949 | 1913 | 555 |  |  |  |  | # findings
| 1.l. | Level 3 findings in HFTD for other inspections (list types of "other" inspections in comments) - Distribution lines | 241 | 124 | 186 | 878 | 77369 | 1263 | 1134 | 3135 | 297 | 472 | 319 | 128 | 196 |  |  |  |  | # findings
1. Grid condition findings from inspection - Distribution lines total | 1.a.ii. | Number of total circuit miles inspected from patrol inspections - Distribution lines | 40194 | 40199 | 40198 | 40206 | 40207 | 3045 | 24160 | 10753 | 2719 | 5417 | 14645 | 16238 | 4318 |  |  |  |  | # circuit miles | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected.
| 1.b.ii. | Number of total circuit miles inspected from detailed inspections - Distribution lines | 7950 | 8034 | 7865 | 9069 | 24059 | 4477 | 5540 | 5938 | 6604 | 4328 | 6673 | 5118 | 2379 |  |  |  |  | # circuit miles | This row is the sum of the four detailed inspection programs found in the submetrics at the bottom of this table.
| 1.c.ii. | Number of total circuit miles inspected from other inspections (list types of "other" inspections in comments) - Distribution lines | 4320 | 4509 | 4093 | 29902 | 8887 | 2106 | 2106 | 2106 | 2106 | 3458 | 2986 | 1092 | 876 |  |  |  |  | # circuit miles | This row is the sum of the two programs below that are considered as "other" and found in the submetrics at the bottom of this table
| 1.d.ii. | Level 1 findings for patrol inspections - Distribution lines | 2 | 2 | 4 | 5 | 25 | 1 | 76 | 0 | 19 | 15 | 11 | 1 | 0 |  |  |  |  | # findings
| 1.e.ii. | Level 1 findings for detailed inspections - Distribution lines | 17777 | 19676 | 21787 | 19493 | 21964 | 4446 | 4954 | 6345 | 5036 | 4882 | 4617 | 4897 | 5203 |  |  |  |  | # findings
| 1.f.ii. | Level 1 findings for other inspections (list types of "other" inspections in comments) - Distribution lines | 1779 | 2684 | 1806 | 1501 | 2039 | 405 | 556 | 637 | 569 | 370 | 317 | 264 | 299 |  |  |  |  | # findings
| 1.g.ii. | Level 2 findings for patrol inspections - Distribution lines | 26390 | 17642 | 15534 | 15147 | 18308 | 4321 | 4328 | 4799 | 3642 | 4542 | 4452 | 3376 | 2764 |  |  |  |  | # findings
| 1.h.ii. | Level 2 findings for detailed inspections - Distribution lines | 51260 | 48850 | 42281 | 55981 | 105785 | 15259 | 16569 | 15534 | 17033 | 13509 | 25967 | 27300 | 29830 |  |  |  |  | # findings
| 1.i.ii. | Level 2 findings for other inspections (list types of "other" inspections in comments) - Distribution lines | 14748 | 13519 | 11997 | 11990 | 25280 | 3645 | 3718 | 2004 | 3945 | 3278 | 2106 | 1874 | 2045 |  |  |  |  | # findings
| 1.j.ii. | Level 3 findings for patrol inspections - Distribution lines | 326 | 57 | 112 | 80 | 520 | 126 | 10 | 5 | 17 | 26 | 94 | 33 | 0 |  |  |  |  | # findings
| 1.k.ii. | Level 3 findings for detailed inspections - Distribution lines | 83586 | 73546 | 62968 | 69597 | 96715 | 12364 | 17489 | 19045 | 20134 | 17607 | 18746 | 20337 | 19598 |  |  |  |  | # findings
| 1.l.ii. | Level 3 findings for other inspections (list types of "other" inspections in comments) - Distribution lines | 1091 | 697 | 936 | 2616 | 90914 | 1546 | 1524 | 4761 | 595 | 660 | 382 | 637 | 221 |  |  |  |  | # findings
1. Grid condition findings from inspection - Transmission lines in HFTD | 1.a.iii. | Number of circuit miles inspected from patrol inspections in HFTD - Transmission lines | 4438 | 4438 | 4438 | 4438 | 4438 | 1109 | 1109 | 1109 | 1109 | 456 | 1090 | 1246 | 879 |  |  |  |  | # circuit miles | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected.
| 1.b.iii. | Number of circuit miles inspected from detailed inspections in HFTD - Transmission lines | NA | NA | NA | 1479 | 11057 | 2077 | 3887 | 1642 | 1630 | 1434 | 3272 | 1588 | 452 |  |  |  |  | # circuit miles | This row is the sum of the three detailed inspection programs and found in the submetrics section at the bottom of this table.
| 1.c.iii. | Number of circuit miles inspected from other inspections (list types of "other" inspections in comments) in HFTD - Transmission lines | NA | NA | NA | 103 | 5003 | 284 | 284 | 284 | 284 | 43 | 121 | 406 | 658 |  |  |  |  | # circuit miles | This row is the sum of the two programs below that are considered as "other" and found in the submetrics at the bottom of this table
| 1.d.iii. | Level 1 findings in HFTD for patrol inspections - Transmission lines | 49 | 81 | 41 | 31 | 70 | 11 | 6 | 15 | 25 | 12 | 17 | 22 | 6 |  |  |  |  | # findings
| 1.e.iii. | Level 1 findings in HFTD for detailed inspections - Transmission lines | 0 | 0 | 0 | 1 | 37 | 7 | 15 | 39 | 38 | 18 | 42 | 23 | 1 |  |  |  |  | # findings
| 1.f.iii. | Level 1 findings in HFTD for other inspections (list types of "other" inspections in comments) - Transmission lines | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 14 |  |  |  |  | # findings
| 1.g.iii. | Level 2 findings in HFTD for patrol inspections - Transmission lines | 693 | 823 | 851 | 892 | 933 | 497 | 1971 | 533 | 141 | 339 | 744 | 544 | 148 |  |  |  |  | # findings
| 1.h.iii. | Level 2 findings in HFTD for detailed inspections - Transmission lines | 15 | 62 | 134 | 346 | 14199 | 1331 | 4832 | 1529 | 911 | 520 | 1406 | 369 | 31 |  |  |  |  | # findings
| 1.i.iii. | Level 2 findings in HFTD for other inspections (list types of "other" inspections in comments) - Transmission lines | 277 | 127 | 393 | 413 | 433 | 16 | 47 | 45 | 79 | 21 | 34 | 29 | 89 |  |  |  |  | # findings
| 1.j.iii. | Level 3 findings in HFTD for patrol inspections - Transmission lines | 908 | 681 | 690 | 261 | 515 | 136 | 387 | 176 | 49 | 613 | 265 | 166 | 40 |  |  |  |  | # findings
| 1.k.iii. | Level 3 findings in HFTD for detailed inspections - Transmission lines | 6 | 41 | 5 | 93 | 2020 | 44 | 399 | 505 | 218 | 203 | 549 | 83 | 2 |  |  |  |  | # findings
| 1.l.iii. | Level 3 findings in HFTD for other inspections (list types of "other" inspections in comments) - Distribution lines | 0 | 0 | 0 | 0 | 41 | 5 | 1 | 2 | 4 | 0 | 1 | 2 | 0 |  |  |  |  | # findings
1. Grid condition findings from inspection - Transmission lines total | 1.a.iv. | Number of total circuit miles inspected from patrol inspections - Transmission lines | 13068 | 13068 | 13068 | 13068 | 13068 | 3267 | 3267 | 3267 | 3267 | 1757 | 2202 | 2836 | 2502 |  |  |  |  | # circuit miles | For 2015-2017, patrol inspections doubled as detailed inspections being completed on every transmission asset in the service territory. Beginning in 2018, the recorded inspection numbers estimate the patrol type inspections in circuit miles being completed. Additionally, SCE tracks completed inspections by "Grids". SCE's complete transmission line network is broken out into large areas called "Grids" and all execution and tracking are recorded at the grid level. The number being represented uses the current transmission circuit mile counts in HFTD for each year. 2020 in particular, evenly distributes the current transmission mile circuit counts into each quarter.
| 1.b.iv. | Number of total circuit miles inspected from detailed inspections - Transmission lines | NA | NA | NA | 4210 | 10818 | 2447 | 4749 | 2545 | 2287 | 1957 | 3939 | 1955 | 897 |  |  |  |  | # circuit miles | This row is the sum of the three detailed inspection found in the submetrics section at the bottom of this table.
| 1.c.iv. | Number of total circuit miles inspected from other inspections (list types of "other" inspections in comments) - Transmission lines | 6460 | 4592 | 6226 | 7309 | 5529 | 1637 | 1637 | 1637 | 1637 | 267 | 2066 | 562 | 767 |  |  |  |  | # circuit miles | This row is the sum of the two programs below that are considered as "other" and found in the submetrics at the bottom of this table
| 1.d.iv. | Level 1 findings for patrol inspections - Transmission lines | 241 | 252 | 211 | 178 | 235 | 50 | 33 | 64 | 61 | 49 | 66 | 49 | 14 |  |  |  |  | # findings
| 1.e.iv. | Level 1 findings for detailed inspections - Transmission lines | 0 | 1 | 0 | 1 | 59 | 8 | 18 | 43 | 47 | 19 | 42 | 24 | 1 |  |  |  |  | # findings
| 1.f.iv. | Level 1 findings for other inspections (list types of "other" inspections in comments) - Transmission lines | 1 | 2 | 2 | 1 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 63 |  |  |  |  | # findings
| 1.g.iv. | Level 2 findings for patrol inspections - Transmission lines | 3897 | 4555 | 5259 | 5118 | 4359 | 1712 | 2956 | 1177 | 797 | 1521 | 1567 | 1165 | 652 |  |  |  |  | # findings
| 1.h.iv. | Level 2 findings for detailed inspections - Transmission lines | 33 | 87 | 165 | 767 | 17570 | 1430 | 4936 | 1586 | 1005 | 535 | 1415 | 378 | 42 |  |  |  |  | # findings
| 1.i.iv. | Level 2 findings for other inspections (list types of "other" inspections in comments) - Transmission lines | 1424 | 577 | 987 | 1133 | 958 | 101 | 135 | 232 | 360 | 124 | 90 | 129 | 181 |  |  |  |  | # findings
| 1.j.iv. | Level 3 findings for patrol inspections - Transmission lines | 7009 | 3299 | 3059 | 1600 | 2717 | 732 | 836 | 479 | 378 | 842 | 520 | 305 | 362 |  |  |  |  | # findings
| 1.k.iv. | Level 3 findings for detailed inspections - Transmission lines | 9 | 44 | 6 | 100 | 2281 | 47 | 403 | 523 | 241 | 206 | 551 | 87 | 2 |  |  |  |  | # findings
| 1.l.iv. | Level 3 findings for other inspections (list types of "other" inspections in comments) - Transmission lines | 1 | 2 | 4 | 3 | 71 | 5 | 2 | 2 | 4 | 0 | 1 | 2 | 0 |  |  |  |  | # findings
2. Vegetation clearance findings from inspection - total | 2.a.i | Number of spans insepcted where at least some vegetation was found in non-compliant condition - total | NA | NA | NA | NA | 2645 | 132 | 568 | 1511 | 924 | 403 | 444 | 550 | 389 |  |  |  |  | # of spans inspected with noncompliant clearance based on applicable rules and regulations at the time of inspection | Prior to July 2019, SCE's work management system did not track the reason why a tree was trimmed, just that trimming was required. In other words, a tree may have been trimmed because it was nearing the regulatory clearance distance (RCD) or because it was inside the RCD. Starting in July of 2019, SCE implemented a new work management system that required inspectors to document whether the tree was found inside the RCD, or other SCE program distances related to clearance which exceed RCD clearance. The historical numbers were updated as a calculation error was discovered.
| 2.a.ii | Number of spans insepcted for vegetation compliance - total | NA | NA | NA | NA | 130934 | 37783 | 58595 | 69975 | 73341 | 67137 | 60876 | 75316 | 48662 |  |  |  |  | # of spans inspected for vegetation compliance | SCE tracks completed vegetation compliance inspections by circuit miles. In order to present completed vegetation compliance inspections in the requested format, SCE divided the recorded circuit miles inspected by the calculated average span length. The historical numbers were updated as a calculation error was discovered.
2. Vegetation clearance findings from inspection - in HFTD | 2.b.i | Number of spans insepcted where at least some vegetation was found in non-compliant condition in HFTD | NA | NA | NA | NA | 1446 | 88 | 368 | 835 | 659 | 282 | 324 | 343 | 256 |  |  |  |  | # of spans inspected with noncompliant clearance based on applicable rules and regulations at the time of inspection | SCE tracks findings by count and does not record specific data that associate the findings to a specific span. Therefore SCE is unable to understand how many findings are on each span. The number being presented are just the counts of findings. The historical numbers were updated as a calculation error was discovered.
| 2.b.ii | Number of spans insepcted for vegetation compliance in HFTD | NA | NA | NA | NA | 69496 | 24536 | 35702 | 35104 | 49555 | 41422 | 39056 | 41354 | 26145 |  |  |  |  | # of spans inspected for vegetation compliance | SCE tracks completed vegetation compliance inspections by circuit miles. In order to present completed vegetation compliance inspections in the requested format, SCE divided the recorded circuit miles inspected by the calculated average span length. The historical numbers were updated as a calculation error was discovered.
3. Community outreach metrics | 3.a. | # Customers in an evacuation zone for utility-ignited wildfire | NA | NA | NA | NA | NA | [12 empty] | # customers (if customer was in an evacuation zone for multiple wildfires, count the customer for each relevant wildfire) | SCE has no jurisdiction over evacuation orders. SCE diligently requested and followed up with local governments and law enforcement, and was only able to obtain information from one county. Even then, the information provided included high-level estimations of evacuation counts estimated by the local government and law enforcement entity for a limited amount of fires. Because of this, SCE is unable to obtain the requested data, analyze it, and report on evacuation related requirements in this table. SCE anticipates this to be a recurring challenge going forward. | bar: 1 to 4
| 3.b. | # Customers notified of evacuation orders | NA | NA | NA | NA | NA | [12 empty] | # customers (count customer multiple times for each unique wildfire of which they were notified) | SCE has no jurisdiction over evacuation orders. SCE diligently requested and followed up with local governments and law enforcement, and was only able to obtain information from one county. Even then, the information provided included high-level estimations of evacuation counts estimated by the local government and law enforcement entity for a limited amount of fires. Because of this, SCE is unable to obtain the requested data, analyze it, and report on evacuation related requirements in this table. SCE anticipates this to be a recurring challenge going forward. | bar: 1 to 4
| 3.c. | % of customers notified of evacuation in evacuation zone of a utility-ignited wildfire | NA | NA | NA | NA | NA | [12 empty] | Percentage of customers notified of evacuation | SCE has no jurisdiction over evacuation orders. SCE diligently requested and followed up with local governments and law enforcement, and was only able to obtain information from one county. Even then, the information provided included high-level estimations of evacuation counts estimated by the local government and law enforcement entity for a limited amount of fires. Because of this, SCE is unable to obtain the requested data, analyze it, and report on evacuation related requirements in this table. SCE anticipates this to be a recurring challenge going forward. | bar: 1 to 4
Table 1 Sub Metrics:
1. Grid condition findings from inspection - Distribution lines in HFTD | 1.b. | Number of circuit miles inspected from detailed inspections in HFTD - Distribution lines (Subtotals) | bar: 1 to 4
|  | Overhead Detailed Inspections | 1869 | 2324 | 1984 | 1566 | 1846 | 515 | 1348 | 48 | 3 | 649 | 289 | 45 | 12 | [5 empty] | From 2015-2019, the number represents the completed detailed inspections completed in circuit miles. Starting in 2020, the numbers represent completed compliance-due detailed inspections by circuit miles. SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected.
|  | Enhanced Overhead Inspections | NA | NA | NA | 859 | 8642 | [13 empty] | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. | bar: 1 to 4
|  | High Fire Risk Informed Inspections | NA | NA | NA | NA | NA | 1195 | 762 | 1757 | 1065 | 2967 | 1835 | 316 | 7 | [5 empty] | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected.
|  | Aerial Inspections | NA | NA | NA | NA | 3861 | 2427 | 2427 | 2427 | 2427 | 215 | 3347 | 2401 | 78 | [5 empty] | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. Additionally, for 2020, SCE tracked the completed asset inspected by the year and in order to represent the 2020 completed asset inspection in circuit mile by quarter, SCE evenly distributed the completed inspections to each of the four quarters in 2020.
| 1.c. | Number of circuit miles inspected from other inspections (list types of "other" inspections in comments) in HFTD - Distribution lines (Subtotals) | bar: 1 to 4
|  | Infrared Scan | NA | NA | NA | 11775 | 4962 | 1112 | 1112 | 1112 | 1112 | 2465 | 1945 | 0 | 0 | [5 empty] | For 2020, SCE tracks the completed asset inspected by year and in order to represent the 2020 completed asset inspection by quarter, SCE evenly distributed the completed inspections to each of the four quarters in 2020.
|  | Intrusive Pole Inspections | 1080 | 1127 | 1023 | 830 | 701 | 271 | 271 | 271 | 271 | 83 | 238 | 258 | 339 | [5 empty] | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. Additionally, for 2020, SCE tracked the completed asset inspected by year and in order to represent the 2020 completed asset inspection by quarter, SCE evenly distributed the completed inspections to each of the four quarters in 2020.
1. Grid condition findings from inspection - Distribution lines total | 1.b.ii. | Number of total circuit miles inspected from detailed inspections - Distribution lines (Subtotals) | bar: 1 to 4
|  | Overhead Detailed Inspections | 7950 | 8034 | 7865 | 7851 | 7956 | 851 | 2343 | 1743 | 3104 | 912 | 1359 | 2309 | 2284 | [5 empty] | From 2015-2019, the number represents the completed detailed inspections completed in circuit miles. Starting in 2020, the numbers represent completed compliance-due detailed inspections by circuit miles. SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected.
|  | Enhanced Overhead Inspections | NA | NA | NA | 1218 | 12242 | [13 empty] | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. | bar: 1 to 4
|  | High fire Risk Informed Inspections | NA | NA | NA | NA | NA | 1199 | 770 | 1768 | 1073 | 3201 | 1967 | 408 | 17 | [5 empty] | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected.
|  | Aerial Inspections | NA | NA | NA | NA | 3861 | 2427 | 2427 | 2427 | 2427 | 215 | 3347 | 2401 | 78 | [5 empty] | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. Additionally, for 2020, SCE tracked the completed asset inspected by the year and in order to represent the 2020 completed asset inspection in circuit mile by quarter, SCE evenly distributed the completed inspections to each of the four quarters in 2020.
| 1.c.ii. | Number of total circuit miles inspected from other inspections (list types of "other" inspections in comments) - Distribution lines | bar: 1 to 4
|  | Infrared Scan | NA | NA | NA | 26055 | 4962 | 1112 | 1112 | 1112 | 1112 | 2465 | 1945 | 0 | 0 | [5 empty] | For 2020, SCE tracks the completed asset inspected by the year and in order to represent the 2020 completed asset inspection by quarter, SCE just evenly distributed the completed inspections to each of the four quarters in 2020.
|  | Intrusive Pole Inspections | 4320 | 4509 | 4093 | 3847 | 3925 | 995 | 995 | 995 | 995 | 993 | 1041 | 1092 | 876 | [5 empty] | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. Additionally, for 2020, SCE tracked the completed asset inspected by the year and in order to represent the 2020 completed asset inspection by quarter, SCE just evenly distributed the completed inspections to each of the four quarters in 2020.
1. Grid condition findings from inspection - Transmission lines in HFTD | 1.b.iii. | Number of circuit miles inspected from detailed inspections in HFTD - Transmission lines | bar: 1 to 4
|  | Detailed Inspections | NA | NA | NA | 1479 | 1479 | 370 | 370 | 370 | 370 | 311 | 323 | 734 | 423 | [5 empty] | For 2015-2017, patrol inspections doubled as detailed inspections being completed on every transmission asset in the service territory. Beginning in 2018 the recorded inspection numbers estimate the detail inspections in circuit miles being completed. Additionally, the detailed inspection program completes inspections of 1/3 of all SCE transmission assets per year. The completed inspections are tracked by "Grids". SCE's complete transmission line network is broken out into large areas called "Grids" and all execution and tracking are recorded at the grid level. The number being represented uses 1/3rd of the current transmission circuit mile counts in HFTD for each year. 2020 in particular, evenly distributes the 1/3rd of the current transmission mile circuit counts into each quarter. An error was found in the calculation methodology for the historical years, therefore the outlined methodology was properly applied and the historical numbers were updated.
|  | High Fire Inspections | NA | NA | NA | NA | 4948 | 839 | 2649 | 404 | 392 | 577 | 1439 | 497 | 0 | [5 empty] | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. A correction was made to the Q1 value as it incorrectly included some Q2 inspections.
|  | Aerial Inspections | NA | NA | NA | NA | 4630 | 868 | 868 | 868 | 868 | 546 | 1509 | 357 | 29 | [5 empty] | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. Additionally, for 2020, SCE tracked the completed asset inspected by the year and in order to represent the 2020 completed asset inspection by quarter, just evenly distributed the completed inspections to each of the four quarters in 2020.
| 1.c.iii | Number of total circuit miles inspected from other inspections (list types of "other" inspections in comments) - Transmission lines (SubTotals) | bar: 1 to 4
|  | IR Corona | NA | NA | NA | NA | 4901 | 251 | 251 | 251 | 251 | 0 | 73 | 380 | 594 | [5 empty] | For 2020, SCE tracked the completed inspections by the year. In order to represent the 2020 completed inspection by quarter, SCE evenly distributed the completed inspections to each of the four quarters evenly in 2020.
|  | Intrusive Pole Inspections | NA | NA | NA | 103 | 102 | 32 | 32 | 32 | 32 | 43 | 49 | 26 | 64 | [5 empty] | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. Additionally, for 2020, SCE tracked the completed asset inspected by the year and in order to represent the 2020 completed asset inspection by quarter, SCE just evenly distributed the completed inspections to each of the four quarters in 2020.
1. Grid condition findings from inspection - Transmission lines total | 1.b.iv. | Number of total circuit miles inspected from detailed inspections - Transmission lines | bar: 1 to 4
|  | Detailed Inspections | NA | NA | NA | 4210 | 4760 | 697 | 1188 | 1229 | 983 | 834 | 990 | 1101 | 868 | [5 empty] | For 2015-2017, patrol inspections doubled as detailed inspections being completed on every transmission asset in the service territory. Beginning in 2018 the recorded inspection numbers estimate the detail inspections in circuit miles being completed. Additionally, the detailed inspection program completes inspections of 1/3 of all SCE transmission assets per year. The completed inspections are tracked by "Grids". SCE's complete transmission line network is broken out into large areas called "Grids" and all execution and tracking are recorded at the grid level. The number being represented uses 1/3rd of the current transmission circuit mile counts in HFTD for each year. 2020 in particular, evenly distributes the 1/3rd of the current transmission mile circuit counts into each quarter.
|  | High Fire Inspections | NA | NA | NA | NA | 4948 | 839 | 2649 | 404 | 392 | 577 | 1439 | 497 | 0 | [5 empty] | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. A correction was made to the Q1 value as it incorrectly included some Q2 inspections.
|  | Aerial Inspections | NA | NA | NA | NA | 1109 | 911 | 911 | 911 | 911 | 546 | 1509 | 357 | 29 | [5 empty] | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. Additionally, for 2020, SCE tracked the completed asset inspected by the year and in order to represent the 2020 completed asset inspection by quarter, just evenly distributed the completed inspections to each of the four quarters in 2020.
| 1.c.iv. | Number of total circuit miles inspected from other inspections (list types of "other" inspections in comments) - Transmission lines | bar: 1 to 4
|  | IR Corona | 0 | 0 | 0 | 0 | 0 | 43 | 43 | 43 | 43 | 0 | 73 | 380 | 594 | [5 empty] | For 2020, SCE tracked the completed inspections by the year. In order to represent the 2020 completed inspection by quarter, SCE evenly distributed the completed inspections to each of the four quarters evenly in 2020.
|  | Intrusive Pole Inspections | 6460 | 4592 | 6226 | 7309 | 5529 | 1594 | 1594 | 1594 | 1594 | 267 | 1993 | 182 | 173 | [5 empty] | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. Additionally, for 2020, SCE tracked the completed asset inspected by the year and in order to represent the 2020 completed asset inspection by quarter, SCE just evenly distributed the completed inspections to each of the four quarters in 2020.

## Table 2
Utility | Southern California Edison Company | Notes:
Table No. | 2 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.
Date Modified | 2022-02-11 | HWW = High wind warning
RFW = Red flag warning
Note: These columns are placeholders for future QR submissions.
Table 2: Recent performance on outcome metrics | [9 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Outcome metric name | Wind Warning Status | HFTD Tier | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
1. Risk Events | 1.a. | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | All | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Number per year
|  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | RFW | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW & RFW | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW & not RFW | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | All | 2 | 886 | 1047 | 1196 | 1116 | 1783 | 322 | 321 | 414 | 292 | 303 | 286 | 283 | 291
|  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | RFW | 2 | 6 | 27 | 67 | 53 | 15 | 0 | 5 | 24 | 48 | 26 | 6 | 0 | 6
|  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW | 2 | 53 | 51 | 86 | 32 | 64 | 36 | 7 | 0 | 32 | 36 | 2 | 0 | 12
|  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW & RFW | 2 | 0 | 7 | 30 | 16 | 1 | 0 | 0 | 0 | 32 | 15 | 2 | 0 | 4
|  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW & not RFW | 2 | 53 | 46 | 64 | 18 | 64 | 40 | 8 | 0 | 5 | 24 | 0 | 0 | 8
|  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | All | 3 | 1342 | 1676 | 1779 | 1691 | 2972 | 381 | 467 | 556 | 469 | 466 | 329 | 388 | 456
|  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | RFW | 3 | 4 | 74 | 169 | 141 | 86 | 0 | 7 | 24 | 89 | 62 | 2 | 0 | 16
|  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW | 3 | 59 | 91 | 156 | 47 | 81 | 43 | 7 | 0 | 39 | 86 | 1 | 0 | 11
|  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW & RFW | 3 | 0 | 17 | 87 | 32 | 26 | 0 | 1 | 0 | 40 | 54 | 0 | 0 | 4
|  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW & not RFW | 3 | 59 | 74 | 69 | 17 | 55 | 43 | 6 | 0 | 0 | 32 | 1 | 0 | 7
|  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | All | Non- HFTD | 9872 | 11602 | 12410 | 13166 | 13154 | 2498 | 3036 | 4545 | 2932 | 2862 | 3025 | 3130 | 3192
|  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | RFW | Non- HFTD | 35 | 235 | 598 | 479 | 240 | 0 | 28 | 167 | 463 | 189 | 18 | 0 | 224
|  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW | Non- HFTD | 128 | 352 | 653 | 311 | 268 | 122 | 19 | 0 | 292 | 297 | 14 | 0 | 187
|  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW & RFW | Non- HFTD | 0 | 68 | 198 | 183 | 70 | 0 | 4 | 0 | 294 | 118 | 12 | 0 | 116
|  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW & not RFW | Non- HFTD | 128 | 283 | 459 | 127 | 198 | 122 | 15 | 0 | 0 | 179 | 2 | 0 | 71
1. Risk Events | 1.b. | Number of wires down | All | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Number of wires down per year
|  | Number of wires down | RFW | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of wires down | HWW | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of wires down | HWW & RFW | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of wires down | HWW & not RFW | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of wires down | All | 2 | 104 | 168 | 194 | 117 | 155 | 28 | 29 | 21 | 34 | 46 | 30 | 29 | 38
|  | Number of wires down | RFW | 2 | 0 | 1 | 6 | 3 | 0 | 0 | 0 | 2 | 7 | 2 | 0 | 0 | 0
|  | Number of wires down | HWW | 2 | 10 | 5 | 10 | 1 | 4 | 5 | 2 | 0 | 3 | 3 | 0 | 0 | 0
|  | Number of wires down | HWW & RFW | 2 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | 0 | 0
|  | Number of wires down | HWW & not RFW | 2 | 10 | 5 | 7 | 1 | 4 | 5 | 2 | 0 | 0 | 2 | 0 | 0 | 0
|  | Number of wires down | All | 3 | 173 | 328 | 377 | 221 | 254 | 49 | 69 | 60 | 58 | 96 | 33 | 35 | 91
|  | Number of wires down | RFW | 3 | 0 | 17 | 25 | 15 | 16 | 0 | 1 | 4 | 19 | 17 | 0 | 0 | 3
|  | Number of wires down | HWW | 3 | 10 | 17 | 29 | 6 | 8 | 4 | 4 | 0 | 7 | 18 | 0 | 0 | 1
|  | Number of wires down | HWW & RFW | 3 | 0 | 4 | 12 | 2 | 2 | 0 | 0 | 0 | 7 | 13 | 0 | 0 | 1
|  | Number of wires down | HWW & not RFW | 3 | 10 | 13 | 17 | 4 | 6 | 4 | 4 | 0 | 0 | 5 | 0 | 0 | 0
|  | Number of wires down | All | Non- HFTD | 1252 | 1888 | 2006 | 1415 | 1376 | 318 | 441 | 444 | 515 | 487 | 425 | 339 | 407
|  | Number of wires down | RFW | Non- HFTD | 3 | 50 | 87 | 47 | 26 | 0 | 5 | 15 | 83 | 41 | 3 | 0 | 35
|  | Number of wires down | HWW | Non- HFTD | 25 | 68 | 105 | 33 | 26 | 18 | 3 | 0 | 54 | 45 | 3 | 0 | 22
|  | Number of wires down | HWW & RFW | Non- HFTD | 0 | 16 | 31 | 20 | 8 | 0 | 1 | 0 | 54 | 24 | 2 | 0 | 16
|  | Number of wires down | HWW & not RFW | Non- HFTD | 25 | 52 | 74 | 13 | 18 | 18 | 2 | 0 | 0 | 21 | 1 | 0 | 6
1. Risk Events | 1.c. | Number of outage events not caused by contact with vegetation | All | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Number of outage events per year
|  | Number of outage events not caused by contact with vegetation | RFW | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of outage events not caused by contact with vegetation | HWW | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of outage events not caused by contact with vegetation | HWW & RFW | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of outage events not caused by contact with vegetation | HWW & not RFW | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of outage events not caused by contact with vegetation | All | 2 | 733 | 807 | 918 | 938 | 1564 | 277 | 279 | 384 | 247 | 245 | 241 | 247 | 241
|  | Number of outage events not caused by contact with vegetation | RFW | 2 | 6 | 25 | 57 | 41 | 14 | 0 | 5 | 22 | 34 | 21 | 6 | 0 | 6
|  | Number of outage events not caused by contact with vegetation | HWW | 2 | 39 | 46 | 76 | 31 | 60 | 31 | 5 | 0 | 29 | 33 | 2 | 0 | 12
|  | Number of outage events not caused by contact with vegetation | HWW & RFW | 2 | 0 | 7 | 25 | 14 | 1 | 0 | 0 | 0 | 24 | 12 | 2 | 0 | 4
|  | Number of outage events not caused by contact with vegetation | HWW & not RFW | 2 | 39 | 39 | 51 | 17 | 59 | 31 | 5 | 0 | 5 | 21 | 0 | 0 | 8
|  | Number of outage events not caused by contact with vegetation | All | 3 | 1076 | 1207 | 1257 | 1388 | 2557 | 303 | 366 | 482 | 385 | 349 | 283 | 337 | 327
|  | Number of outage events not caused by contact with vegetation | RFW | 3 | 4 | 51 | 115 | 116 | 64 | 0 | 5 | 20 | 61 | 41 | 2 | 0 | 11
|  | Number of outage events not caused by contact with vegetation | HWW | 3 | 42 | 62 | 99 | 37 | 62 | 26 | 2 | 0 | 29 | 62 | 1 | 0 | 10
|  | Number of outage events not caused by contact with vegetation | HWW & RFW | 3 | 0 | 13 | 58 | 27 | 22 | 0 | 1 | 0 | 29 | 37 | 0 | 0 | 3
|  | Number of outage events not caused by contact with vegetation | HWW & not RFW | 3 | 42 | 49 | 41 | 10 | 40 | 26 | 1 | 0 | 0 | 25 | 1 | 0 | 7
|  | Number of outage events not caused by contact with vegetation | All | Non- HFTD | 8254 | 9274 | 9910 | 11374 | 11361 | 2106 | 2513 | 4058 | 2312 | 2286 | 2541 | 2724 | 2647
|  | Number of outage events not caused by contact with vegetation | RFW | Non- HFTD | 31 | 176 | 468 | 366 | 190 | 0 | 19 | 150 | 343 | 141 | 15 | 0 | 166
|  | Number of outage events not caused by contact with vegetation | HWW | Non- HFTD | 85 | 267 | 467 | 246 | 222 | 97 | 10 | 0 | 209 | 248 | 11 | 0 | 147
|  | Number of outage events not caused by contact with vegetation | HWW & RFW | Non- HFTD | 0 | 47 | 143 | 134 | 49 | 0 | 2 | 0 | 209 | 93 | 10 | 0 | 82
|  | Number of outage events not caused by contact with vegetation | HWW & not RFW | Non- HFTD | 85 | 220 | 329 | 112 | 173 | 97 | 8 | 0 | 0 | 155 | 1 | 0 | 65
1. Risk Events | 1.d. | Number of outage events caused by contact with vegetation | All | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Number of outage events per year
|  | Number of outage events caused by contact with vegetation | RFW | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of outage events caused by contact with vegetation | HWW | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of outage events caused by contact with vegetation | HWW & RFW | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of outage events caused by contact with vegetation | HWW & not RFW | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of outage events caused by contact with vegetation | All | 2 | 35 | 60 | 72 | 45 | 49 | 16 | 6 | 4 | 9 | 11 | 3 | 4 | 9
|  | Number of outage events caused by contact with vegetation | RFW | 2 | 0 | 1 | 4 | 8 | 1 | 0 | 0 | 0 | 7 | 3 | 0 | 0 | 0
|  | Number of outage events caused by contact with vegetation | HWW | 2 | 4 | 2 | 8 | 1 | 1 | 4 | 1 | 0 | 5 | 3 | 0 | 0 | 0
|  | Number of outage events caused by contact with vegetation | HWW & RFW | 2 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 5 | 2 | 0 | 0 | 0
|  | Number of outage events caused by contact with vegetation | HWW & not RFW | 2 | 4 | 2 | 6 | 0 | 1 | 4 | 1 | 0 | 0 | 1 | 0 | 0 | 0
|  | Number of outage events caused by contact with vegetation | All | 3 | 61 | 112 | 122 | 61 | 138 | 27 | 17 | 3 | 19 | 15 | 2 | 5 | 37
|  | Number of outage events caused by contact with vegetation | RFW | 3 | 0 | 4 | 27 | 9 | 6 | 0 | 0 | 0 | 9 | 4 | 0 | 0 | 2
|  | Number of outage events caused by contact with vegetation | HWW | 3 | 7 | 12 | 28 | 4 | 11 | 13 | 1 | 0 | 3 | 6 | 0 | 0 | 0
|  | Number of outage events caused by contact with vegetation | HWW & RFW | 3 | 0 | 0 | 17 | 1 | 2 | 0 | 0 | 0 | 3 | 4 | 0 | 0 | 0
|  | Number of outage events caused by contact with vegetation | HWW & not RFW | 3 | 7 | 12 | 11 | 3 | 9 | 13 | 1 | 0 | 0 | 2 | 0 | 0 | 0
|  | Number of outage events caused by contact with vegetation | All | Non- HFTD | 305 | 385 | 424 | 305 | 331 | 61 | 46 | 15 | 83 | 66 | 16 | 23 | 123
|  | Number of outage events caused by contact with vegetation | RFW | Non- HFTD | 0 | 9 | 43 | 63 | 22 | 0 | 4 | 1 | 36 | 7 | 0 | 0 | 23
|  | Number of outage events caused by contact with vegetation | HWW | Non- HFTD | 18 | 16 | 80 | 31 | 20 | 7 | 6 | 0 | 29 | 4 | 0 | 0 | 18
|  | Number of outage events caused by contact with vegetation | HWW & RFW | Non- HFTD | 0 | 5 | 24 | 29 | 13 | 0 | 1 | 0 | 29 | 1 | 0 | 0 | 18
|  | Number of outage events caused by contact with vegetation | HWW & not RFW | Non- HFTD | 18 | 11 | 56 | 2 | 7 | 7 | 5 | 0 | 0 | 3 | 0 | 0 | 0
2. Utility inspection findings - Distribution | 2.a. | Number of Level 1 findings (distribution) | N/A | 1 | 15 | 12 | 16 | 12 | 6 | 0 | 2 | 0 | 2 | 2 | 1 | 0 | 2
|  | Number of Level 1 findings (distribution) | N/A | 2 | 929 | 1082 | 1175 | 976 | 1632 | 374 | 312 | 291 | 335 | 344 | 289 | 217 | 235
|  | Number of Level 1 findings (distribution) | N/A | 3 | 1469 | 2828 | 2249 | 2008 | 3142 | 508 | 536 | 725 | 660 | 518 | 413 | 401 | 508
|  | Number of Level 1 findings (distribution) | N/A | Non- HFTD | 17145 | 18440 | 20157 | 18003 | 19248 | 3970 | 4736 | 5966 | 4627 | 4403 | 4242 | 4544 | 4757
| 2.b. | Number of Level 2 findings (distribution) | N/A | 1 | 121 | 107 | 96 | 52 | 35 | 8 | 6 | 1 | 1 | 1 | 0 | 2 | 1
|  | Number of Level 2 findings (distribution) | N/A | 2 | 5721 | 5262 | 3827 | 6733 | 29877 | 4024 | 4294 | 2215 | 1570 | 5167 | 6178 | 1349 | 1100
|  | Number of Level 2 findings (distribution) | N/A | 3 | 12479 | 11995 | 9909 | 16884 | 53386 | 8446 | 7987 | 5181 | 5123 | 6483 | 9440 | 4469 | 1535
|  | Number of Level 2 findings (distribution) | N/A | Non- HFTD | 74077 | 62647 | 55980 | 59449 | 66075 | 10747 | 12328 | 14940 | 17926 | 9678 | 16907 | 26730 | 32003
| 2.c. | Number of Level 3 findings (distribution) | N/A | 1 | 29 | 24 | 7 | 19 | 22 | 2 | 1 | 2 | 0 | 0 | 0 | 3 | 0
|  | Number of Level 3 findings (distribution) | N/A | 2 | 4866 | 7847 | 5092 | 5211 | 43687 | 3404 | 4122 | 3307 | 393 | 7342 | 3849 | 461 | 446
|  | Number of Level 3 findings (distribution) | N/A | 3 | 9472 | 10076 | 7664 | 8564 | 65707 | 6743 | 6257 | 6834 | 710 | 7013 | 5509 | 1605 | 305
|  | Number of Level 3 findings (distribution) | N/A | Non- HFTD | 70636 | 56353 | 51253 | 58499 | 78733 | 3887 | 8643 | 13668 | 19643 | 3938 | 9864 | 18938 | 19068
| 2.d. | Number of distribution circuit miles inspected | N/A | 1 | 36 | 37 | 33 | 809 | 298 | 115 | 116 | 114 | 114 | 83 | 166 | 80 | 13 | [5 empty] | 2021 year-end data is going through final quality assurance review and if any changes are needed, they will be updated in the next quarterly submission.
|  | Number of distribution circuit miles inspected | N/A | 2 | 4824 | 5303 | 4951 | 13193 | 10819 | 2127 | 4890 | 2265 | 1510 | 4016 | 4651 | 979 | 143 | [5 empty] | 2021 year-end data is going through final quality assurance review and if any changes are needed, they will be updated in the next quarterly submission.
|  | Number of distribution circuit miles inspected | N/A | 3 | 7808 | 7835 | 7748 | 25038 | 18626 | 4872 | 7848 | 4471 | 3487 | 5988 | 8732 | 2915 | 281 | [5 empty] | 2021 year-end data is going through final quality assurance review and if any changes are needed, they will be updated in the next quarterly submission.
|  | Number of distribution circuit miles inspected | N/A | Non- HFTD | 39797 | 39567 | 39424 | 40137 | 43410 | 2516 | 18954 | 11947 | 6318 | 3117 | 10755 | 18474 | 7137 | [5 empty] | 2021 year-end data is going through final quality assurance review and if any changes are needed, they will be updated in the next quarterly submission.
2. Utility inspection findings - Transmission | 2.a.ii | Number of Level 1 findings (transmission) | N/A | 1 | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4
|  | Number of Level 1 findings (transmission) | N/A | 2 | 27 | 22 | 24 | 12 | 80 | 8 | 13 | 31 | 42 | 15 | 29 | 17 | 9
|  | Number of Level 1 findings (transmission) | N/A | 3 | 20 | 59 | 15 | 20 | 33 | 10 | 8 | 23 | 21 | 15 | 30 | 28 | 8
|  | Number of Level 1 findings (transmission) | N/A | Non- HFTD | 193 | 174 | 172 | 148 | 192 | 40 | 30 | 54 | 45 | 38 | 49 | 28 | 57
| 2.b.ii | Number of Level 2 findings (transmission) | N/A | 1 | 1 | 1 | 447 | 0 | 4 | 1 | 2 | 3 | 1 | 0 | 0 | 3 | 0
|  | Number of Level 2 findings (transmission) | N/A | 2 | 595 | 566 | 929 | 1091 | 9705 | 1025 | 3283 | 1126 | 470 | 391 | 881 | 362 | 108
|  | Number of Level 2 findings (transmission) | N/A | 3 | 389 | 445 | 2 | 560 | 5856 | 818 | 3565 | 978 | 660 | 489 | 1303 | 577 | 160
|  | Number of Level 2 findings (transmission) | N/A | Non- HFTD | 4369 | 4207 | 5033 | 5367 | 7322 | 1399 | 1177 | 888 | 1031 | 1300 | 888 | 730 | 607
| 2.c.ii | Number of Level 3 findings (transmission) | N/A | 1 | 3 | 0 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of Level 3 findings (transmission) | N/A | 2 | 641 | 550 | 323 | 178 | 1507 | 109 | 371 | 297 | 96 | 417 | 377 | 123 | 21
|  | Number of Level 3 findings (transmission) | N/A | 3 | 270 | 172 | 0 | 176 | 1069 | 76 | 416 | 386 | 175 | 399 | 438 | 128 | 21
|  | Number of Level 3 findings (transmission) | N/A | Non- HFTD | 6105 | 2623 | 2374 | 1349 | 2493 | 599 | 454 | 321 | 352 | 232 | 257 | 143 | 322
| 2.d.ii | Number of transmission circuit miles inspected | N/A | 1 | 194 | 138 | 187 | 219 | 1346 | 76 | 76 | 76 | 76 | 24 | 107 | 28 | 24
|  | Number of transmission circuit miles inspected | N/A | 2 | 2459 | 1861 | 2384 | 2857 | 4500 | 1489 | 2406 | 1110 | 1032 | 603 | 2053 | 665 | 355
|  | Number of transmission circuit miles inspected | N/A | 3 | 4852 | 3638 | 4700 | 5615 | 7035 | 2098 | 3035 | 2125 | 2170 | 882 | 3150 | 1066 | 684
|  | Number of transmission circuit miles inspected | N/A | Non- HFTD | 12023 | 12023 | 12023 | 15896 | 16533 | 3688 | 4134 | 4137 | 3910 | 2472 | 2896 | 3594 | 3103
| 3.a. | Fatalities due to utility-related ignitions (total) | N/A | N/A | 0 | 0 | 2 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3.b. | Injuries due to utility-related igntions (total) | N/A | N/A | 0 | 3 | 2 | 3 | 3 | 0 | 0 | 6 | 2 | 0 | 0 | 0 | 0
4. Value of assets destroyed by utility-related ignitions, listed by asset type | 4.a. | Value of assets destroyed by utility-related ignitions (total) | N/A | N/A | 21944989 | 483632927 | 1601205795 | 3342821539 | 21714000 | 150400 | 300800 | 120688284 | 12082300 | 188000 | 451200 | 2739090 | 338400
5. Structures damaged or destroyed by utility-related ignitions | 5.a. | Number of structures destroyed by utility-related ignitions (total) | N/A | N/A | 45 | 290 | 1072 | 1667 | 26 | 0 | 0 | 47 | 13 | 0 | 0 | 0 | 0
| 5.b. | Critical infrastructure damaged/destroyed by utility-rleated ignitions (total) | N/A | N/A | NA | NA | 36 | 31 | NA | bar: 1 to 4
6. Acreage burned by utility-related ignitions | 6.a. | Acreage burned by utility-rleated ignitions | N/A | N/A | 15711 | 82897 | 292051 | 97240 | 22784 | 4 | 574 | 115871 | 12863 | 12 | 513 | 30 | 41
7. Number of utility-related ignitions | 7.a. | Number of ignitions (total) according to existing ignition data reporting requirement | N/A | N/A | 107 | 96 | 105 | 109 | 124 | 16 | 58 | 44 | 31 | 29 | 66 | 58 | 18
| 7.b. | Number of ignitions | All | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of ignitions | RFW | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of ignitions | HWW | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of ignitions | HWW & RFW | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of ignitions | HWW & not RFW | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of ignitions | All | 2 | 14 | 12 | 12 | 16 | 15 | 1 | 7 | 5 | 2 | 1 | 12 | 3 | 3
|  | Number of ignitions | RFW | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of ignitions | HWW | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of ignitions | HWW & RFW | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of ignitions | HWW & not RFW | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of ignitions | All | 3 | 32 | 29 | 23 | 21 | 23 | 2 | 15 | 11 | 7 | 6 | 11 | 11 | 1
|  | Number of ignitions | RFW | 3 | 0 | 2 | 2 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of ignitions | HWW | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of ignitions | HWW & RFW | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
|  | Number of ignitions | HWW & not RFW | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of ignitions | All | Non- HFTD | 61 | 55 | 70 | 72 | 86 | 13 | 36 | 28 | 22 | 23 | 43 | 44 | 15
|  | Number of ignitions | RFW | Non- HFTD | 1 | 0 | 0 | 3 | 2 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0
|  | Number of ignitions | HWW | Non- HFTD | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of ignitions | HWW & RFW | Non- HFTD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0
|  | Number of ignitions | HWW & not RFW | Non- HFTD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8. Fatalities resulting from utility wildfire mitigation initiatives | 8.a. | Fatalities due to utility wildfire mitigation activities (total) - "activities" defined as all activities accounted for in the 2020 WMP proposed WMP spend | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9. OSHA-reportable injuries from utility wildfire mitigation initiatives | 9.a. | OSHA-reportable injuries due to utility wildfire mitigation activities (total) - "activities" defined as all activities accounted for in the 2020 WMP proposed WMP spend | N/A | N/A | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 3 | 0 | 0 | 1 | 0 | 0
Table 2 Sub Metrics:
1. Risk Events | 1.b. | Number of wires down | Unknown | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of wires down | Unknown | 2 | 9 | 35 | 25 | 13 | 13 | 0 | 0 | 1 | 1 | 3 | 2 | 0 | 2
|  | Number of wires down | Unknown | 3 | 8 | 70 | 71 | 34 | 18 | 3 | 6 | 2 | 1 | 3 | 2 | 5 | 3
|  | Number of wires down | Unknown | Non- HFTD | 33 | 285 | 183 | 98 | 59 | 4 | 6 | 11 | 12 | 20 | 25 | 28 | 10
|  | Number of wires down | Unknown | Unknown | 3 | 30 | 40 | 7 | 5 | 1 | 0 | 0 | 2 | 0 | 0 | 1 | 0
1. Risk Events | 1.c. | Number of outage events not caused by contact with vegetation | Unknown | Unknown | 1824 | 511 | 482 | 504 | 747 | 113 | 142 | 124 | 114 | 119 | 124 | 108 | 165
1. Risk Events | 1.d. | Number of outage events caused by contact with vegetation | Unknown | Unknown | 9 | 16 | 4 | 14 | 17 | 0 | 1 | 4 | 5 | 3 | 0 | 1 | 6

## Table 3
Utility | Southern California Edison Company
Table No. | 3
Date Modified | 2022-02-11
Note: These columns are placeholders for future QR submissions.
Table 3: List and description of additional metrics | [9 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric | Definition | Purpose | Assumptions made to connect metric to purpose | Third-party validation (if any) | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
CPUC reportable ignitions in High Fire Risk Areas (HFRA) | Events meeting reportable ignition status per Decision 14-02-015 and falling within BL322, HFTD Zone 1 HFTD Tier 2 and 200 ft. Outer Buffer, and HFTD Tier 3 and 200 ft. Outer Buffer areas | To measure changes in rate of ignitions between years | Factors outside of SCE's control (e.g., wind, live fuel moisture) have a significant effect on CPUC reportable ignition counts in HFRA. | Annual submission of CPUC reportable ignition totals to CPUC | 46 | 41 | 35 | 37 | 38 | 3 | 22 | 16 | 9 | 7 | 22 | 9 | 4 |  |  |  |  | Number of reportable ignitions in HFRA | HFRA includes HFTD Tier 3, HFTD Tier 2, HFTD Zone 1, and BL322 (non-CPUC HFRA)
Faults in HFRA | Events in which electrical current deviates from the anticpated path via SCE facilities within BL322, HFTD Zone 1 HFTD Tier 2 and 200 ft. Outer Buffer, and HFTD Tier 3 and 200 ft. Outer Buffer areas | To measure changes in rate of fault events which are a pre-cursor both ignition and safety events | Number of faults in HFRA based on cause. These metrics may help to provide insight on controllable and uncontrollable risks or help plan future activities to focus on a particular type of fault or outage that may be of wildfire risk. | Deep-dive audits of select portions of utility grid | 1905 | 2186 | 2369 | 2432 | 4309 | 623 | 668 | 873 | 660 | 620 | 529 | 593 | 614 |  |  |  |  | Number of faults in HFRA | HFRA includes HFTD Tier 3, HFTD Tier 2, HFTD Zone 1, and BL322 (non-CPUC HFRA). Note: SCE is incorporating additional Transmission outage data as an improvement to its outage reporting. Historical reporting has been revised to reflect the additional Transmission outage data.
Wire Down Incidents in HFRA | Events in which SCE overhead conductors (energized or de-energized) fall within 8ft above ground or lower, within BL322, HFTD Tier 2 and 200 ft. Outer Buffer, and HFTD Tier 3 and 200 ft. Outer Buffer areas | To measure changes in rate of wire down events which are a pre-cursor both ignition and safety events | Number of wire down incidents in HFRA based on cause. These metrics may help to provide insight on controllable and uncontrollable risks or help plan future activities to focus on a particular type of fault or outage that may be of wildfire risk. | Deep-dive audits of select portions of utility grid | 277 | 496 | 571 | 338 | 409 | 77 | 98 | 81 | 92 | 142 | 63 | 64 | 129 |  |  |  |  | Number of wire downs per year in HFRA | HFRA includes HFTD Tier 3, HFTD Tier 2, HFTD Zone 1, and BL322 (non-CPUC HFRA)
Number of customers and average duration of Public Safety Power Shutoff (PSPS) events
Total # of customers de-energized | Count of customers de-energized, with duplicates, per year | To measure the scale of impact of outages due to PSPS to customers, with duplicates | Not Applicable | Not Applicable | Refer to Table 11, # 4.a. | Refer to Table 11, # 4.a. | Refer to Table 11, # 4.a. | Refer to Table 11, # 4.a. | Refer to Table 11, # 4.a. | Refer to Table 11, # 4.a. | Refer to Table 11, # 4.a. | Refer to Table 11, # 4.a. | Refer to Table 11, # 4.a. | Refer to Table 11, # 4.a. | Refer to Table 11, # 4.a. | Refer to Table 11, # 4.a. | Refer to Table 11, # 4.a. |  |  |  |  | Number of customers | None
Average duration of de-energization across all customers. | Average outage duration (hours per customer) experienced by PSPS de-energization per customer de-energized | Of the customers de-energized due to PSPS, to measure the magnitude of the effect of the PSPS de-energization | Not Applicable | Not Applicable | N/A | N/A | 30.3 | 23.2 | 27 | N/A | N/A | 2.2 | 18.3 | 23.9 | 2.9 | 9.8 | 25.03 |  |  |  |  | Hours | Applies to each instance of a customer being de-energized due to PSPS
Timeliness and accuracy of PSPS notifications
% of customers notified prior to a PSPS event impacting them | # of customers notified prior to initiation of PSPS event who were impacted by PSPS/ # of customers impacted by PSPS (if multiple PSPS events impact the same customer, count each event as a separate customer) | To measure success rate of notification for the customers who were impacted by de-energization | Not Applicable | Not Applicable | Refer to Table 11, # 4.e. | Refer to Table 11, # 4.e. | Refer to Table 11, # 4.e. | Refer to Table 11, # 4.e. | Refer to Table 11, # 4.e. | Refer to Table 11, # 4.e. | Refer to Table 11, # 4.e. | Refer to Table 11, # 4.e. | Refer to Table 11, # 4.e. | Refer to Table 11, # 4.e. | Refer to Table 11, # 4.e. | Refer to Table 11, # 4.e. | Refer to Table 11, # 4.e. |  |  |  |  | Percentage | None
% of customers notified prior to a PSPS event that did not impact them | % of customers notified of potential de-energization that were not de-energized for that PSPS event (on a total customer basis) 1 - (# of total customers de-energized / # of imminent de-energization notifications sent) | To measure the occurrence of PSPS notifications and de-energizations | Not Applicable | Not Applicable | N/A | N/A | N/A | N/A | N/A | N/A | 100% | 39% | 61% | 64.6% | 87% | 0% | 25% |  |  |  |  | % of customers notified of imminent potential de-energization that were not de-energized for that PSPS event (on a total customer basis) | This data was not recorded prior to 2020.

## Table 4
Utility | Southern California Edison Company
Table No. | 4
Date Modified | 2022-02-11
Note: These columns are placeholders for future QR submissions.
Table 4: Fatalities due to utility wildfire mitigation initiatives | [7 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Outcome metric name | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
1. Fatalities - Full-time Employee | 1.a. | Fatalities due to utility inspection - Full-time employee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # fatalities
| 1.b. | Fatalities due to vegetation management - Full-time employee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # fatalities
| 1.c. | Fatalities due to utility fuel management - Full-time employee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # fatalities
| 1.d. | Fatalities due to grid hardening - Full-time employee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # fatalities
| 1.e. | Fatalities due to other - Full-time employee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # fatalities
2. Fatalities - Contractor | 2.a. | Fatalities due to utility inspection - Contractor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # fatalities
| 2.b. | Fatalities due to vegetation management - Contractor | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # fatalities | By providing this data, SCE is not admitting: 1) any responsibility or liability for any incident reported herein or 2) that a wildfire mitigation activity caused a fatality.
| 2.c. | Fatalities due to utility fuel management - Contractor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # fatalities
| 2.d. | Fatalities due to grid hardening - Contractor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # fatalities
| 2.e. | Fatalities due to other - Contractor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # fatalities
3. Fatalities - Member of public | 3.a. | Fatalities due to utility inspection - Public | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # fatalities
| 3.b. | Fatalities due to vegetation management - Public | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # fatalities
| 3.c. | Fatalities due to utility fuel management - Public | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # fatalities
| 3.d. | Fatalities due to grid hardening - Public | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # fatalities
| 3.e. | Fatalities due to other - Public | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # fatalities

## Table 5
Utility | Southern California Edison Company
Table No. | 5
Date Modified | 2022-02-11
Note: These columns are placeholders for future QR submissions.
Table 5: OSHA-reportable injuries due to utility wildfire mitigation initiatives | [7 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | -
Metric type | # | Outcome metric name | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
1. OSHA injuries - Full-time Employee | 1.a. | OSHA injuries due to utility inspection - Full-time employee | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # OSHA-reportable injuries | By providing this data, SCE is not admitting that 1) any responsibility or liability for any incident reported herein or 2) that a wildfire mitigation activity caused an injury.
| 1.b. | OSHA injuries due to vegetation management - Full-time employee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # OSHA-reportable injuries
| 1.c. | OSHA injuries due to utility fuel management - Full-time employee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # OSHA-reportable injuries
| 1.d. | OSHA injuries due to grid hardening - Full-time employee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # OSHA-reportable injuries | By providing this data, SCE is not admitting that 1) any responsibility or liability for any incident reported herein or 2) that a wildfire mitigation activity caused an injury.
| 1.e. | OSHA injuries due to other - Full-time employee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # OSHA-reportable injuries
2. OSHA injuries - Contractor | 2.a. | OSHA injuries due to utility inspection - Contractor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # OSHA-reportable injuries
| 2.b. | OSHA injuries due to vegetation management - Contractor | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 |  |  |  |  | # OSHA-reportable injuries | By providing this data, SCE is not admitting that 1) any responsibility or liability for any incident reported herein or 2) that a wildfire mitigation activity caused an injury.
| 2.c. | OSHA injuries due to utility fuel management - Contractor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # OSHA-reportable injuries
| 2.d. | OSHA injuries due to grid hardening - Contractor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # OSHA-reportable injuries | By providing this data, SCE is not admitting that 1) any responsibility or liability for any incident reported herein or 2) that a wildfire mitigation activity caused an injury.
| 2.e. | OSHA injuries due to other - Contractor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # OSHA-reportable injuries
3. OSHA injuries - Member of public | 3.a. | OSHA injuries due to utility inspection - Public | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # OSHA-reportable injuries
| 3.b. | OSHA injuries due to vegetation management - Public | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # OSHA-reportable injuries
| 3.c. | OSHA injuries due to utility fuel management - Public | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # OSHA-reportable injuries
| 3.d. | OSHA injuries due to grid hardening - Public | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # OSHA-reportable injuries
| 3.e. | OSHA injuries due to other - Public | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # OSHA-reportable injuries

## Table 6
Utility | Southern California Edison Company
Table No. | 6
Date Modified | 2022-02-11
Note: These columns are placeholders for future QR submissions.
Table 6: Weather patterns | [7 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Outcome metric name | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
1. Red Flag Warning Overhead circuit mile Days | 1.a. | Red Flag Warning Overhead circuit mile days - entire utility territory | 80503.67 | 286326.53 | 476404.26 | 283806.28 | 201423 | 0 | 24844.84 | 62241.17 | 162421.73 | 58515.1798 | 16825.39 | 5764.5 | 107566.67 |  |  |  |  | Sum of overhead circuit miles of utility grid subject to Red Flag Warning each day within a given time period, calculated as the number of overhead circuit miles that were under an RFW multiplied by the number of days those circuit miles were under said RFW. For example, if 100 overhead circuit miles were under an RFW for 1 day, and 10 of those miles were under RFW for an additional day, then the total RFW OH circuit mile days would be 110. | GIS systems are used in order to overlay the locational information of each red flag warning. GIS models are updated frequently with changes within SCE's service territroy and does not have the ability to analyze and calculate information in previous years. As such, the overhead lengths of distribution and transmission circuits are based on 2020 circuit mile information for the calculation of historical years 2015-2019. Additionally, this overall number may be slightly different than the 2020 WMP filing due to the use of the 2020 GIS information. Historical information was re-calculated as high fire threat district break outs are new requirements in the 2021 WMP.
| 1.b. | Red Flag Warning Overhead circuit mile days - HFTD Zone 1 | 0.75 | 8.01 | 4.14 | 2.78 | 1.74 | 0 | 0.39 | 1.25 | 1.65 | 0.59552 | 0.32 | 0.28 | 0.3 |  |  |  |  | Red Flag Warning Overhead circuit mile days, see above for definition | GIS systems are used in order to overlay the locational information of each red flag warning. GIS models are updated frequently with changes within SCE's service territroy and does not have the ability to analyze and calculate information in previous years. As such, the overhead lengths of distribution and transmission circuits are based on 2020 circuit mile information for the calculation of historical years 2015-2019. Additionally, this overall number may be slightly different than the 2020 WMP filing due to the use of the 2020 GIS information. Historical information was re-calculated as high fire threat district break outs are new requirements in the 2021 WMP.
| 1.c. | Red Flag Warning Overhead circuit mile days - HFTD Tier 2 | 9213.87 | 31921.01 | 50038.98 | 31294.57 | 21597.87 | 0 | 4391.03 | 10010.96 | 17964.31 | 7002.8517 | 3074.07 | 2859.56 | 10162.57 |  |  |  |  | Red Flag Warning Overhead circuit mile days, see above for definition | GIS systems are used in order to overlay the locational information of each red flag warning. GIS models are updated frequently with changes within SCE's service territroy and does not have the ability to analyze and calculate information in previous years. As such, the overhead lengths of distribution and transmission circuits are based on 2020 circuit mile information for the calculation of historical years 2015-2019. Additionally, this overall number may be slightly different than the 2020 WMP filing due to the use of the 2020 GIS information. Historical information was re-calculated as high fire threat district break outs are new requirements in the 2021 WMP.
| 1.d. | Red Flag Warning Overhead circuit mile days - HFTD Tier 3 | 25523.13 | 88117.02 | 127005.19 | 82216.16 | 57321.44 | 0 | 4030.7 | 13919.77 | 36805.02 | 17403.5949 | 1214.14 | 2029.13 | 25933.09 |  |  |  |  | Red Flag Warning Overhead circuit mile days, see above for definition | GIS systems are used in order to overlay the locational information of each red flag warning. GIS models are updated frequently with changes within SCE's service territroy and does not have the ability to analyze and calculate information in previous years. As such, the overhead lengths of distribution and transmission circuits are based on 2020 circuit mile information for the calculation of historical years 2015-2019. Additionally, this overall number may be slightly different than the 2020 WMP filing due to the use of the 2020 GIS information. Historical information was re-calculated as high fire threat district break outs are new requirements in the 2021 WMP.
| 1.e. | Red Flag Warning Overhead circuit mile days - Non-HFTD | 45765.92 | 166280.5 | 299355.96 | 170292.77 | 122501.95 | 0 | 16422.72 | 38309.19 | 107650.74 | 34108.1376 | 12536.87 | 875.53 | 71470.72 |  |  |  |  | Red Flag Warning Overhead circuit mile days, see above for definition | GIS systems are used in order to overlay the locational information of each red flag warning. GIS models are updated frequently with changes within SCE's service territroy and does not have the ability to analyze and calculate information in previous years. As such, the overhead lengths of distribution and transmission circuits are based on 2020 circuit mile information for the calculation of historical years 2015-2019. Additionally, this overall number may be slightly different than the 2020 WMP filing due to the use of the 2020 GIS information. Historical information was re-calculated as high fire threat district break outs are new requirements in the 2021 WMP.
2. Wind conditions | 2.a. | High wind warning overhead circuit mile days | 78964.76 | 116378.06 | 144820.11 | 133880.48 | 95208.03 | 61544.8 | 9235.36 | 61.99 | 57071.56 | 78100.9077 | 10502.66 | 0 | 28925.62 |  |  |  |  | Sum of overhead circuit miles of utility grid subject to High Wind Warnings (HWW, as defined by the National Weather Service) each day within a given time period, calculated as the number of overhead circuit miles that were under an HWW multiplied by the number of days those miles were under said HWW. For example, if 100 overhead circuit miles were under an HWW for 1 day, and 10 of those miles were under HWW for an additional day, then the total HWW OH circuit mile days would be 110. | GIS systems are used in order to overlay the locational information of each red flag warning. GIS models are updated frequently with changes within SCE's service territroy and does not have the ability to analyze and calculate information in previous years. As such, the overhead lengths of distribution and transmission circuits are based on 2020 circuit mile information for the calculation of historical years 2015-2019. Additionally, this overall number may be slightly different than the 2020 WMP filing due to the use of the 2020 GIS information. Historical information was re-calculated as high fire threat district break outs are new requirements in the 2021 WMP.
3. Other | 3.a. | Other relevant weather pattern metrics tracked (add additional rows as needed) | bar: 1 to 4; 2 to 3

## Table 7.1
| Utility | Southern California Edison Company | Notes:
| Table No. | 7.1 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.
| Date Modified | 2022-02-11 | Data from 2015 - 2021 Q4 should be actual numbers. 2022 Q1 - 2024 should be projected. In future submissions update projected numbers with actuals
[6 empty] | Number of risk events | [12 empty] | Projected risk events
| Table 7.1: Key recent and projected drivers of risk events | [9 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
| Risk Event category | Cause category | # | Sub-cause category | Are risk events tracked for ignition driver? (yes / no) | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | 2023 | 2023 | 2023 | 2023 | Unit(s) | Comments
x | Wire down event - Distribution | 1. Contact from object - Distribution | 1.a. | Veg. contact- Distribution | Yes | 279 | 404 | 382 | 158 | 308 | 86 | 103 | 80 | 150 | 113 | 68 | 57 | 133 | 86.3601 | 60.0977 | 60.8892 | 93.2761 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 1.b. | Animal contact- Distribution | Yes | 74 | 59 | 53 | 48 | 38 | 10 | 19 | 28 | 11 | 11 | 13 | 11 | 14 | 12.7331 | 13.3783 | 12.7899 | 13.7709 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 1.c. | Balloon contact- Distribution | Yes | 115 | 113 | 115 | 134 | 98 | 22 | 47 | 27 | 12 | 24 | 48 | 21 | 13 | 24.2749 | 47.4048 | 22.6233 | 13.7262 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 1.d. | Vehicle contact- Distribution | Yes | 227 | 374 | 248 | 267 | 269 | 78 | 121 | 89 | 97 | 80 | 120 | 104 | 100 | 89.7606 | 102.4194 | 98.6233 | 96.8305 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 1.e. | Other contact from object - Distribution | Yes | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.054219 | 0.07062 | 0.064271 | 0.070865 |  |  |  |  | # risk events (excluding ignitions)
|  | 2. Equipment / facility failure - Distribution | 2.a. | Connector damage or failure- Distribution | Yes | 84 | 112 | 81 | 75 | 68 | 25 | 34 | 37 | 19 | 24 | 17 | 22 | 15 | 21.3217 | 19.5424 | 21.4758 | 19.1857 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 2.b. | Splice damage or failure — Distribution | Yes | 35 | 28 | 24 | 24 | 28 | 3 | 10 | 10 | 6 | 11 | 3 | 5 | 6 | 7.7862 | 6.2674 | 6.1981 | 6.2792 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 2.c. | Crossarm damage or failure - Distribution | Yes | 31 | 29 | 26 | 25 | 35 | 10 | 10 | 5 | 9 | 15 | 3 | 3 | 11 | 12.9477 | 4.8219 | 3.6828 | 11.3536 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 2.d. | Insulator damage or failure- Distribution | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 2.e. | Lightning arrestor damage or failure- Distribution | Yes | 0 | 0 | 2 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0.19648 | 0.1829 | 0.4258 | 0.21005 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 2.f. | Tap damage or failure - Distribution | Yes | 0 | 0 | 4 | 5 | 12 | 4 | 3 | 2 | 2 | 5 | 0 | 1 | 2 | 2.9718 | 1.3197 | 1.6492 | 1.9839 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 2.g. | Tie wire damage or failure - Distribution | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 2.h. | Other - Distribution | Yes | 105 | 120 | 141 | 151 | 231 | 53 | 127 | 160 | 144 | 111 | 110 | 97 | 141 | 132.3467 | 132.1197 | 130.0619 | 141.6982 |  |  |  |  | # risk events (excluding ignitions)
|  | 3. Wire-to-wire contact - Distribution | 3.a. | Wire-to-wire contact / contamination- Distribution | Yes | 0 | 0 | 1 | 2 | 1 | 0 | 4 | 2 | 1 | 4 | 0 | 0 | 0 | 1.4751 | 0.18558 | 0.29645 | 0.49665 |  |  |  |  | # risk events (excluding ignitions)
|  | 4. Contamination - Distribution | 4.a. | Contamination - Distribution | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # risk events (excluding ignitions)
|  | 5. Utility work / Operation | 5.a. | Utility work / Operation | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # risk events (excluding ignitions)
|  | 6. Vandalism / Theft - Distribution | 6.a. | Vandalism / Theft - Distribution | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # risk events (excluding ignitions)
|  | 7. Other- Distribution | 7.a. | All Other- Distribution | Yes | 580 | 1154 | 1530 | 863 | 678 | 101 | 58 | 82 | 154 | 231 | 104 | 79 | 99 | 138.2815 | 94.1709 | 86.527 | 92.3761 |  |  |  |  | # risk events (excluding ignitions)
|  | 8. Unknown- Distribution | 8.a. | Unknown - Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # risk events (excluding ignitions)
x | Wire down event - Transmission | 9. Contact from object - Transmission | 9.a. | Veg. contact- Transmission | Yes | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 9.b. | Animal contact- Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 9.c. | Balloon contact- Transmission | Yes | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.0049464 | 0.33821 | 0.017492 | 0.012264 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 9.d. | Vehicle contact- Transmission | Yes | 0 | 3 | 2 | 2 | 8 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0.14512 | 0.17515 | 0.14902 | 0.1355 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 9.e. | Other contact from object - Transmission | Yes | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # risk events (excluding ignitions)
|  | 10. Equipment / facility failure - Transmission | 10.a. | Connector damage or failure- Transmission | Yes | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 10.b. | Splice damage or failure — Transmission | Yes | 0 | 0 | 1 | 3 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0.13774 | 0.10957 | 0.72527 | 0.45358 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 10.c. | Crossarm damage or failure - Transmission | Yes | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 10.d. | Insulator damage or failure- Transmission | Yes | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 10.e. | Lightning arrestor damage or failure- Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 10.f. | Tap damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 10.g. | Tie wire damage or failure - Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 10.h. | Other - Transmission | Yes | 0 | 8 | 2 | 1 | 6 | 0 | 2 | 2 | 1 | 0 | 1 | 1 | 0 | 0.21844 | 0.51184 | 0.4274 | 0.19199 |  |  |  |  | # risk events (excluding ignitions)
|  | 11. Wire-to-wire contact - Transmission | 11.a. | Wire-to-wire contact / contamination- Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # risk events (excluding ignitions)
|  | 12. Contamination - Transmission | 12.a. | Contamination - Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # risk events (excluding ignitions)
|  | 13. Utility work / Operation | 13.a. | Utility work / Operation | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # risk events (excluding ignitions)
|  | 14. Vandalism / Theft - Transmission | 14.a. | Vandalism / Theft - Transmission | Yes | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # risk events (excluding ignitions)
|  | 15. Other- Transmission | 15.a. | All Other- Transmission | Yes | 1 | 6 | 4 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.000608 | 0.0022747 | 0.000618 | 0.3346 |  |  |  |  | # risk events (excluding ignitions)
|  | 16. Unknown- Transmission | 16.a. | Unknown - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # risk events (excluding ignitions)
x | Outage - Distribution | 17. Contact from object - Distribution | 17.a. | Veg. contact- Distribution | Yes | 395 | 557 | 609 | 416 | 527 | 104 | 70 | 25 | 111 | 93 | 20 | 33 | 174 | 108.2988 | 2.434 | 28.3861 | 93.0672 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 17.b. | Animal contact- Distribution | Yes | 655 | 598 | 622 | 648 | 686 | 122 | 202 | 169 | 163 | 78 | 169 | 143 | 103 | 61.3148 | 158.7059 | 126.1378 | 96.6285 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 17.c. | Balloon contact- Distribution | Yes | 758 | 785 | 911 | 975 | 776 | 178 | 348 | 272 | 191 | 245 | 436 | 246 | 166 | 235.4307 | 375.3217 | 231.5689 | 172.4497 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 17.d. | Vehicle contact- Distribution | Yes | 508 | 586 | 528 | 647 | 517 | 116 | 113 | 153 | 132 | 144 | 128 | 146 | 142 | 140.9088 | 132.3035 | 134.7587 | 134.5126 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 17.e. | Other contact from object - Distribution | Yes | 869 | 393 | 289 | 369 | 449 | 44 | 28 | 35 | 42 | 66 | 75 | 115 | 129 | 108.299 | 85.6883 | 109.1642 | 113.1869 |  |  |  |  | # risk events (excluding ignitions)
|  | 18. Equipment / facility failure - Distribution | 18.a. | Capacitor bank damage or failure- Distribution | Yes | 280 | 275 | 372 | 337 | 426 | 126 | 159 | 72 | 46 | 110 | 98 | 124 | 80 | 96.0146 | 95.9572 | 102.3693 | 90.1684 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 18.b. | Conductor damage or failure — Distribution | Yes | 463 | 594 | 654 | 713 | 1116 | 206 | 144 | 211 | 252 | 276 | 109 | 133 | 319 | 304.1422 | 235.3905 | 208.8959 | 296.3291 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 18.c. | Fuse damage or failure - Distribution | Yes | 232 | 195 | 245 | 508 | 1245 | 169 | 176 | 317 | 167 | 179 | 132 | 201 | 183 | 181.3253 | 158.3721 | 156.2129 | 178.1778 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 18.d. | Lightning arrestor damage or failure- Distribution | Yes | 105 | 127 | 99 | 106 | 216 | 27 | 21 | 26 | 25 | 12 | 21 | 18 | 22 | 23.6016 | 26.2623 | 23.943 | 26.707 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 18.e. | Switch damage or failure- Distribution | Yes | 51 | 46 | 45 | 67 | 78 | 17 | 11 | 16 | 19 | 14 | 10 | 18 | 22 | 15.2391 | 12.6869 | 16.0462 | 18.8884 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 18.f. | Pole damage or failure - Distribution | Yes | 98 | 126 | 130 | 207 | 541 | 57 | 36 | 31 | 40 | 32 | 22 | 21 | 60 | 52.201 | 47.0909 | 42.9422 | 55.9623 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 18.g. | Insulator and brushing damage or failure - Distribution | Yes | 42 | 75 | 79 | 123 | 121 | 28 | 14 | 11 | 43 | 30 | 13 | 22 | 45 | 27.4538 | 15.2802 | 21.1726 | 37.2442 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 18.h. | Crossarm damage or failure - Distribution | Yes | 127 | 143 | 138 | 354 | 834 | 98 | 45 | 29 | 45 | 39 | 17 | 17 | 61 | 56.0094 | 46.3906 | 35.8058 | 62.5023 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 18.i. | Voltage regulator / booster damage or failure - Distribution | Yes | 1 | 2 | 1 | 2 | 4 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 0.3571 | 0.68991 | 1.0212 | 0.35675 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 18.j. | Recloser damage or failure - Distribution | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 18.k. | Anchor / guy damage or failure - Distribution | Yes | 17 | 20 | 18 | 17 | 20 | 3 | 3 | 3 | 4 | 3 | 1 | 3 | 5 | 3.9382 | 1.9015 | 2.6805 | 5.0533 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 18.l. | Sectionalizer damage or failure - Distribution | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 18.m. | Connection device damage or failure - Distribution | Yes | 386 | 490 | 406 | 501 | 500 | 123 | 111 | 86 | 97 | 165 | 108 | 66 | 145 | 130.748 | 99.9575 | 84.0685 | 112.7493 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 18.n. | Transformer damage or failure - Distribution | Yes | 1889 | 1649 | 1978 | 2594 | 2489 | 416 | 559 | 1890 | 536 | 403 | 547 | 724 | 501 | 523.89 | 613.3196 | 1052.7943 | 556.0551 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 18.o. | Other - Distribution | Yes | 97 | 150 | 117 | 178 | 320 | 38 | 50 | 64 | 66 | 50 | 60 | 50 | 64 | 55.6923 | 58.7818 | 54.5714 | 60.2029 |  |  |  |  | # risk events (excluding ignitions)
|  | 19. Wire-to-wire contact - Distribution | 19.a. | Wire-to-wire contact / contamination- Distribution | Yes | 46 | 78 | 64 | 41 | 13 | 6 | 5 | 8 | 7 | 3 | 2 | 11 | 21 | 15.0051 | 14.6221 | 17.5477 | 20.9139 |  |  |  |  | # risk events (excluding ignitions)
|  | 20. Contamination - Distribution | 20.a. | Contamination - Distribution | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # risk events (excluding ignitions)
|  | 21. Utility work / Operation | 21.a. | Utility work / Operation | Yes | 152 | 128 | 110 | 98 | 67 | 32 | 15 | 18 | 10 | 14 | 10 | 12 | 14 | 13.5963 | 12.2393 | 12.8501 | 13.5822 |  |  |  |  | # risk events (excluding ignitions)
|  | 22. Vandalism / Theft - Distribution | 22.a. | Vandalism / Theft - Distribution | Yes | 78 | 80 | 78 | 102 | 103 | 23 | 21 | 21 | 15 | 9 | 16 | 21 | 17 | 16.273 | 18.8957 | 20.6616 | 19.3955 |  |  |  |  | # risk events (excluding ignitions)
|  | 23. Other- Distribution | 23.a. | All Other- Distribution | Yes | 2006 | 2237 | 2346 | 3137 | 3099 | 482 | 574 | 965 | 445 | 374 | 526 | 700 | 524 | 383.4583 | 522.039 | 743.2394 | 495.2009 |  |  |  |  | # risk events (excluding ignitions)
|  | 24. Unknown- Distribution | 24.a. | Unknown - Distribution | Yes | 2142 | 2141 | 2408 | 1741 | 1879 | 361 | 460 | 508 | 538 | 603 | 509 | 483 | 570 | 546.2855 | 513.5077 | 500.6974 | 516.8793 |  |  |  |  | # risk events (excluding ignitions)
x | Outage - Transmission | 25. Contact from object - Transmission | 25.a. | Veg. contact- Transmission | Yes | 15 | 16 | 13 | 9 | 8 | 0 | 0 | 1 | 5 | 2 | 1 | 0 | 1 | 2.1082 | 1.8673 | 1.5347 | 1.8684 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 25.b. | Animal contact- Transmission | Yes | 79 | 75 | 67 | 70 | 33 | 8 | 20 | 5 | 12 | 6 | 14 | 10 | 6 | 7.4305 | 10.054 | 8.8978 | 7.5832 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 25.c. | Balloon contact- Transmission | Yes | 23 | 39 | 56 | 50 | 24 | 3 | 14 | 7 | 8 | 10 | 14 | 4 | 8 | 10.7541 | 10.2615 | 6.927 | 8.3115 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 25.d. | Vehicle contact- Transmission | Yes | 36 | 39 | 39 | 38 | 18 | 3 | 5 | 6 | 4 | 8 | 6 | 3 | 5 | 5.8211 | 5.2008 | 4.202 | 4.8694 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 25.e. | Other contact from object - Transmission | Yes | 77 | 36 | 36 | 45 | 28 | 7 | 4 | 5 | 3 | 1 | 2 | 4 | 9 | 2.9157 | 3.6309 | 4.3077 | 5.9796 |  |  |  |  | # risk events (excluding ignitions)
|  | 26. Equipment / facility failure - Transmission | 26.a. | Capacitor bank damage or failure- Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0.03376 | 0.033735 | 0.42465 | 0.033761 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 26.b. | Conductor damage or failure — Transmission | Yes | 23 | 16 | 91 | 47 | 38 | 6 | 3 | 13 | 7 | 9 | 5 | 6 | 20 | 9.2757 | 7.8552 | 8.1953 | 12.9265 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 26.c. | Fuse damage or failure - Transmission | Yes | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 26.d. | Lightning arrestor damage or failure- Transmission | Yes | 2 | 5 | 2 | 4 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0.37974 | 0.37927 | 0.37931 | 0.37966 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 26.e. | Switch damage or failure- Transmission | Yes | 5 | 3 | 4 | 5 | 2 | 3 | 2 | 0 | 0 | 0 | 1 | 0 | 1 | 0.61777 | 0.95062 | 0.61733 | 0.95102 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 26.f. | Pole damage or failure - Transmission | Yes | 13 | 13 | 18 | 10 | 14 | 3 | 0 | 3 | 3 | 3 | 8 | 3 | 3 | 3.0399 | 4.7036 | 3.0372 | 3.0394 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 26.g. | Insulator and brushing damage or failure - Transmission | Yes | 10 | 13 | 20 | 4 | 9 | 2 | 3 | 1 | 2 | 0 | 1 | 0 | 3 | 1.7113 | 1.9934 | 1.6369 | 2.6271 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 26.h. | Crossarm damage or failure - Transmission | Yes | 11 | 7 | 8 | 7 | 8 | 2 | 1 | 2 | 0 | 0 | 1 | 0 | 4 | 1.1396 | 1.4717 | 1.1385 | 2.4727 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 26.i. | Voltage regulator / booster damage or failure - Transmission | Yes | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 26.j. | Recloser damage or failure - Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 26.k. | Anchor / guy damage or failure - Transmission | Yes | 3 | 8 | 8 | 1 | 4 | 0 | 1 | 2 | 4 | 0 | 1 | 0 | 1 | 0.7819 | 1.1138 | 0.78054 | 1.115 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 26.l. | Sectionalizer damage or failure - Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 26.m. | Connection device damage or failure - Transmission | Yes | 1 | 1 | 3 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19013 | 0.19 | 0.19002 | 0.19011 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 26.n. | Transformer damage or failure - Transmission | Yes | 0 | 1 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # risk events (excluding ignitions)
|  |  | 26.o. | Other - Transmission | Yes | 14 | 26 | 10 | 25 | 41 | 3 | 8 | 9 | 10 | 10 | 5 | 5 | 6 | 7.1466 | 5.4721 | 5.4727 | 5.8118 |  |  |  |  | # risk events (excluding ignitions)
|  | 27. Wire-to-wire contact - Transmission | 27.a. | Wire-to-wire contact / contamination- Transmission | Yes | 14 | 20 | 17 | 29 | 42 | 10 | 10 | 1 | 3 | 1 | 9 | 4 | 2 | 2.4938 | 6.9496 | 4.3741 | 3.341 |  |  |  |  | # risk events (excluding ignitions)
|  | 28. Contamination - Transmission | 28.a. | Contamination - Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # risk events (excluding ignitions)
|  | 29. Utility work / Operation | 29.a. | Utility work / Operation | Yes | 11 | 25 | 12 | 9 | 11 | 1 | 1 | 1 | 1 | 2 | 2 | 3 | 0 | 1.6629 | 2.0647 | 2.3983 | 1.3989 |  |  |  |  | # risk events (excluding ignitions)
|  | 30. Vandalism / Theft - Transmission | 30.a. | Vandalism / Theft - Transmission | Yes | 4 | 7 | 3 | 10 | 2 | 0 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 0.66391 | 0.66282 | 0.99636 | 0.66341 |  |  |  |  | # risk events (excluding ignitions)
|  | 31. Other- Transmission | 31.a. | All Other- Transmission | Yes | 189 | 212 | 224 | 244 | 187 | 38 | 63 | 47 | 55 | 47 | 54 | 48 | 53 | 49.7552 | 53.468 | 50.242 | 52.9635 |  |  |  |  | # risk events (excluding ignitions)
|  | 32. Unknown- Transmission | 32.a. | Unknown - Transmission | Yes | 369 | 335 | 311 | 134 | 267 | 38 | 70 | 36 | 59 | 53 | 55 | 48 | 66 | 60.008 | 60.0116 | 57.8051 | 64.0355 |  |  |  |  | # risk events (excluding ignitions)

## Table 7.2
| Utility | Southern California Edison Company | Notes:
| Table No. | 7.2 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.
| Date Modified | 2022-02-11 | Data from 2015 - 2021 should be actual numbers. 2022 and 2023 should be projected. In future submissions update projected numbers with actuals
| Table 7.2: Key recent and projected drivers of ignitions | [5 empty] | Number of ignitions | [6 empty] | Projected ignitions
| Metric type | # | Ignition driver | Line Type | HFTD tier | Are ignitions tracked for ignition driver? (yes / no) | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | Unit(s) | Comments
x | 1. Contact from object | 1.a.i | Veg. contact | Distribution | Non-HFTD |  | 7 | 7 | 10 | 10 | 10 | 8 | 12 | 11.5037 |  | # ignitions
|  | 1.a.ii | Veg. contact | Distribution | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 1.a.iii | Veg. contact | Distribution | HFTD Tier 2 |  | 2 | 1 | 1 | 4 | 2 | 2 | 3 | 1.5413 |  | # ignitions
|  | 1.a.iv | Veg. contact | Distribution | HFTD Tier 3 |  | 4 | 4 | 5 | 1 | 1 | 1 | 5 | 2.6799 |  | # ignitions
|  | 1.a.v | Veg. contact | Distribution | System |  | 13 | 12 | 16 | 15 | 13 | 11 | 20 | 15.7249 |  | # ignitions
|  | 1.a.vi | Veg. contact | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.019333 |  | # ignitions
|  | 1.a.vii | Veg. contact | Transmission | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 1.a.viii | Veg. contact | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 1.a.ix | Veg. contact | Transmission | HFTD Tier 3 |  | 1 | 2 | 0 | 0 | 2 | 0 | 0 | 0.019568 |  | # ignitions
|  | 1.a.x | Veg. contact | Transmission | System |  | 1 | 2 | 0 | 0 | 3 | 0 | 0 | 0.038901 |  | # ignitions
|  | 1.b.i | Animal contact | Distribution | Non-HFTD |  | 2 | 4 | 3 | 8 | 14 | 15 | 10 | 10.0633 |  | # ignitions
|  | 1.b.ii | Animal contact | Distribution | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 1.b.iii | Animal contact | Distribution | HFTD Tier 2 |  | 1 | 2 | 1 | 3 | 2 | 2 | 0 | 1.0849 |  | # ignitions
|  | 1.b.iv | Animal contact | Distribution | HFTD Tier 3 |  | 6 | 2 | 2 | 1 | 2 | 5 | 3 | 2.6693 |  | # ignitions
|  | 1.b.v | Animal contact | Distribution | System |  | 9 | 8 | 6 | 12 | 18 | 22 | 13 | 13.8175 |  | # ignitions
|  | 1.b.vi | Animal contact | Transmission | Non-HFTD |  | 0 | 0 | 3 | 0 | 0 | 2 | 0 | 0.18621 |  | # ignitions
|  | 1.b.vii | Animal contact | Transmission | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 1.b.viii | Animal contact | Transmission | HFTD Tier 2 |  | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0.9286 |  | # ignitions
|  | 1.b.ix | Animal contact | Transmission | HFTD Tier 3 |  | 0 | 1 | 0 | 0 | 0 | 2 | 0 | 0.96913 |  | # ignitions
|  | 1.b.x | Animal contact | Transmission | System |  | 2 | 1 | 3 | 0 | 0 | 4 | 2 | 2.0839 |  | # ignitions
|  | 1.c.i | Balloon contact | Distribution | Non-HFTD |  | 10 | 7 | 11 | 24 | 10 | 10 | 18 | 15.4905 |  | # ignitions
|  | 1.c.ii | Balloon contact | Distribution | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 1.c.iii | Balloon contact | Distribution | HFTD Tier 2 |  | 0 | 0 | 3 | 1 | 2 | 2 | 1 | 1.1333 |  | # ignitions
|  | 1.c.iv | Balloon contact | Distribution | HFTD Tier 3 |  | 2 | 3 | 4 | 5 | 3 | 5 | 2 | 2.328 |  | # ignitions
|  | 1.c.v | Balloon contact | Distribution | System |  | 12 | 10 | 18 | 30 | 15 | 17 | 21 | 18.9519 |  | # ignitions
|  | 1.c.vi | Balloon contact | Transmission | Non-HFTD |  | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0.42654 |  | # ignitions
|  | 1.c.vii | Balloon contact | Transmission | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 1.c.viii | Balloon contact | Transmission | HFTD Tier 2 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0.10595 |  | # ignitions
|  | 1.c.ix | Balloon contact | Transmission | HFTD Tier 3 |  | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0.43928 |  | # ignitions
|  | 1.c.x | Balloon contact | Transmission | System |  | 1 | 1 | 2 | 0 | 1 | 1 | 1 | 0.97176 |  | # ignitions
|  | 1.d.i | Vehicle contact | Distribution | Non-HFTD |  | 7 | 4 | 4 | 4 | 8 | 3 | 7 | 6.3415 |  | # ignitions
|  | 1.d.ii | Vehicle contact | Distribution | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 1.d.iii | Vehicle contact | Distribution | HFTD Tier 2 |  | 0 | 0 | 1 | 4 | 2 | 1 | 1 | 1.286 |  | # ignitions
|  | 1.d.iv | Vehicle contact | Distribution | HFTD Tier 3 |  | 4 | 2 | 1 | 5 | 0 | 2 | 0 | 1.8544 |  | # ignitions
|  | 1.d.v | Vehicle contact | Distribution | System |  | 11 | 6 | 6 | 13 | 10 | 6 | 8 | 9.4818 |  | # ignitions
|  | 1.d.vi | Vehicle contact | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 1.d.vii | Vehicle contact | Transmission | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 1.d.viii | Vehicle contact | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 1.d.ix | Vehicle contact | Transmission | HFTD Tier 3 |  | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0.83133 |  | # ignitions
|  | 1.d.x | Vehicle contact | Transmission | System |  | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0.83133 |  | # ignitions
|  | 1.e.i | Other contact from object | Distribution | Non-HFTD |  | 2 | 3 | 3 | 0 | 4 | 4 | 10 | 7.6709 |  | # ignitions
|  | 1.e.ii | Other contact from object | Distribution | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 1.e.iii | Other contact from object | Distribution | HFTD Tier 2 |  | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 0.3082 |  | # ignitions
|  | 1.e.iv | Other contact from object | Distribution | HFTD Tier 3 |  | 1 | 2 | 1 | 0 | 2 | 0 | 2 | 1.0813 |  | # ignitions
|  | 1.e.v | Other contact from object | Distribution | System |  | 4 | 6 | 5 | 0 | 6 | 5 | 12 | 9.0603 |  | # ignitions
|  | 1.e.vi | Other contact from object | Transmission | Non-HFTD |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.063438 |  | # ignitions
|  | 1.e.vii | Other contact from object | Transmission | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 1.e.viii | Other contact from object | Transmission | HFTD Tier 2 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.064878 |  | # ignitions
|  | 1.e.ix | Other contact from object | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0.46442 |  | # ignitions
|  | 1.e.x | Other contact from object | Transmission | System |  | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 0.59273 |  | # ignitions
| 2. Equipment / facility failure | 2.a.i | Capacitor bank damage or failure | Distribution | Non-HFTD |  | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0.14022 |  | # ignitions
|  | 2.a.ii | Capacitor bank damage or failure | Distribution | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.a.iii | Capacitor bank damage or failure | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.a.iv | Capacitor bank damage or failure | Distribution | HFTD Tier 3 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.067265 |  | # ignitions
|  | 2.a.v | Capacitor bank damage or failure | Distribution | System |  | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0.20748 |  | # ignitions
|  | 2.a.vi | Capacitor bank damage or failure | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.072732 |  | # ignitions
|  | 2.a.vii | Capacitor bank damage or failure | Transmission | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.a.viii | Capacitor bank damage or failure | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.a.ix | Capacitor bank damage or failure | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.a.x | Capacitor bank damage or failure | Transmission | System |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.072732 |  | # ignitions
|  | 2.b.i | Conductor damage or failure | Distribution | Non-HFTD |  | 1 | 14 | 14 | 1 | 6 | 11 | 21 | 17.7966 |  | # ignitions
|  | 2.b.ii | Conductor damage or failure | Distribution | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.b.iii | Conductor damage or failure | Distribution | HFTD Tier 2 |  | 1 | 2 | 0 | 1 | 2 | 2 | 2 | 1.7068 |  | # ignitions
|  | 2.b.iv | Conductor damage or failure | Distribution | HFTD Tier 3 |  | 0 | 3 | 1 | 3 | 3 | 12 | 5 | 2.5864 |  | # ignitions
|  | 2.b.v | Conductor damage or failure | Distribution | System |  | 2 | 19 | 15 | 5 | 11 | 25 | 28 | 22.0898 |  | # ignitions
|  | 2.b.vi | Conductor damage or failure | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.b.vii | Conductor damage or failure | Transmission | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.b.viii | Conductor damage or failure | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.b.ix | Conductor damage or failure | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.b.x | Conductor damage or failure | Transmission | System |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.c.i | Fuse damage or failure | Distribution | Non-HFTD |  | 1 | 0 | 1 | 0 | 2 | 1 | 1 | 1.0686 |  | # ignitions
|  | 2.c.ii | Fuse damage or failure | Distribution | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.c.iii | Fuse damage or failure | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.34628 |  | # ignitions
|  | 2.c.iv | Fuse damage or failure | Distribution | HFTD Tier 3 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.02538 |  | # ignitions
|  | 2.c.v | Fuse damage or failure | Distribution | System |  | 1 | 1 | 1 | 0 | 2 | 1 | 2 | 1.4403 |  | # ignitions
|  | 2.c.vi | Fuse damage or failure | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.c.vii | Fuse damage or failure | Transmission | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.c.viii | Fuse damage or failure | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.c.ix | Fuse damage or failure | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.c.x | Fuse damage or failure | Transmission | System |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.d.i | Lightning arrestor damage or failure | Distribution | Non-HFTD |  | 2 | 0 | 2 | 0 | 1 | 2 | 3 | 2.1386 |  | # ignitions
|  | 2.d.ii | Lightning arrestor damage or failure | Distribution | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.d.iii | Lightning arrestor damage or failure | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.d.iv | Lightning arrestor damage or failure | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.d.v | Lightning arrestor damage or failure | Distribution | System |  | 2 | 0 | 2 | 0 | 1 | 2 | 3 | 2.1386 |  | # ignitions
|  | 2.d.vi | Lightning arrestor damage or failure | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.035004 |  | # ignitions
|  | 2.d.vii | Lightning arrestor damage or failure | Transmission | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.d.viii | Lightning arrestor damage or failure | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.d.ix | Lightning arrestor damage or failure | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.d.x | Lightning arrestor damage or failure | Transmission | System |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.035004 |  | # ignitions
|  | 2.e.i | Switch damage or failure | Distribution | Non-HFTD |  | 0 | 0 | 0 | 1 | 2 | 5 | 3 | 3.3946 |  | # ignitions
|  | 2.e.ii | Switch damage or failure | Distribution | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.e.iii | Switch damage or failure | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.e.iv | Switch damage or failure | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.38025 |  | # ignitions
|  | 2.e.v | Switch damage or failure | Distribution | System |  | 0 | 0 | 0 | 1 | 2 | 5 | 4 | 3.7749 |  | # ignitions
|  | 2.e.vi | Switch damage or failure | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.e.vii | Switch damage or failure | Transmission | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.e.viii | Switch damage or failure | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.e.ix | Switch damage or failure | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.e.x | Switch damage or failure | Transmission | System |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.f.i | Pole damage or failure | Distribution | Non-HFTD |  | 1 | 2 | 1 | 0 | 0 | 2 | 0 | 0.74397 |  | # ignitions
|  | 2.f.ii | Pole damage or failure | Distribution | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.f.iii | Pole damage or failure | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.034127 |  | # ignitions
|  | 2.f.iv | Pole damage or failure | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.034094 |  | # ignitions
|  | 2.f.v | Pole damage or failure | Distribution | System |  | 1 | 2 | 1 | 0 | 1 | 3 | 0 | 0.81219 |  | # ignitions
|  | 2.f.vi | Pole damage or failure | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.f.vii | Pole damage or failure | Transmission | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.f.viii | Pole damage or failure | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.f.ix | Pole damage or failure | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.f.x | Pole damage or failure | Transmission | System |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.g.i | Insulator and brushing damage or failure | Distribution | Non-HFTD |  | 0 | 0 | 0 | 0 | 2 | 5 | 1 | 1.5862 |  | # ignitions
|  | 2.g.ii | Insulator and brushing damage or failure | Distribution | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.g.iii | Insulator and brushing damage or failure | Distribution | HFTD Tier 2 |  | 1 | 2 | 0 | 0 | 0 | 1 | 0 | 0.39137 |  | # ignitions
|  | 2.g.iv | Insulator and brushing damage or failure | Distribution | HFTD Tier 3 |  | 0 | 0 | 2 | 1 | 0 | 1 | 0 | 0.38049 |  | # ignitions
|  | 2.g.v | Insulator and brushing damage or failure | Distribution | System |  | 1 | 2 | 2 | 1 | 2 | 7 | 1 | 2.3581 |  | # ignitions
|  | 2.g.vi | Insulator and brushing damage or failure | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | # ignitions
|  | 2.g.vii | Insulator and brushing damage or failure | Transmission | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.g.viii | Insulator and brushing damage or failure | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.g.ix | Insulator and brushing damage or failure | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.g.x | Insulator and brushing damage or failure | Transmission | System |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | # ignitions
|  | 2.h.i | Crossarm damage or failure | Distribution | Non-HFTD |  | 1 | 2 | 1 | 1 | 0 | 0 | 0 | 0.31512 |  | # ignitions
|  | 2.h.ii | Crossarm damage or failure | Distribution | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.h.iii | Crossarm damage or failure | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.h.iv | Crossarm damage or failure | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.055128 |  | # ignitions
|  | 2.h.v | Crossarm damage or failure | Distribution | System |  | 1 | 2 | 1 | 1 | 1 | 0 | 0 | 0.37025 |  | # ignitions
|  | 2.h.vi | Crossarm damage or failure | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.035004 |  | # ignitions
|  | 2.h.vii | Crossarm damage or failure | Transmission | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.h.viii | Crossarm damage or failure | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.h.ix | Crossarm damage or failure | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.h.x | Crossarm damage or failure | Transmission | System |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.035004 |  | # ignitions
|  | 2.i.i | Voltage regulator / booster damage or failure | Distribution | Non-HFTD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.i.ii | Voltage regulator / booster damage or failure | Distribution | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.i.iii | Voltage regulator / booster damage or failure | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.i.iv | Voltage regulator / booster damage or failure | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.i.v | Voltage regulator / booster damage or failure | Distribution | System |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.i.vi | Voltage regulator / booster damage or failure | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.i.vii | Voltage regulator / booster damage or failure | Transmission | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.i.viii | Voltage regulator / booster damage or failure | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.i.ix | Voltage regulator / booster damage or failure | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.i.x | Voltage regulator / booster damage or failure | Transmission | System |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.j.i | Recloser damage or failure | Distribution | Non-HFTD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.j.ii | Recloser damage or failure | Distribution | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.j.iii | Recloser damage or failure | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.j.iv | Recloser damage or failure | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.j.v | Recloser damage or failure | Distribution | System |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.j.vi | Recloser damage or failure | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.j.vii | Recloser damage or failure | Transmission | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.j.viii | Recloser damage or failure | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.j.ix | Recloser damage or failure | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.j.x | Recloser damage or failure | Transmission | System |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.k.i | Anchor / guy damage or failure | Distribution | Non-HFTD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.k.ii | Anchor / guy damage or failure | Distribution | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.k.iii | Anchor / guy damage or failure | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.k.iv | Anchor / guy damage or failure | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.k.v | Anchor / guy damage or failure | Distribution | System |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.k.vi | Anchor / guy damage or failure | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.k.vii | Anchor / guy damage or failure | Transmission | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.k.viii | Anchor / guy damage or failure | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.k.ix | Anchor / guy damage or failure | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.k.x | Anchor / guy damage or failure | Transmission | System |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.l.i | Sectionalizer damage or failure | Distribution | Non-HFTD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.l.ii | Sectionalizer damage or failure | Distribution | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.l.iii | Sectionalizer damage or failure | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.l.iv | Sectionalizer damage or failure | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.l.v | Sectionalizer damage or failure | Distribution | System |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.l.vi | Sectionalizer damage or failure | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.l.vii | Sectionalizer damage or failure | Transmission | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.l.viii | Sectionalizer damage or failure | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.l.ix | Sectionalizer damage or failure | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.l.x | Sectionalizer damage or failure | Transmission | System |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.m.i | Connection device damage or failure | Distribution | Non-HFTD |  | 1 | 1 | 2 | 0 | 4 | 3 | 7 | 4.2329 |  | # ignitions
|  | 2.m.ii | Connection device damage or failure | Distribution | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.m.iii | Connection device damage or failure | Distribution | HFTD Tier 2 |  | 1 | 2 | 0 | 0 | 1 | 0 | 4 | 2.1395 |  | # ignitions
|  | 2.m.iv | Connection device damage or failure | Distribution | HFTD Tier 3 |  | 2 | 1 | 1 | 1 | 2 | 0 | 2 | 3.4304 |  | # ignitions
|  | 2.m.v | Connection device damage or failure | Distribution | System |  | 4 | 4 | 3 | 1 | 7 | 3 | 13 | 9.8028 |  | # ignitions
|  | 2.m.vi | Connection device damage or failure | Transmission | Non-HFTD |  | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0.035004 |  | # ignitions
|  | 2.m.vii | Connection device damage or failure | Transmission | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.m.viii | Connection device damage or failure | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.m.ix | Connection device damage or failure | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.m.x | Connection device damage or failure | Transmission | System |  | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0.035004 |  | # ignitions
|  | 2.n.i | Transformer damage or failure | Distribution | Non-HFTD |  | 2 | 1 | 1 | 8 | 2 | 8 | 8 | 4.0239 |  | # ignitions
|  | 2.n.ii | Transformer damage or failure | Distribution | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.n.iii | Transformer damage or failure | Distribution | HFTD Tier 2 |  | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0.40138 |  | # ignitions
|  | 2.n.iv | Transformer damage or failure | Distribution | HFTD Tier 3 |  | 1 | 0 | 1 | 2 | 1 | 1 | 2 | 1.4853 |  | # ignitions
|  | 2.n.v | Transformer damage or failure | Distribution | System |  | 3 | 2 | 2 | 10 | 3 | 10 | 11 | 5.9106 |  | # ignitions
|  | 2.n.vi | Transformer damage or failure | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.n.vii | Transformer damage or failure | Transmission | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.n.viii | Transformer damage or failure | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.n.ix | Transformer damage or failure | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.n.x | Transformer damage or failure | Transmission | System |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.o.i | Other | Distribution | Non-HFTD |  | 4 | 4 | 0 | 6 | 2 | 2 | 7 | 5.9333 |  | # ignitions
|  | 2.o.ii | Other | Distribution | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.o.iii | Other | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0.54796 |  | # ignitions
|  | 2.o.iv | Other | Distribution | HFTD Tier 3 |  | 2 | 3 | 1 | 1 | 0 | 1 | 2 | 1.8175 |  | # ignitions
|  | 2.o.v | Other | Distribution | System |  | 6 | 7 | 1 | 7 | 2 | 4 | 10 | 8.2988 |  | # ignitions
|  | 2.o.vi | Other | Transmission | Non-HFTD |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.035004 |  | # ignitions
|  | 2.o.vii | Other | Transmission | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.o.viii | Other | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 2.o.ix | Other | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0.036466 |  | # ignitions
|  | 2.o.x | Other | Transmission | System |  | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0.07147 |  | # ignitions
| 3. Wire-to-wire contact | 3.a.i | Wire-to-wire contact / contamination | Distribution | Non-HFTD |  | 0 | 1 | 2 | 1 | 6 | 4 | 5 | 5.3819 |  | # ignitions
|  | 3.a.ii | Wire-to-wire contact / contamination | Distribution | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 3.a.iii | Wire-to-wire contact / contamination | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 2 | 1 | 0 | 1 | 0.54269 |  | # ignitions
|  | 3.a.iv | Wire-to-wire contact / contamination | Distribution | HFTD Tier 3 |  | 1 | 0 | 1 | 0 | 1 | 1 | 0 | 0.38676 |  | # ignitions
|  | 3.a.v | Wire-to-wire contact / contamination | Distribution | System |  | 1 | 1 | 3 | 3 | 8 | 5 | 6 | 6.3113 |  | # ignitions
|  | 3.a.vi | Wire-to-wire contact / contamination | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 3.a.vii | Wire-to-wire contact / contamination | Transmission | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 3.a.viii | Wire-to-wire contact / contamination | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 3.a.ix | Wire-to-wire contact / contamination | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 3.a.x | Wire-to-wire contact / contamination | Transmission | System |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
| 4. Contamination | 4.a.i | Contamination | Distribution | Non-HFTD |  | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0.34824 |  | # ignitions
|  | 4.a.ii | Contamination | Distribution | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 4.a.iii | Contamination | Distribution | HFTD Tier 2 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.023179 |  | # ignitions
|  | 4.a.iv | Contamination | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 4.a.v | Contamination | Distribution | System |  | 1 | 0 | 1 | 0 | 2 | 0 | 0 | 0.37142 |  | # ignitions
|  | 4.a.vi | Contamination | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 4.a.vii | Contamination | Transmission | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 4.a.viii | Contamination | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 4.a.ix | Contamination | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.0053284 |  | # ignitions
|  | 4.a.x | Contamination | Transmission | System |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.0053284 |  | # ignitions
| 5. Utility work / Operation | 5.a.i | Utility work / Operation | Distribution | Non-HFTD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 5.a.ii | Utility work / Operation | Distribution | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 5.a.iii | Utility work / Operation | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 5.a.iv | Utility work / Operation | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 5.a.v | Utility work / Operation | Distribution | System |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 5.a.vi | Utility work / Operation | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 5.a.vii | Utility work / Operation | Transmission | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 5.a.viii | Utility work / Operation | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 5.a.ix | Utility work / Operation | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 5.a.x | Utility work / Operation | Transmission | System |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
| 6. Vandalism / Theft | 6.a.i | Vandalism / Theft | Distribution | Non-HFTD |  | 3 | 0 | 0 | 1 | 4 | 4 | 5 | 5.0606 |  | # ignitions
|  | 6.a.ii | Vandalism / Theft | Distribution | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 6.a.iii | Vandalism / Theft | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.027611 |  | # ignitions
|  | 6.a.iv | Vandalism / Theft | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | 1 | 2 | 1 | 0.42944 |  | # ignitions
|  | 6.a.v | Vandalism / Theft | Distribution | System |  | 3 | 0 | 0 | 1 | 6 | 6 | 6 | 5.5176 |  | # ignitions
|  | 6.a.vi | Vandalism / Theft | Transmission | Non-HFTD |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0043235 |  | # ignitions
|  | 6.a.vii | Vandalism / Theft | Transmission | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 6.a.viii | Vandalism / Theft | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 6.a.ix | Vandalism / Theft | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 6.a.x | Vandalism / Theft | Transmission | System |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0043235 |  | # ignitions
| 7. Other | 7.a.i | All Other | Distribution | Non-HFTD |  | 2 | 0 | 0 | 0 | 1 | 6 | 6 | 7.4133 |  | # ignitions
|  | 7.a.ii | All Other | Distribution | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 7.a.iii | All Other | Distribution | HFTD Tier 2 |  | 1 | 0 | 1 | 0 | 2 | 0 | 2 | 1.4884 |  | # ignitions
|  | 7.a.iv | All Other | Distribution | HFTD Tier 3 |  | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 0.84147 |  | # ignitions
|  | 7.a.v | All Other | Distribution | System |  | 4 | 0 | 1 | 0 | 4 | 7 | 9 | 9.7432 |  | # ignitions
|  | 7.a.vi | All Other | Transmission | Non-HFTD |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.0043235 |  | # ignitions
|  | 7.a.vii | All Other | Transmission | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 7.a.viii | All Other | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  | # ignitions
|  | 7.a.ix | All Other | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 7.a.x | All Other | Transmission | System |  | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0.0043235 |  | # ignitions
| 8. Unknown | 8.a.i | Unknown | Distribution | Non-HFTD |  | 14 | 3 | 7 | 5 | 0 | 3 | 1 | 1.7856 |  | # ignitions
|  | 8.a.ii | Unknown | Distribution | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 8.a.iii | Unknown | Distribution | HFTD Tier 2 |  | 1 | 0 | 2 | 1 | 0 | 0 | 0 | 0.38798 |  | # ignitions
|  | 8.a.iv | Unknown | Distribution | HFTD Tier 3 |  | 6 | 2 | 3 | 0 | 1 | 0 | 0 | 0.059298 |  | # ignitions
|  | 8.a.v | Unknown | Distribution | System |  | 21 | 5 | 12 | 6 | 1 | 3 | 1 | 2.2329 |  | # ignitions
|  | 8.a.vi | Unknown | Transmission | Non-HFTD |  | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0.066021 |  | # ignitions
|  | 8.a.vii | Unknown | Transmission | HFTD Zone 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 8.a.viii | Unknown | Transmission | HFTD Tier 2 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0.3766 |  | # ignitions
|  | 8.a.ix | Unknown | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | # ignitions
|  | 8.a.x | Unknown | Transmission | System |  | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0.44262 |  | # ignitions

## Table 8
Utility | Southern California Edison Company
Table No. | 8
Date Modified | 2022-02-11
Note: These columns are placeholders for future QR submissions.
Table 8: State of service territory and utility equipment |  |  | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3
Metric type | # | Outcome metric name | 2015 | 2015 | 2015 | 2015 | 2016 | 2016 | 2016 | 2016 | 2017 | 2017 | 2017 | 2017 | 2018 | 2018 | 2018 | 2018 | 2019 | 2019 | 2019 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
1. State of service territory and equipment in urban areas | 1.a. | Circuit miles (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 17159.88 | 0.85 | 1126.19 | 1452.86 | 17052.6827 | 0.85 | 1035.1765 | 1428.4968 | 16353.0149 | 0.23993 | 1011.0023 | 1128.5294 |  |  |  |  | Circuit miles | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 1.b. | Circuit miles in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 3446.19 | 0.48 | 749.7 | 1363.52 | 3482.0979 | 0.48 | 674.3718 | 1339.4887 | 2264.0846 | 0 | 480.8793 | 762.1729 |  |  |  |  | Circuit miles in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 1.c. | Number of critical facilities (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 36757 | 6 | 2550 | 3923 | 36911 | 6 | 2207 | 3917 | 36944 |  | 1889 | 2991 |  |  |  |  | Number of critical facilities | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included some locations outside of SCE’s service territory within California, whereas 2020 data solely includes critical facilities within SCE’s service territory within California. SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 1.d. | Number of critical facilities in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 7305 | 5 | 1676 | 3489 | 7502 | 5 | 1417 | 3489 | 4657 | 0 | 860 | 2098 |  |  |  |  | Number of critical facilities in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included some locations outside of SCE’s service territory within California, whereas 2020 data solely includes critical facilities within SCE’s service territory within California. SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 1.e. | Number of customers (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 3790432 | 545 | 209126 | 323745 | 3790432 | 545 | 209126 | 323745 | 3316257 | 15 | 126254 | 226932 |  |  |  |  | Number of customers | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 1.f. | Number of customers in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 778819 | 525 | 149646 | 294005 | 778819 | 525 | 149646 | 294005 | 511274 | 13 | 71212 | 183954 |  |  |  |  | Number of customers in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 1.g. | Number of customers belonging to access and functional needs populations (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 1032899 | 32 | 30783 | 44840 | 1032899 | 32 | 30783 | 44840 | 1201396 | 7 | 27699 | 44897 |  |  |  |  | Number of customers belonging to access and functional needs populations | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 1.h. | Number of customers belonging to access and functional needs populations in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 206260 | 21 | 23970 | 41362 | 206260 | 21 | 23970 | 41362 | 168390 | 0 | 16523 | 37295 |  |  |  |  | Number of customers belonging to access and functional needs populations in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 1.i. | Circuit miles of overhead transmission lines (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 1953.85 | 0.08 | 217.92 | 223.98 | 1937.0513 | 0.08 | 203.8292 | 215.4523 | 2580.7369 | 0.086399 | 302.6203 | 353.0634 |  |  |  |  | Circuit miles of overhead transmission lines | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 1.j. | Circuit miles of overhead transmission lines in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 293.15 | 0 | 130.59 | 182.31 | 300.6119 | 0 | 120.9586 | 173.5481 | 255.1986 | 0 | 110.3893 | 158.4173 |  |  |  |  | Circuit miles of overhead transmission lines in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 1.k. | Circuit miles of overhead distribution lines (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 15206.04 | 0.77 | 908.27 | 1228.89 | 15115.6314 | 0.77 | 831.3473 | 1213.0444 | 13772.278 | 0.15353 | 708.382 | 775.466 |  |  |  |  | Circuit miles of overhead distribution lines | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 1.l. | Circuit miles of overhead distribution lines in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 3153.05 | 0.48 | 619.12 | 1181.22 | 3181.4859 | 0.48 | 553.4132 | 1165.9407 | 2008.886 | 0 | 370.49 | 603.7556 |  |  |  |  | Circuit miles of overhead distribution lines in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 1.m. | Number of substations (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 231 | 0 | 23 | 17 | 230 | 0 | 12 | 13 | 392 | 0 | 18 | 19 |  |  |  |  | Number of substations | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 1.n | Number of substations in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 47 | 0 | 16 | 16 | 43 | 0 | 6 | 12 | 43 | 0 | 6 | 10 |  |  |  |  | Number of substations in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
, | 1.o. | Number of weather stations (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 35 | 0 | 18 | 32 | 51 | 0 | 107 | 94 | 51 | 0 | 142 | 136 |  |  |  |  | Number of weather stations | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 1.p. | Number of weather stations in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 20 | 0 | 11 | 31 | 29 | 0 | 63 | 89 | 16 | 0 | 69 | 86 |  |  |  |  | Number of weather stations in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
2. State of service territory and equipment in rural areas | 2.a. | Circuit miles (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 8536.18 | 0.46 | 2127.05 | 3723.5 | 8543.3122 | 0.47 | 2011.53 | 3676.3 | 6186.4269 | 0.87132 | 1982.3407 | 3389.7389 |  |  |  |  | Circuit miles | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 2.b. | Circuit miles in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 3262.55 | 0.04 | 1491.89 | 2729.02 | 3306.7952 | 0.05 | 1407.8787 | 2695.1743 | 1758.3625 | 0.038866 | 829.6762 | 1677.37 |  |  |  |  | Circuit miles in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 2.c. | Number of critical facilities (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 7692 | 0 | 1456 | 2894 | 7744 | 0 | 1338 | 2890 | 4846 | 0 | 1290 | 2948 |  |  |  |  | Number of critical facilities | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 2.d. | Number of critical facilities in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 2397 | 0 | 1036 | 2348 | 2460 | 0 | 940 | 2343 | 1613 | 0 | 687 | 1822 |  |  |  |  | Number of critical facilities in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 2.e. | Number of customers (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 225587 | 20 | 53624 | 92195 | 225587 | 20 | 53624 | 92195 | 195511 | 8 | 55535 | 112997 |  |  |  |  | Number of customers | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 2.f. | Number of customers in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 94950 | 16 | 44971 | 83235 | 94950 | 16 | 44971 | 83235 | 107381 | 2 | 45662 | 99248 |  |  |  |  | Number of customers in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 2.g. | Number of customers belonging to access and functional needs populations (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 37100 | 4 | 7741 | 9410 | 37100 | 4 | 7741 | 9410 | 61769 | 0 | 15305 | 21164 |  |  |  |  | Number of customers belonging to access and functional needs populations | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 2.h. | Number of customers belonging to access and functional needs populations in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 19384 | 1 | 6718 | 8676 | 19384 | 1 | 6718 | 8676 | 37808 | 0 | 13355 | 19610 |  |  |  |  | Number of customers belonging to access and functional needs populations in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 2.i. | Circuit miles of overhead transmission lines (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 1353.32 | 0.09 | 453.91 | 771.52 | 1348.1553 | 0.09 | 444.1284 | 756.8649 | 1327.737 | 0 | 647.3204 | 1027.232 |  |  |  |  | Circuit miles of overhead transmission lines | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 2.j. | Circuit miles of overhead transmission lines in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 333.8 | 0 | 283.81 | 419.23 | 336.3493 | 0 | 277.3478 | 410.3605 | 132.7305 | 0 | 144.0662 | 235.99 |  |  |  |  | Circuit miles of overhead transmission lines in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 2.k. | Circuit miles of overhead distribution lines (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 7182.86 | 0.37 | 1673.14 | 2951.98 | 7195.1569 | 0.38 | 1567.4016 | 2919.435 | 4858.6899 | 0.87132 | 1335.0203 | 2362.5069 |  |  |  |  | Circuit miles of overhead distribution lines | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 2.l. | Circuit miles of overhead distribution lines in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 2928.75 | 0.04 | 1208.08 | 2309.79 | 2970.4459 | 0.05 | 1130.531 | 2284.8138 | 1625.632 | 0.038866 | 685.61 | 1441.38 |  |  |  |  | Circuit miles of overhead distribution lines in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 2.m. | Number of substations (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 125 | 0 | 18 | 32 | 112 | 0 | 13 | 29 | 124 | 0 | 24 | 39 |  |  |  |  | Number of substations | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 2.n | Number of substations in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 25 | 0 | 10 | 26 | 21 | 0 | 6 | 24 | 16 | 0 | 5 | 18 |  |  |  |  | Number of substations in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 2.o. | Number of weather stations (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 20 | 0 | 53 | 152 | 30 | 0 | 144 | 273 | 30 | 0 | 187 | 395 |  |  |  |  | Number of weather stations | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 2.p. | Number of weather stations in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 9 | 0 | 39 | 119 | 14 | 0 | 105 | 216 | 11 | 0 | 75 | 187 |  |  |  |  | Number of weather stations in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
3. State of service territory and equipment in highly rural areas | 3.a. | Circuit miles (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 12178.84 | 0.84 | 2757.67 | 2992.26 | 11688.2696 | 0.84 | 2645.3755 | 2916.0365 | 14411.2596 | 1.0413 | 2875.942 | 3499.872 |  |  |  |  | Circuit miles | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 3.b. | Circuit miles in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 93.66 | 0 | 34.64 | 43.6 | 94.0503 | 0 | 24.5049 | 44.4822 | 2722.0028 | 0.48865 | 909.6626 | 1629.4658 |  |  |  |  | Circuit miles in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 3.c. | Number of critical facilities (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 21784 | 0 | 1767 | 2598 | 21728 | 0 | 1613 | 2560 | 13483 | 5 | 2062 | 3260 |  |  |  |  | Number of critical facilities | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 3.d. | Number of critical facilities in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 98 | 0 | 22 | 32 | 99 | 0 | 18 | 29 | 3020 | 4 | 938 | 1881 |  |  |  |  | Number of critical facilities in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 3.e. | Number of customers (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 379812 | 8 | 24861 | 37774 | 379812 | 8 | 24861 | 37774 | 944764 | 420 | 92639 | 127383 |  |  |  |  | Number of customers | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 3.f. | Number of customers in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 2566 | 0 | 968 | 1578 | 2566 | 0 | 968 | 1578 | 297274 | 377 | 67958 | 110603 |  |  |  |  | Number of customers in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 3.g. | Number of customers belonging to access and functional needs populations (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 44535 | 0 | 2492 | 2674 | 44535 | 0 | 2492 | 2674 | 332340 | 0 | 19356 | 25302 |  |  |  |  | Number of customers belonging to access and functional needs populations | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 3.h. | Number of customers belonging to access and functional needs populations in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 342 | 0 | 54 | 100 | 342 | 0 | 54 | 100 | 107332 | 0 | 15341 | 23146 |  |  |  |  | Number of customers belonging to access and functional needs populations in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 3.i. | Circuit miles of overhead transmission lines (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 5161.27 | 0.02 | 1285.5 | 1399.53 | 4764.2274 | 0.03 | 1255.9612 | 1371.7135 | 4034.4534 | 0.10757 | 1000.407 | 987.547 |  |  |  |  | Circuit miles of overhead transmission lines | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 3.j. | Circuit miles of overhead transmission lines in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 7.75 | 0 | 3.18 | 2.97 | 7.9707 | 0 | 3.3432 | 5.4962 | 238.7637 | 0 | 162.0705 | 200.9038 |  |  |  |  | Circuit miles of overhead transmission lines in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 3.k. | Circuit miles of overhead distribution lines (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 7017.57 | 0.81 | 1472.17 | 1592.74 | 6924.0422 | 0.81 | 1389.4144 | 1544.323 | 10376.8062 | 0.93373 | 1875.535 | 2512.325 |  |  |  |  | Circuit miles of overhead distribution lines | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 3.l. | Circuit miles of overhead distribution lines in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 85.92 | 0 | 31.46 | 40.63 | 86.0796 | 0 | 21.1617 | 38.9861 | 2483.239 | 0.48865 | 747.5921 | 1428.562 |  |  |  |  | Circuit miles of overhead distribution lines in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 3.m. | Number of substations (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 420 | 0 | 62 | 49 | 322 | 0 | 49 | 40 | 241 | 0 | 63 | 46 |  |  |  |  | Number of substations | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 3.n | Number of substations in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 23 | 0 | 12 | 16 |  |  |  |  | Number of substations in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 3.o. | Number of weather stations (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 36 | 0 | 90 | 137 | 47 | 0 | 348 | 465 | 43 | 0 | 248 | 342 |  |  |  |  | Number of weather stations | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 3.p. | Number of weather stations in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | 3 | 0 | 0 | 0 | 10 | 4 | 14 | 0 | 80 | 157 |  |  |  |  | Number of weather stations in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.

## Table 9
Utility | Southern California Edison Company | Notes:
Table No. | 9 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV. Report net additions using positive numbers and net removals and undergrounding using negative numbers for circuit miles and numbers of substations. Only report changes expected within the target year.
Date Modified | 2022-02-11 | For example, if 20 net overhead circuit miles are planned for addition by 2023, with 15 being added by 2022 and 5 more added by 2023, then report “15” for 2022 and “5” for 2023. Do not report cumulative change across years. In this case, do not report “20” for 2023, but instead the number planned to be added for just that year, which is “5”.
|  |  | Actual |  |  |  | Projected
Table 9: Location of actual and planned utility equipment additions or removal year over year |  |  | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3
Metric type | # | Outcome metric name | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
1. Planned utility equipment net addition (or removal) year over year - in urban areas | 1.a. | Circuit miles of overhead transmission lines (including WUI and non-WUI) | 3.97 | 0 | 1.54 | 1.52 | 7.3 | 0 | 2.47 | 1.03 | 10.49 | 0 | 0 | 0 | Circuit miles
| 1.b. | Circuit miles of overhead distribution lines (including WUI and non-WUI) | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Circuit miles | SCE does not routinely track planned additions or removals by population density or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map all projects in GIS and subdivide as requested. SCE is also seeking to improve its processes associated with this WMP requirement.
| 1.c. | Circuit miles of overhead transmission lines in WUI | 0.12 | 0 | 1.54 | 1.13 | 0.67 | 0 | 2.47 | 1.03 | 0.6 | 0 | 0 | 0 | Circuit miles in WUI
| 1.d. | Circuit miles of overhead distribution lines in WUI | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Circuit miles in WUI | SCE does not routinely track planned additions or removals by population density or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map all projects in GIS and subdivide as requested. SCE is also seeking to improve its processes associated with this WMP requirement.
| 1.e. | Number of substations (including WUI and non-WUI) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of substations
| 1.f. | Number of substations in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of substations in WUI
| 1.g. | Number of weather stations (including WUI and non-WUI) | 16 | 0 | 89 | 62 | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Number of weather stations | Actual site/structure locations have not yet been determined and SCE is therefore unable to provide the locational attributes as requested
| 1.h. | Number of weather stations in WUI | 9 | 0 | 52 | 58 | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Number of weather stations in WUI | Actual site/structure locations have not yet been determined and SCE is therefore unable to provide the locational attributes as requested
2. Planned utility equipment net addition (or removal) year over year - in rural areas | 2.a. | Circuit miles of overhead transmission lines (including WUI and non-WUI) | 3.54 | 0 | 3.68 | 5.51 | 2.55 | 0 | 5.92 | 2.71 | 8.75 | 0 | 0 | 0 | Circuit miles
| 2.b. | Circuit miles of overhead distribution lines (including WUI and non-WUI) | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Circuit miles | SCE does not routinely track planned additions or removals by population density or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map all projects in GIS and subdivide as requested. SCE is also seeking to improve its processes associated with this WMP requirement.
| 2.c. | Circuit miles of overhead transmission lines in WUI | 2.47 | 0 | 2.54 | 3.91 | 1.44 | 0 | 4.5 | 2.49 | 0 | 0 | 0 | 0 | Circuit miles in WUI
| 2.d. | Circuit miles of overhead distribution lines in WUI | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Circuit miles in WUI | SCE does not routinely track planned additions or removals by population density or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map all projects in GIS and subdivide as requested. SCE is also seeking to improve its processes associated with this WMP requirement.
| 2.e. | Number of substations (including WUI and non-WUI) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of substations
| 2.f. | Number of substations in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of substations in WUI
| 2.g. | Number of weather stations (including WUI and non-WUI) | 10 | 0 | 91 | 121 | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Number of weather stations | Actual site/structure locations have not yet been determined and SCE is therefore unable to provide the locational attributes as requested
| 2.h. | Number of weather stations in WUI | 5 | 0 | 66 | 97 | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Number of weather stations in WUI | Actual site/structure locations have not yet been determined and SCE is therefore unable to provide the locational attributes as requested
3. Planned utility equipment net addition (or removal) year over year - in highly rural areas | 3.a. | Circuit miles of overhead transmission lines (including WUI and non-WUI) | 4.25 | 0 | 5.73 | 18.89 | 3.61 | 0 | 4.34 | 5.29 | 4.47 | 0 | 0 | 0 | Circuit miles
| 3.b. | Circuit miles of overhead distribution lines (including WUI and non-WUI) | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Circuit miles | SCE does not routinely track planned additions or removals by population density or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map all projects in GIS and subdivide as requested. SCE is also seeking to improve its processes associated with this WMP requirement.
| 3.c. | Circuit miles of overhead transmission lines in WUI | 0 | 0 | 0 | 0.26 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Circuit miles in WUI
| 3.d. | Circuit miles of overhead distribution lines in WUI | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Circuit miles in WUI | SCE does not routinely track planned additions or removals by population density or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map all projects in GIS and subdivide as requested. SCE is also seeking to improve its processes associated with this WMP requirement.
| 3.e. | Number of substations (including WUI and non-WUI) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of substations
| 3.f. | Number of substations in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of substations in WUI
| 3.g. | Number of weather stations (including WUI and non-WUI) | 11 | 0 | 91 | 102 | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Number of weather stations | Actual site/structure locations have not yet been determined and SCE is therefore unable to provide the locational attributes as requested
| 3.h. | Number of weather stations in WUI | 0 | 0 | 2 | 2 | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Number of weather stations in WUI | Actual site/structure locations have not yet been determined and SCE is therefore unable to provide the locational attributes as requested

## Table 10
Utility | Southern California Edison Company | Notes:
Table No. | 10 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.
Date Modified | 2022-02-11 | In future submissions update planned upgrade numbers with actuals
|  | In the comments column on the far-right, enter the relevant program target(s) associated | Actual |  |  |  | Projected
Table 10: Location of actual and planned utility infrastructure upgrades year over year |  |  | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3
Metric type | # | Outcome metric name | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
1. Planned utility infrastructure upgrades year over year - in urban areas | 1.a. | Circuit miles of overhead transmission lines planned for upgrades (including WUI and non-WUI) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Circuit miles | SCE does not routinely track planned upgrades by population density or WUI but has endeavored to provide this data where feasible. SCE is also seeking to improve its processes associated with this WMP requirement.
| 1.b. | Circuit miles of overhead distribution lines planned for upgrades (including WUI and non-WUI) | 4.71 | 0.03 | 16.43 | 46.17 | 32.25 | 0.02 | 63.91 | 252.59 | 35.2 | 0 | 73.49 | 149.41 | Circuit miles | SCE does not routinely track planned upgrades by population density or WUI but has endeavored to provide this data where feasible. SCE is also seeking to improve its processes associated with this WMP requirement.
| 1.c. | Circuit miles of overhead transmission lines planned for upgrades in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Circuit miles in WUI | SCE does not routinely track planned upgrades by population density or WUI but has endeavored to provide this data where feasible. SCE is also seeking to improve its processes associated with this WMP requirement.
| 1.d. | Circuit miles of overhead distribution lines planned for upgrades in WUI | 4.32 | 0.03 | 16.06 | 44.94 | 16.42 | 0.02 | 62.32 | 247.05 | 28.45 | 0 | 66.77 | 148.11 | Circuit miles in WUI | SCE does not routinely track planned upgrades by population density or WUI but has endeavored to provide this data where feasible. SCE is also seeking to improve its processes associated with this WMP requirement.
| 1.e. | Number of substations planned for upgrades (including WUI and non-WUI) | 1 | 0 | 6 | 1 | 4 | 0 | 1 | 2 | 5 | 0 | 0 | 2 | Number of substations | SCE does not routinely track planned upgrades by population density or WUI but has endeavored to provide this data where feasible. SCE is also seeking to improve its processes associated with this WMP requirement.
| 1.f. | Number of substations planned for upgrades in WUI | 1 | 0 | 4 | 1 | 1 | 0 | 1 | 2 | 2 | 0 | 0 | 2 | Number of substations in WUI | SCE does not routinely track planned upgrades by population density or WUI but has endeavored to provide this data where feasible. SCE is also seeking to improve its processes associated with this WMP requirement.
| 1.g. | Number of weather stations planned for upgrades (including WUI and non-WUI) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of weather stations | SCE does not routinely track planned upgrades by population density or WUI but has endeavored to provide this data where feasible. SCE is also seeking to improve its processes associated with this WMP requirement.
| 1.h. | Number of weather stations planned for upgrades in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of weather stations in WUI | SCE does not routinely track planned upgrades by population density or WUI but has endeavored to provide this data where feasible. SCE is also seeking to improve its processes associated with this WMP requirement.
2. Planned utility infrastructure upgrades year over year - in rural areas | 2.a. | Circuit miles of overhead transmission lines planned for upgrades (including WUI and non-WUI) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Circuit miles | SCE does not routinely track planned upgrades by population density or WUI but has endeavored to provide this data where feasible. SCE is also seeking to improve its processes associated with this WMP requirement.
| 2.b. | Circuit miles of overhead distribution lines planned for upgrades (including WUI and non-WUI) | 9.52 | 0 | 92.99 | 390.43 | 60.69 | 0 | 304.88 | 938.55 | 28.75 | 0 | 186.87 | 268.34 | Circuit miles | SCE does not routinely track planned upgrades by population density or WUI but has endeavored to provide this data where feasible. SCE is also seeking to improve its processes associated with this WMP requirement.
| 2.c. | Circuit miles of overhead transmission lines planned for upgrades in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Circuit miles in WUI | SCE does not routinely track planned upgrades by population density or WUI but has endeavored to provide this data where feasible. SCE is also seeking to improve its processes associated with this WMP requirement.
| 2.d. | Circuit miles of overhead distribution lines planned for upgrades in WUI | 7.36 | 0 | 58.52 | 296.18 | 47.94 | 0 | 247.84 | 763.86 | 19.87 | 0 | 132.5 | 202.15 | Circuit miles in WUI | SCE does not routinely track planned upgrades by population density or WUI but has endeavored to provide this data where feasible. SCE is also seeking to improve its processes associated with this WMP requirement.
| 2.e. | Number of substations planned for upgrades (including WUI and non-WUI) | 0 | 0 | 0 | 4 | 2 | 0 | 1 | 2 | 2 | 0 | 3 | 2 | Number of substations | SCE does not routinely track planned upgrades by population density or WUI but has endeavored to provide this data where feasible. SCE is also seeking to improve its processes associated with this WMP requirement.
| 2.f. | Number of substations planned for upgrades in WUI | 0 | 0 | 0 | 4 | 1 | 0 | 1 | 2 | 2 | 0 | 2 | 2 | Number of substations in WUI | SCE does not routinely track planned upgrades by population density or WUI but has endeavored to provide this data where feasible. SCE is also seeking to improve its processes associated with this WMP requirement.
| 2.g. | Number of weather stations planned for upgrades (including WUI and non-WUI) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of weather stations | SCE does not routinely track planned upgrades by population density or WUI but has endeavored to provide this data where feasible. SCE is also seeking to improve its processes associated with this WMP requirement.
| 2.h. | Number of weather stations planned for upgrades in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of weather stations in WUI | SCE does not routinely track planned upgrades by population density or WUI but has endeavored to provide this data where feasible. SCE is also seeking to improve its processes associated with this WMP requirement.
3. Planned utility infrastructure upgrades year over year - in highly rural areas | 3.a. | Circuit miles of overhead transmission lines planned for upgrades (including WUI and non-WUI) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Circuit miles | SCE does not routinely track planned upgrades by population density or WUI but has endeavored to provide this data where feasible. SCE is also seeking to improve its processes associated with this WMP requirement.
| 3.b. | Circuit miles of overhead distribution lines planned for upgrades (including WUI and non-WUI) | 2.98 | 0 | 121.22 | 88.83 | 30.93 | 0 | 109.61 | 381.79 | 19.21 | 0 | 108.52 | 149.68 | Circuit miles | SCE does not routinely track planned upgrades by population density or WUI but has endeavored to provide this data where feasible. SCE is also seeking to improve its processes associated with this WMP requirement.
| 3.c. | Circuit miles of overhead transmission lines planned for upgrades in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Circuit miles in WUI | SCE does not routinely track planned upgrades by population density or WUI but has endeavored to provide this data where feasible. SCE is also seeking to improve its processes associated with this WMP requirement.
| 3.d. | Circuit miles of overhead distribution lines planned for upgrades in WUI | 0.1 | 0 | 1.79 | 2.16 | 0.43 | 0 | 1.45 | 12.12 | 0.12 | 0 | 2.18 | 2.58 | Circuit miles in WUI | SCE does not routinely track planned upgrades by population density or WUI but has endeavored to provide this data where feasible. SCE is also seeking to improve its processes associated with this WMP requirement.
| 3.e. | Number of substations planned for upgrades (including WUI and non-WUI) | 5 | 0 | 1 | 3 | 1 | 0 | 2 | 2 | 8 | 0 | 8 | 5 | Number of substations | SCE does not routinely track planned upgrades by population density or WUI but has endeavored to provide this data where feasible. SCE is also seeking to improve its processes associated with this WMP requirement.
| 3.f. | Number of substations planned for upgrades in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of substations in WUI | SCE does not routinely track planned upgrades by population density or WUI but has endeavored to provide this data where feasible. SCE is also seeking to improve its processes associated with this WMP requirement.
| 3.g. | Number of weather stations planned for upgrades (including WUI and non-WUI) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of weather stations | SCE does not routinely track planned upgrades by population density or WUI but has endeavored to provide this data where feasible. SCE is also seeking to improve its processes associated with this WMP requirement.
| 3.h. | Number of weather stations planned for upgrades in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of weather stations in WUI | SCE does not routinely track planned upgrades by population density or WUI but has endeavored to provide this data where feasible. SCE is also seeking to improve its processes associated with this WMP requirement.

## Table 11
Utility | Southern California Edison Company | Notes:
Table No. | 11 | "PSPS" = Public Safety Power Shutoff | [19 empty] | 1
Date Modified | 2022-02-11 | In future submissions update planned upgrade numbers with actuals
Note: Final QC of PSPS data is being peformed. Updated statistics of SCE's 2021 PSPS season will be provided in SCE's March 1, 2022 PSPS Post Season Report and incorporated into future Quarterly Data Table submissions' |  |  | Actual | [12 empty] | Projected
Table 11: Recent use of PSPS and other PSPS metrics | [7 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Outcome metric name | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
1. Recent use of PSPS | 1.a. | Frequency of PSPS events (total) | 0 | 0 | 1 | 3 | 7 | 0 | 0 | 2 | 8 | 1 | 1 | 1 | 5 | 0 | 0 | 2 | 6 | Number of instances where utility operating protocol requires de-energization of a circuit or portion thereof to reduce ignition probability, per year. Only include events in which de-energization ultimately occurred | During 2020, SCE initiated 12 PSPS events (2 of which SCE did not de-energize, Table 11, Metric Type 5.a.) with 16 periods of concern, i.e., periods of time when de-energization was likely to occur due to forecast weather and fuel conditions, 16 relates to periods of concerns. For Q2-Q4 2021 time periods, SCE used 2020 recorded data adjusted for improvement expected based on SCE's planned wildfire mitigation activities to create a baseline. To factor in weather variability, which has significant impacts on PSPS events, SCE developed a range around the baseline. The range was based on an 18 year backcast analysis that analyzed how current PSPS triggers would have resulted in PSPS events when applied to historical weather data. For further details on calculating the range, please see section 8.5
| 1.b. | Scope of PSPS events (total) | 0 | 0 | 7 | 6 | 267 | 0 | 0 | 7 | 417 | 160 | 1 | 1 | 122 | 0 | 0 | 13 | 182 | Circuit-events, measured in number of events multiplied by number of circuits de-energized per year | SCE interprets this line item as de-energized circuit count. Additionally, the numbers being reported may not align with the ESRB-8 report because that report uses preliminary operations data that has not been fully validated. For Q2-Q4 2021 time periods, SCE used 2020 recorded data adjusted for improvement expected based on SCE's planned wildfire mitigation activities to create a baseline. To factor in weather variability, which has significant impacts on PSPS events, SCE developed a range around the baseline. The range was based on an 18 year backcast analysis that analyzed how current PSPS triggers would have resulted in PSPS events when applied to historical weather data. For further details on calculating the range, please see section 8.5
| 1.c. | Duration of PSPS events (total) | 0 | 0 | 87019 | 3570 | 5275193 | 0 | 0 | 3981 | 4451955 | 1953961.7833 | 224 | 88 | 1745980 | 540596 | 62 | 227118 | 2469956 | Customer hours per year | For Q2-Q4 2021 time periods, SCE used 2020 recorded data adjusted for improvement expected based on SCE's planned wildfire mitigation activities to create a baseline. To factor in weather variability, which has significant impacts on PSPS events, SCE developed a range around the baseline. The range was based on an 18 year backcast analysis that analyzed how current PSPS triggers would have resulted in PSPS events when applied to historical weather data. For further details on calculating the range, please see section 8.5
2. Customer hours of PSPS and other outages | 2.a. | Customer hours of planned outages including PSPS (total) | 0 | 11067181.7 | 10406441.7833 | 9556441.9167 | 10918480.1 | 1236490.8 | 770810.9833 | 1295679.4 | 6103854.7333 | 3778267.95 | Not Currently Available | Not Currently Available | Not Currently Available | Not Currently Available | Not Currently Available | Not Currently Available | Not Currently Available | Total customer hours of planned outages per year | SCE has not traditionally calculated reliability metrics tied to planned outages. Since 2019, SCE has been improving and refining its planned outage reliability reporting, therefore the years after 2018 reflect not only actual changes but changes due to the improved process. Further, SCE does not consider PSPS to be planned outages but has included PSPS metrics in this row as requested by WSD. SCE is currently unable to provide planned outage data metrics due to recent IT system implementation issues. SCE is actively investigating this issue and will provide the data when it is available. Forecast is based on time-series forecast.
| 2.b. | Customer hours of unplanned outages, not including PSPS (total) | 8401612 | 9276813 | 7788697 | 6088158 | 7617913 | 1480964 | 1496752 | 2350456 | 2224812 | 1615913 | 1896189.1 | 3106303.7 | 173281.34 | 1688577 | 1696470.55 | 2728379.85 | 1199046.67 | Total customer hours of unplanned outages per year | Forecast is based on time-series forecast.
| 2.c. | System Average Interruption Duration Index (SAIDI) (including PSPS) | 100.1517 | 241.208 | 214.2783 | 183.0854 | 215.9119 | 31.4562 | 26.2485 | 42.2063 | 96.4095 | 63.0777 | Not Currently Available | Not Currently Available | Not Currently Available | Not Currently Available | Not Currently Available | Not Currently Available | Not Currently Available | SAIDI index value = sum of all interruptions in time period where each interruption is defined as sum(duration of interruption * # of customer interruptions) / Total number of customers served | SCE has not traditionally calculated reliability metrics tied to planned outages. Since 2019, SCE has been improving and refining its planned outage reliability reporting, therefore the years after 2018 reflect not only actual changes but changes due to the improved process. Further, SCE does not consider PSPS to be planned outages but has included PSPS metrics in this row as requested by WSD. SCE is currently unable to provide planned outage data metrics due to recent IT system implementation issues. SCE is actively investigating this issue and will provide the data when it is available. Forecast is based on time-series forecast.
| 2.d. | System Average Interruption Duration Index (SAIDI) (excluding PSPS) | 100.1517 | 241.208 | 213.2535 | 183.0436 | 154.4665 | 31.4562 | 26.2484 | 42.1602 | 44.8753 | 39.7594 | Not Currently Available | Not Currently Available | Not Currently Available | Not Currently Available | Not Currently Available | Not Currently Available | Not Currently Available | SAIDI index value = sum of all interruptions in time period where each interruption is defined as sum(duration of interruption * # of customer interruptions) / Total number of customers served | SCE has not traditionally calculated reliability metrics tied to planned outages. Since 2019, SCE has been improving and refining its planned outage reliability reporting, therefore the years after 2018 reflect not only actual changes but changes due to the improved process. Forecast is based on time-series forecast. SCE is currently unable to provide planned outage data metrics due to recent IT system implementation issues. SCE is actively investigating this issue and will provide the data when it is available.
| 2.e. | System Average Interruption Frequency Index (SAIFI) (including PSPS) | 1.1639 | 1.3346 | 1.2033 | 1.029 | 1.1054 | 0.22238 | 0.21626 | 0.28152 | 0.32123 | 0.29281 | Not Currently Available | Not Currently Available | Not Currently Available | Not Currently Available | Not Currently Available | Not Currently Available | Not Currently Available | SAIFI index value = sum of all interruptions in time period where each interruption is defined as (total # of customer interruptions) / (total # of customers served) | SCE has not traditionally calculated reliability metrics tied to planned outages. Since 2019, SCE has been improving and refining its planned outage reliability reporting, therefore the years after 2018 reflect not only actual changes but changes due to the improved process. Further, SCE does not consider PSPS to be planned outages but has included PSPS metrics in this row as requested by WSD. SCE is currently unable to provide planned outage data metrics due to recent IT system implementation issues. SCE is actively investigating this issue and will provide the data when it is available. Forecast is based on time-series forecast.
| 2.f. | System Average Interruption Frequency Index (SAIFI) (excluding PSPS) | 1.1639 | 1.3346 | 1.2027 | 1.029 | 1.0668 | 0.22238 | 0.21626 | 0.28147 | 0.27915 | 0.26995 | Not Currently Available | Not Currently Available | Not Currently Available | Not Currently Available | Not Currently Available | Not Currently Available | Not Currently Available | SAIFI index value = sum of all interruptions in time period where each interruption is defined as (total # of customer interruptions) / (total # of customers served) | SCE is currently unable to provide planned outage data metrics due to recent IT system implementation issues. SCE is actively investigating this issue and will provide the data when it is available. Forecast is based on time-series forecast.
3. Critical infrastructure impacted by PSPS | 3.a. | Critical infrastructure impacted by PSPS | 0 | 0 | NA | NA | 5868 | 0 | 0 | 12 | 5123 | 2066 | 78 | 3 | 2497 | 857.39 | 32.37 | 6.225 | 3162.3 | Number of critical infrastructure (in accordance with D.19-05-042) locations impacted per hour multiplied by hours offline per year | The numbers being reported may not align with the ESRB-8 report because that report uses preliminary operations data that has not been fully validated. SCE also notes, that earlier PSPS events were not tracked and recorded in the same level of detail as it is now, therefore not all data is available. For Q2-Q4 2021 time periods, SCE used 2020 recorded data adjusted for improvement expected based on SCE's planned wildfire mitigation activities to create a baseline. To factor in weather variability, which has significant impacts on PSPS events, SCE developed a range around the baseline. The range was based on an 18 year backcast analysis that analyzed how current PSPS triggers would have resulted in PSPS events when applied to historical weather data. For further details on calculating the range, please see section 8.5 Historical data was updated as a typing error was discovered.
4. Community outreach of PSPS metrics | 4.a. | # of customers impacted by PSPS | 0 | 0 | 2861 | 112 | 198826 | 0 | 0 | 270 | 229530 | 116349 | 78 | 9 | 83968 | 43630.875 | 29.25 | 104.625 | 117561.75 | # of customers impacted by PSPS (if multiple PSPS events impact the same customer, count each event as a separate customer) | The numbers being reported may not align with the ESRB-8 report because that report uses preliminary operations data that has not been fully validated. For Q2-Q4 2021 time periods, SCE used 2020 recorded data adjusted for improvement expected based on SCE's planned wildfire mitigation activities to create a baseline. To factor in weather variability, which has significant impacts on PSPS events, SCE developed a range around the baseline. The range was based on an 18 year backcast analysis that analyzed how current PSPS triggers would have resulted in PSPS events when applied to historical weather data. For further details on calculating the range, please see section 8.5
| 4.b. | # of medical baseline customers impacted by PSPS | 0 | 0 | NA | NA | 4043 | 0 | 0 | 11 | 7725 | 3415 | 2 | 0 | 3174 | 1280.625 | 0.75 | 4.125 | 4087.125 | # of customers impacted by PSPS (if multiple PSPS events impact the same customer, count each event as a separate customer) | The numbers being reported may not align with the ESRB-8 report because that report uses preliminary operations data that has not been fully validated. SCE also notes, that earlier PSPS events were not tracked and recorded in the same level of detail as it is now, therefore not all data is available. For Q2-Q4 2021 time periods, SCE used 2020 recorded data adjusted for improvement expected based on SCE's planned wildfire mitigation activities to create a baseline. To factor in weather variability, which has significant impacts on PSPS events, SCE developed a range around the baseline. The range was based on an 18 year backcast analysis that analyzed how current PSPS triggers would have resulted in PSPS events when applied to historical weather data. For further details on calculating the range, please see section 8.5
| 4.c. | # of customers notified prior to initiation of PSPS event | 0 | 0 | NA | NA | 155824 | 0 | 0 | 232 | 143908 | 110217 | 66 | 0 | 78120 | 41449.3312 | 27.7875 | 99.3937 | 111683.6625 | # of customers notified of PSPS event prior to initiation (if multiple PSPS events impact the same customer, count each event in which customer was notified as a separate customer) | The numbers being reported may not align with the ESRB-8 report because that report uses preliminary operations data that has not been fully validated. SCE also notes, that earlier PSPS events were not tracked and recorded in the same level of detail as it is now, therefore not all data is available.
| 4.d. | # of medical baseline customers notified prior to initiation of PSPS event | 0 | 0 | NA | NA | 3044 | 0 | 0 | 15 | 7531 | 3138 | 2 | 0 | 2136 | 1216.5938 | 0.7125 | 3.9187 | 3882.7687 | # of customers notified of PSPS event prior to initiation (if multiple PSPS events impact the same customer, count each event in which customer was notified as a separate customer) | The numbers being reported may not align with the ESRB-8 report because that report uses preliminary operations data that has not been fully validated. SCE also notes, that earlier PSPS events were not tracked and recorded in the same level of detail as it is now, therefore not all data is available.
| 4.e. | % of customers notified prior to a PSPS event impacting them | 0 | 0 | NA | NA | 78% | 0 | 0 | 84.67% | 62.42% | 94.73% | 84.62% | 0% | 93.04% | 95% | 95% | 95% | 95% | =4.c. / 4.a. | SCE also notes, that earlier PSPS events were not tracked and recorded in the same level of detail as it is now, therefore not all data is available.
| 4.f. | % of medical baseline customers notified prior to a PSPS event impacting them | 0 | 0 | NA | NA | 75% | 0 | 0 | 100% | 88.26% | 91.89% | 100% | 0% | 67.3% | 95% | 95% | 95% | 95% | =4.d. / 4.b. | SCE also notes, that earlier PSPS events were not tracked and recorded in the same level of detail as it is now, therefore not all data is available.
5. Other PSPS metrics | 5.a. | Number of PSPS events triggered where no de-energization occurred | 0 | 0 | NA | NA | 7 | 0 | 2 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2 | 2 | 0 | Number of instances where utility notified the public of a potential PSPS event but no de-energization followed | SCE also notes, that earlier PSPS events were not tracked and recorded in the same level of detail as it is now, therefore not all data is available.
| 5.b. | Number of customers located on de-energized circuit | 0 | 0 | NA | NA | 237666 | 0 | 0 | 5820 | 407853 | 597448 | 78 | 9 | 155522 | 0 | 0 | 18725 | 262154 | Number of customers | This data includes the number of customers on a circuit whether they were de-energized or not For Q2-Q4 2021 time periods, SCE used 2020 recorded data adjusted for improvement expected based on SCE's planned wildfire mitigation activities to create a baseline. To factor in weather variability, which has significant impacts on PSPS events, SCE developed a range around the baseline. The range was based on an 18 year backcast analysis that analyzed how current PSPS triggers would have resulted in PSPS events when applied to historical weather data. For further details on calculating the range, please see section 8.5 SCE also notes, that earlier PSPS events were not tracked and recorded in the same level of detail as it is now, therefore not all data is available.
| 5.c. | Customer hours of PSPS per RFW OH circuit mile day | 0 | 0 | NA | NA | NA | 0 | 0 | 17 | 434 | 875.0389 | 11 | 0 | 491 | 363 | 5 | 7 | 384 | =1.c. / RFW OH circuit mile days in time period | For Q2-Q4 2021 time periods, SCE used 2020 recorded data adjusted for improvement expected based on SCE's planned wildfire mitigation activities to create a baseline. To factor in weather variability, which has significant impacts on PSPS events, SCE developed a range around the baseline. The range was based on an 18 year backcast analysis that analyzed how current PSPS triggers would have resulted in PSPS events when applied to historical weather data. For further details on calculating the range, please see section 8.5 SCE also notes, that earlier PSPS events were not tracked and recorded in the same level of detail as it is now, therefore not all data is available. Historical numbers were corrected as the original anlaysis methodology was found to be faulty. Additionally, Since historical numbers were adjusted, the forecast numbers were re-forecasted.
| 5.d. | Frequency of PSPS events (total) - High Wind Warning wind conditions | 0 | 0 | NA | NA | NA | 0 | 0 | 1 | 8 | 1 | 1 | 0 | 2 | 1 | 1 | 1 | 5 | Events over time period that overlapped with a High Wind Warning as defined by the National Weather Service | For Q2-Q4 2021 time periods, SCE used 2020 recorded data adjusted for improvement expected based on SCE's planned wildfire mitigation activities to create a baseline. To factor in weather variability, which has significant impacts on PSPS events, SCE developed a range around the baseline. The range was based on an 18 year backcast analysis that analyzed how current PSPS triggers would have resulted in PSPS events when applied to historical weather data. For further details on calculating the range, please see section 8.5 SCE also notes, that earlier PSPS events were not tracked and recorded in the same level of detail as it is now, therefore not all data is available. Historical numbers were corrected as the original anlaysis methodology was found to be faulty. Additionally, Since historical numbers were adjusted, the forecast numbers were re-forecasted.
| 5.e. | Scope of PSPS events (total) - High Wind Warning wind conditions | 0 | 0 | NA | NA | NA | 0 | 0 | 7 | 392 | 151 | 1 | 0 | 88 | 57 | 1 | 3 | 180 | Estimated customers impacted over time period that overlapped with a High Wind Warning as defined by the National Weather Service | For Q2-Q4 2021 time periods, SCE used 2020 recorded data adjusted for improvement expected based on SCE's planned wildfire mitigation activities to create a baseline. To factor in weather variability, which has significant impacts on PSPS events, SCE developed a range around the baseline. The range was based on an 18 year backcast analysis that analyzed how current PSPS triggers would have resulted in PSPS events when applied to historical weather data. For further details on calculating the range, please see section 8.5 SCE also notes, that earlier PSPS events were not tracked and recorded in the same level of detail as it is now, therefore not all data is available. SCE interprets this line item as de-energized circuit counts that overlap with High Wind Warnings. Historical numbers were corrected as the original anlaysis methodology was found to be faulty. Additionally, since historical numbers were adjusted, the forecast numbers were re-forecasted.
| 5.f. | Duration of PSPS events (total) - High Wind Warning wind conditions | 0 | 0 | NA | NA | NA | 0 | 0 | 3499.5 | 4298691.8 | 1826480 | 4 | 0 | 1741266 | 757989 | 2 | 1452 | 2506582 | Customer hours over time period that overlapped with a High Wind Warning as defined by the National Weather Service | For Q2-Q4 2021 time periods, SCE used 2020 recorded data adjusted for improvement expected based on SCE's planned wildfire mitigation activities to create a baseline. To factor in weather variability, which has significant impacts on PSPS events, SCE developed a range around the baseline. The range was based on an 18 year backcast analysis that analyzed how current PSPS triggers would have resulted in PSPS events when applied to historical weather data. For further details on calculating the range, please see section 8.5 SCE also notes, that earlier PSPS events were not tracked and recorded in the same level of detail as it is now, therefore not all data is available. Historical numbers were corrected as the original anlaysis methodology was found to be faulty. Additionally, Since historical numbers were adjusted, the forecast numbers were re-forecasted.

## Table 12
Utility | Southern California Edison Company | Notes:
Table No. | 12 | Risk-Spend-Efficiency (RSE) is defined as "An estimate of the cost-effectiveness of initiative, calculated by dividing the mitigation risk reduction benefit by the mitigation cost estimate based on the full set of risk reduction benefits estimated from the incurred costs."
Date Modified | 2022-02-11 | CAPEX = Capital expenditure; OPEX = Operating expenditure. In future submissions update planned spend, line miles treated, RSE, etc. with updated projections and actuals. Additional instructions can be found in QR information.
|  | Regarding the Territory and HFTD split requested per the 2022 WMP Update Guidelines, SCE has taken three approaches. (1) Wildfire activities – SCE deploys its wildfire activity spend to mitigate risk in the HFTD. Accordingly, spend for wildfire activities is shown as entirely within HFTD (i.e., Territory spend = HFTD spend). (2) Vegetation management to achieve clearances around electric lines and equipment – SCE is complying with the 2022 WMP Update Guidelines by setting forth these costs broken down by HFTD and Non-HFTD. SCE notes, however, that this estimate reflects SCE’s attempt to reasonably allocate these costs across its service area pursuant to respective tree counts and trim cadences in the HFTD and Non-HFTD areas, respectively. From an operational perspective, though, the same vegetation management contract crews often work in both HFTD and Non-HFTD areas, sometimes on the same days, making it difficult to precisely calculate the costs incurred in different areas. SCE further notes that from a regulatory cost recovery perspective, the CPUC’s SCE 2021 General Rate Case Final Decision (D.21-08-036) authorized a Vegetation Management Balancing Account (VMBA) that does not differentiate between HFTD and Non-HFTD areas. Accordingly, SCE records all vegetation management line clearance costs in the VMBA, irrespective of where the trims take place. (3) Non-wildfire activities – SCE does not track the HFTD vs. Non-HFTD split of its non-wildfire activities. Accordingly, all spend for these activities is simply shown in the Territory column, though this is not to imply that no spend occurs in the HFTD areas. | [16 empty] | Actual | [20 empty] | Projected | [6 empty] | Projected
[19 empty] | 1112295.703 | 649079.703 | 772975.0578 | 591817.0947 |  |  |  | 1150909.8236 | 769836.8236 | 797303.2027 | 587086.1787 |  |  |  | 1708649.9646 | 1106244.9646 | 771576.0872 | 552607.8093 |  |  |  | 1622205.9993 | 978740.8783 | 801519.9556 | 641642.7139 |  |  |  | 1608272.984 | 962562.109 | 777538.0607 | 628822.9103
Table 12: Mitigation initiative financials | [18 empty] | CAPEX ($ thousands) |  | OPEX ($ thousands) |  | Line miles treated |  | Alternative units (if used) | CAPEX ($ thousands) |  | OPEX ($ thousands) |  | Line miles treated |  | Alternative units (if used) | CAPEX ($ thousands) |  | OPEX ($ thousands) |  | Line miles treated |  | Alternative units (if used) | CAPEX ($ thousands) |  | OPEX ($ thousands) |  | Line miles to be treated |  | Alternative units (if used) | CAPEX ($ thousands) |  | OPEX ($ thousands) |  | Line miles to be treated |  | Alternative units (if used)
[19 empty] | Territory | HFTD | Territory | HFTD | Territory | HFTD |  | Territory | HFTD | Territory | HFTD | Territory | HFTD |  | Territory | HFTD | Territory | HFTD | Territory | HFTD |  | Territory | HFTD | Territory | HFTD | Territory | HFTD |  | Territory | HFTD | Territory | HFTD | Territory | HFTD
Metric type | WMP Table # / Category | 2022 WMP Initiative # | Initiative activity | 2022 WMP ID | Primary driver targeted | Secondary driver targeted | Year initiated | Estimated RSE territory-wide | Estimated RSE in non-HFTD region | Estimated RSE in HFTD Zone 1 | Estimated RSE in HFTD Tier 2 | Estimated RSE in HFTD Tier 3 | If existing: most recent proceeding that has reviewed program | If new: memorandum account | Current compiance status - In / exceeding compliance with regulations | Associated rule(s) - if multiple, separate by semi-colon - ";" | If spend not disaggregated by category, note spend category or mark general operations | Comments | 2019 | [6 empty] | 2020 | [6 empty] | 2021 | [6 empty] | 2022 | [6 empty] | 2023
Other | Risk Assessment & Mapping | 7.3.1.1 | A summarized risk map that shows the overall ignition probability and estimated wildfire consequence along the electric lines and equipment |  |  |  |  | N/A | N/A | N/A | N/A | N/A
Other | Risk Assessment & Mapping | 7.3.1.2 | Climate-driven risk map and modelling based on various relevant weather scenarios |  |  |  |  | N/A | N/A | N/A | N/A | N/A
Other | Risk Assessment & Mapping | 7.3.1.3 | Ignition probability mapping showing the probability of ignition along the electric lines and equipment |  |  |  |  | N/A | N/A | N/A | N/A | N/A
Other | Risk Assessment & Mapping | 7.3.1.4 | Initiative mapping and estimation of wildfire and PSPS risk-reduction impact |  |  |  |  | N/A | N/A | N/A | N/A | N/A
Other | Risk Assessment & Mapping | 7.3.1.5 | Match drop simulations showing the potential wildfire consequence of ignitions that occur along the electric lines and equipment |  |  |  |  | N/A | N/A | N/A | N/A | N/A
Other | Situational Awareness & Forecasting | 7.3.2.1 | Advanced weather monitoring and weather stations | SA-1 | PSPS - for sectionalization, etc. |  | 2018 | 1.2257 | 0.54806 | N/A | 1.7263 | 1.5341 |  | GSRPBA |  |  |  |  | 4282 | 4282 | 1244.1383 | 1244.1383 |  |  | 352 | 7508.8599 | 7508.8599 | 2073.4879 | 2073.4879 |  |  | 593 | 5607.2372 | 5607.2372 | 2022.9986 | 2022.9986 |  |  | 406 | 3020.6941 | 3020.6941 | 3369.244 | 3369.244 |  |  | 175 | 1445.4262 | 1445.4262 | 3394.1187 | 3394.1187 |  |  | 95
Other | Situational Awareness & Forecasting | 7.3.2.2.1 | Continuous monitoring sensors | SA-9 |  |  | 2018 | N/A | N/A | N/A | N/A | N/A |  | GSRPBA; WMPMA |  |  |  |  | 3445 | 3445 | 154.0196 | 154.0196 |  |  | 60 | 260.4045 | 260.4045 | 215.1821 | 215.1821 |  |  | 60 | 8362.0962 | 8362.0962 | 134.7077 | 134.7077 |  |  | 130 | 100 | 100 | 299 | 299 | [5 empty] | 294.1401 | 294.1401
Other | Situational Awareness & Forecasting | 7.3.2.2.2 | Continuous monitoring sensors | SA-10 | PSPS - for sectionalization, etc. |  | 2018 | 585.6398 | 599.9016 | N/A | 551.72 | 595.7085 |  | NA |  |  |  |  | 970 | 970 | 469.0158 | 469.0158 |  |  | 91 | 94.0863 | 94.0863 | 2235.2265 | 2235.2265 |  |  | 5 |  |  | 2993.755 | 2993.755 |  |  | 0 | 127.5 | 127.5 | 3906 | 3906 |  |  | 20 Additional HD Cameras | 128.9584 | 128.9584 | 4403.8691 | 4403.8691 |  |  | 20 Additional HD Cameras
Other | Situational Awareness & Forecasting | 7.3.2.3 | Fault indicators for detecting faults on electric lines and equipment |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A |  | NA
Other | Situational Awareness & Forecasting | 7.3.2.3.2 | Forecast of a fire risk index, fire potential index, or similar | SA-8 | PSPS - for sectionalization, etc. |  | 2019 | 104.6514 | 94.2322 | N/A | 104.9088 | 113.9598 |  | NA | [6 empty] | 870.7121 | 870.7121 |  |  |  | 0 | 0 | 1635.9169 | 1635.9169 | [5 empty] | 2755.2893 | 2755.2893 | [5 empty] | 2872.801 | 2872.801 | [5 empty] | 2850.4007 | 2850.4007
Other | Situational Awareness & Forecasting | 7.3.2.4.1 | Forecast of a fire risk index, fire potential index, or similar |  |  |  |  | N/A | N/A | N/A | N/A | N/A
Other | Situational Awareness & Forecasting | 7.3.2.4.2 | Forecast of a fire risk index, fire potential index, or similar |  |  |  | 2019 | N/A | N/A | N/A | N/A | N/A |  | FRMMA
Other | Situational Awareness & Forecasting | 7.3.2.4.3 | Forecast of a fire risk index, fire potential index, or similar |  |  |  | 2020 | N/A | N/A | N/A | N/A | N/A |  | WMPMA
Other | Situational Awareness & Forecasting | 7.3.2.4.4 | Forecast of a fire risk index, fire potential index, or similar |  |  |  |  | N/A | N/A | N/A | N/A | N/A |  | WMPMA | [16 empty] | 14000
Other | Situational Awareness & Forecasting | 7.3.2.5 | Personnel monitoring areas of electric lines and equipment in elevated fire risk conditions | SA-3 | PSPS - for sectionalization, etc. |  | 2018 | 114.5239 | 103.1218 | N/A | 114.8056 | 124.7104 |  | NA |  |  |  |  | 6486.703 | 6486.703 | 1384.3314 | 1384.3314 |  |  |  | 4105.9963 | 4105.9963 | 1657.6793 | 1657.6793 |  |  |  | 3500.3805 | 3500.3805 | 3014.4564 | 3014.4564 |  |  | 2 High Performance Computing Clusters (HPCC) | 703 | 703 | 3234.714 | 3234.714 |  |  | 500 Weather Stations with ML Capability |  |  | 2748.8362 | 2748.8362 |  |  | TBD
Other | Situational Awareness & Forecasting | 7.3.2.6 | Weather forecasting and estimating impacts on electric lines and equipment |  |  |  | 2018 | N/A | N/A | N/A | N/A | N/A |  | GSRPBA; WMPMA | [16 empty] | 14000
Other | Situational Awareness & Forecasting | 7.3.2.6 | Weather forecasting and estimating impacts on electric lines and equipment |  |  |  |  | N/A | N/A | N/A | N/A | N/A |  | FRMMA | [16 empty] | 14000
Grid hardening | Grid Design & System Hardening | 7.3.3.1 | Capacitor maintenance and replacement program |  |  |  | NA | N/A | N/A | N/A | N/A | N/A |  | NA |  |  |  | Costs for this initiative are included as part of 7.3.4.9.1
Grid hardening | Grid Design & System Hardening | 7.3.3.2 | Circuit breaker maintenance and installation to de-energize lines upon detecting a fault | SH-6 | Equipment failure | Other contact with object | 2018 | 17872.8816 | N/A | N/A | 14360.7511 | 20374.1527 |  | GSRPBA |  |  |  |  | 839 | 839 | 419.7767 | 419.7767 |  |  | 156 | 9785.6956 | 9785.6956 | -9.2988 | -9.2988 |  |  | 109 | 5152.9578 | 5152.9578 | 13.6472 | 13.6472 |  |  | 95 | 10193.0328 | 10193.0328 |  |  |  |  | 125 | 3312.2523 | 3312.2523 | 3522.5414 | 3522.5414 |  |  | 114
Grid hardening | Grid Design & System Hardening | 7.3.3.3.1 | Covered conductor installation | SH-1 | Other contact with object | Wire-to-wire contact | 2018 | WCCP: 7,884 FR Poles: 3,725 | N/A | N/A | WCCP: 6,741 FR Poles: 3,758 | WCCP: 8,630 FR Poles: 3,708 |  | GSRPBA |  |  |  | Recorded spend reflects WCCP program only, while miles also include covered conductor installed in HFTD under other programs (95, 185, and 77 miles of non-WCCP in 2019, 2020, and 2021, respectively) | 239911 | 239911 | 0 | 0 |  |  | 372 | 546151.289 | 546151.289 | 0 | 0 |  |  | 982 | 897599.925 | 897599.925 | 544.928 | 544.928 |  |  | 1504 | 719109.567 | 719109.567 | 1450 | 1450 |  |  | 1250 | 765804.9358 | 765804.9358 | 857.0888 | 857.0888 |  |  | 1250
Grid hardening | Grid Design & System Hardening | 7.3.3.3.2 | Covered conductor installation | SH-10 | Equipment failure | Other contact with object | 2018 | 12847.1478 | 9794.5596 | N/A | 8369.8423 | 15264.6716 |  | GSRPBA |  |  |  |  | 9378 | 9378 |  |  |  |  | 101 | 9653.5501 | 9653.5501 | 0 | 0 |  |  | 405 | 21939.7977 | 21939.7977 |  |  |  |  | 527 | 16552.088 | 16552.088 |  |  |  |  | 700 | 16265.4667 | 16265.4667 |  |  |  |  | 500
Grid hardening | Grid Design & System Hardening | 7.3.3.3.3 | Covered conductor installation | SH-16 | Other contact with object | Wire-to-wire contact | 2022 | 537.9277 | N/A | N/A | N/A | 537.9277 |  | NA | [6 empty] | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | [12 empty] | 108.096 | 108.096 |  |  | 115 |  |  | 368.7749 | 368.7749 |  |  | 402
Grid hardening | Grid Design & System Hardening | 7.3.3.4 | Covered conductor maintenance |  |  |  |  | N/A | N/A | N/A | N/A | N/A | [5 empty] | Costs for this initiative are included as part of 7.3.4.9.1
Grid hardening | Grid Design & System Hardening | 7.3.3.5 | Crossarm maintenance, repair, and replacement |  |  |  |  | N/A | N/A | N/A | N/A | N/A | [5 empty] | Costs for this initiative are included as part of 7.3.4.9.1
Grid hardening | Grid Design & System Hardening | 7.3.3.6 | Distribution pole replacement and reinforcement, including with composite poles |  |  |  | NA | N/A | N/A | N/A | N/A | N/A |  | NA |  |  |  |  | 359296 | [6 empty] | 283684 | [6 empty] | 503097 | [6 empty] | 544811.836 | [6 empty] | 544462.377
Grid hardening | Grid Design & System Hardening | 7.3.3.7 | Expulsion fuse replacement | SH-4 | Equipment failure | Other contact with object | 2018 | 3766.9299 | 1143.1756 | N/A | 2917.6174 | 4213.3582 |  | GSRPBA |  |  |  |  | 70298 | 70298 | 258.1237 | 258.1237 |  |  | 7765 | 8955.266 | 8955.266 | 3261.7993 | 3261.7993 |  |  | 3025 | -478.5509 | -478.5509 | 35.8273 | 35.8273 |  |  | 352 |  |  | 1402.0359 | 1402.0359 |  |  | 483 |  |  | 1662.1433 | 1662.1433 |  |  | 574
Grid hardening | Grid Design & System Hardening | 7.3.3.8.1 | Grid topology improvements to mitigate or reduce PSPS events | SH-7 |  |  | 2020 | N/A | N/A | N/A | N/A | N/A | [5 empty] | This activity entails evaluating circuits highly impacted by PSPS to develop targeted plans for grid hardening and circuit modifications to reduce PSPS impact; cost resulting from this evaluation appear in 7.3.3.3.1, 7.3.3.9 and 7.3.2.1. | [7 empty] | 0 | 0 | 0 | 0 | [9 empty] | 140 Circuits identified for scoping | [6 empty] | 70 Circuits identified for scoping | [6 empty] | TBD
Grid hardening | Grid Design & System Hardening | 7.3.3.8.2 | Grid topology improvements to mitigate or reduce PSPS events | SH-12 |  |  | 2021 | N/A | N/A | N/A | N/A | N/A |  | MGOIR | [11 empty] | 0 | 0 | 0 | 0 | [10 empty] | 5393.1033 | 5393.1033 | [5 empty] | 5742.9355 | 5742.9355
Grid hardening | Grid Design & System Hardening | 7.3.3.9 | Installation of system automation equipment | SH-5 | Equipment failure | Other contact with object | 2018 | RAR: 4,946 RCS: 2,981 | RAR: 581 RCS: 2,237 | N/A | RAR: 2,889 RCS: 1,406 | RAR: 7,810 RCS: 4,597 |  | GSRPBA; FHPMA |  |  |  |  | 11112 | 11112 | 0 | 0 |  |  | 71 | 5866.6214 | 5866.6214 | 0 | 0 |  |  | 49 | 2737.9192 | 2737.9192 |  |  |  |  | 23 | 3615.3046 | 3615.3046 |  |  |  |  | 31 | TBD | TBD |  |  |  |  | TBD
Grid hardening | Grid Design & System Hardening | 7.3.3.10 | Maintenance, repair, and replacement of connectors, including hotline clamps |  |  |  |  | N/A | N/A | N/A | N/A | N/A | [5 empty] | Costs for this initiative are included as part of 7.3.4.9.1
Grid hardening | Grid Design & System Hardening | 7.3.3.11 | Mitigation of impact on customers and other residents affected during PSPS event |  |  |  |  | N/A | N/A | N/A | N/A | N/A | [5 empty] | Costs associated with mitigation of impact on customers during PSPS events are included in 7.3.6.6
Grid hardening | Grid Design & System Hardening | 7.3.3.12 | Other corrective action | SH-14 | Wire-to-wire contact | Equipment failure | 2019 | 3496.2075 | N/A | N/A | 2085.8154 | 4922.8943 |  | WMPMA |  |  |  | Additional 2021 recorded spend for this activity is included in 7.3.3.3.1 and 7.3.4.9.1 |  |  | 0 | 0 |  |  |  | 0 | 0 | 554.1823 | 554.1823 |  | 9715 |  | 91.6682 | 91.6682 |  |  |  |  | 361 | 4931.4948 | 4931.4948 | 5815.2757 | 5815.2757 |  |  | 1800 | 7617.1841 | 7617.1841 | 10479.2622 | 10479.2622 |  |  | 3586.8749
Grid hardening | Grid Design & System Hardening | 7.3.3.12.2 | Other corrective action | SH-17 | Other contact with object | Equipment failure | 2020 | 28789.4625 | 0 | N/A | N/A | 29617.8791 |  | NA | [11 empty] | 1854.5692 | 1854.5692 | 0 | 0 |  |  |  | 3668.3767 | 3668.3767 | [5 empty] | 10596.2 | 10596.2 |  |  |  |  | 1 Iso Bank | 23917.0802 | 23917.0802 |  |  |  |  | 2 GFNs
Grid hardening | Grid Design & System Hardening | 7.3.3.13 | Pole loading infrastructure hardening and replacement program based on pole loading assessment program |  |  |  | NA | N/A | N/A | N/A | N/A | N/A |  | NA |  |  |  | This is captured on Initiative 7.3.3.6.; under Distribution Pole Remediations
Grid hardening | Grid Design & System Hardening | 7.3.3.14 | Transformers maintenance and replacement |  |  |  | NA | N/A | N/A | N/A | N/A | N/A |  | NA |  |  |  |  | 102432 |  | 1162.8619 |  |  |  |  | 96432 |  | 1399.415 |  |  |  |  | 97069 |  | 1274.8208 |  |  |  |  | 98653.285 |  | 1482.3676 |  |  |  |  | 101248.498 |  | 1521.144
Grid hardening | Grid Design & System Hardening | 7.3.3.15 | Transmission tower maintenance and replacement | SH-13 | Contamination | Equipment failure | 2020 | 40.8334 | N/A | N/A | 2.3353e-14 | 64.1668 |  | WMPMA |  |  |  | Recorded 2021 spend for this activity is included in 7.3.4.10 |  |  | 0 | 0 | [16 empty] | 52 |  |  | 250 | 250 |  |  | 21 | 0 | 0 |  |  |  |  | 0
Grid hardening | Grid Design & System Hardening | 7.3.3.16 | Undergrounding of electric lines and/or equipment | SH-2 | Other contact with object | Wire-to-wire contact | 2019 | 1421.5906 | N/A | N/A | 1783.8319 | 1374.8826 |  | WMPMA | [11 empty] | 961.3883 | 961.3883 | 0 | 0 |  |  |  | 6585.8 | 6585.8 |  |  |  |  | 5.8 | 51960 | 51960 |  |  |  |  | 13 | 42664.2434 | 42664.2434 |  |  |  |  | 11
Grid hardening | Grid Design & System Hardening | 7.3.3.17.1 | Updates to grid topology to minimize risk of ignition in HFTDs | SH-8 | Equipment failure | Vandalism / Theft | 2019 | 531.5519 | N/A | N/A | 24.5338 | 904.6407 |  | WMPMA | [6 empty] | 0 | 0 |  |  | 1 | 0 | 0 | 124.6627 | 124.6627 |  |  | 6 |  |  | 945.9043 | 945.9043 |  |  | 10 |  |  | 2516 | 2516 |  |  | 11 | TBD | TBD |  |  |  |  | TBD
Grid hardening | Grid Design & System Hardening | 7.3.3.17.2 | Updates to grid topology to minimize risk of ignition in HFTDs | SH-11 | Equipment failure | Other contact with object | 2019 | 202.6623 | N/A | N/A | 55.3253 | 286.8549 |  | WMPMA | [6 empty] | 0 | 0 |  |  |  | 0 | 0 | 73.8882 | 73.8882 |  | 9715 |  | 189.9301 | 189.9301 | 132.4202 | 132.4202 |  |  | 2 Projects, 17 Assessments | 1925 | 1925 | 660 | 660 |  |  | 8 Projects, 13 Assessments | 1799.5693 | 1799.5693 | 199.185 | 199.185 |  |  | TBD
Grid hardening | Grid Design & System Hardening | 7.3.3.17.3 | Updates to grid topology to minimize risk of ignition in HFTDs | SH-15 | Equipment failure |  | 2019 | 5.3458 | N/A | N/A | 0 | 14.5099 |  | WMPMA |  |  |  | Recorded 2021 spend for this activity is included in 7.3.4.9.1 |  |  | 0 | 0 | [16 empty] | 16 | 570.1921 | 570.1921 |  |  |  |  | 25 | 374.6638 | 374.6638 |  |  |  |  | 7
Asset inspection | Asset Management & Inspections | 7.3.4.1 | Detailed inspections of distribution electric lines and equipment |  |  |  | NA | N/A | N/A | N/A | N/A | N/A | [8 empty] | 21681 | [6 empty] | 26362 | [6 empty] | 26522
Asset inspection | Asset Management & Inspections | 7.3.4.2 | Detailed inspections of transmission electric lines and equipment |  |  |  | NA | N/A | N/A | N/A | N/A | N/A | [8 empty] | 3599 | [6 empty] | 5957 | [6 empty] | 5759
Asset inspection | Asset Management & Inspections | 7.3.4.3 | Improvement of inspections | IN-8 |  |  | 2021 | Enabling | Enabling | Enabling | Enabling | Enabling |  | WMPMA |  |  |  |  | 13391 | 13391 | 1978.5651 | 1978.5651 |  |  |  | 28718.5992 | 28718.5992 | 14972.098 | 14972.098 |  | 9715 |  | 27902.9834 | 27902.9834 | 3727.0452 | 3727.0452 |  |  |  | 9504 | 9504 | 3954.7 | 3954.7 |  |  |  | 4700 | 4700 | 3146.7 | 3146.7
Asset inspection | Asset Management & Inspections | 7.3.4.4 | Infrared inspections of distribution electric lines and equipment | IN-3 | Equipment failure |  | 2017 | 560.4208 | N/A | N/A | 534.6492 | 567.4494 |  | Previously GSRPBA, Currently WMPMA | [6 empty] | 0 | 0 |  |  | 4962 | 0 | 0 | 790.7734 | 790.7734 |  | 4416 | 5900 |  |  | 464.0306 | 464.0306 |  |  | 4410 |  |  | 426.559 | 426.559 |  |  | 4400 |  |  | 430.1154 | 430.1154 |  |  | 4425
Asset inspection | Asset Management & Inspections | 7.3.4.5 | Infrared inspections of transmission electric lines and equipment | IN-4 | Equipment failure |  | 2019 | 0 | N/A | N/A | 0 | N/A |  | WMPMA | [6 empty] | 0.58991 | 0.58991 |  |  | 6700 | 0 | 0 | 383.5504 | 383.5504 |  | 1005 |  |  |  | 93.6193 | 93.6193 |  |  | 1046 |  |  | 208.687 | 208.687 |  |  | 1000 |  |  | 219.4712 | 219.4712 |  |  | 1000
Asset inspection | Asset Management & Inspections | 7.3.4.5.1 | Transmission Conductor & Splice Assessment | IN-9 | Equipment failure |  | 2022 | 0 | N/A | N/A | 0 | N/A |  | NA | [6 empty] | 0 | 0 | [19 empty] | 1500 | 1500 |  |  | 150 spans w/ Line Vue, 70 splices with X-Ray, 15 Conductor Samples |  |  | 1493.8875 | 1493.8875 |  |  | 150 spans w/ Line Vue, 70 splices with X-Ray, 15 Conductor Samples
Asset inspection | Asset Management & Inspections | 7.3.4.6 | Intrusive pole inspections |  |  |  | NA | N/A | N/A | N/A | N/A | N/A |  | Base O&M | [6 empty] | 5915.0898 |  |  |  | 147770 |  |  | 6133.0551 |  |  |  | 146621 |  |  | 5966.1738 |  |  |  | 144122 |  |  | 6951.5021 |  |  |  | 143600 |  |  | 7143.9993 |  |  |  | 143600
Asset inspection | Asset Management & Inspections | 7.3.4.7 | LiDAR inspections of distribution electric lines and equipment |  |  |  |  | N/A | N/A | N/A | N/A | N/A | [5 empty] | Costs for this initiative are included as part of 7.3.5.7
Asset inspection | Asset Management & Inspections | 7.3.4.8 | LiDAR inspections of transmission electric lines and equipment |  |  |  |  | N/A | N/A | N/A | N/A | N/A | [5 empty] | Costs for this initiative are included as part of 7.3.5.8
Asset inspection | Asset Management & Inspections | 7.3.4.9.1 | Other discretionary inspection of distribution electric lines and equipment, beyond inspections mandated by rules and regulations | IN-1.1 | Equipment failure | Other contact with object | 2018 | Distribution Ground: 2,668 Distribution Aerial: 856 | N/A | N/A | Distribution Ground: 2,712 Distribution Aerial: 921 | Distribution Ground: 2,643 Distribution Aerial: 818 |  | Previously FRMMA; GSRPBA; Currently WMPMA |  |  |  |  | 229992 | 229992 | 238512.2349 | 238512.2349 |  |  | 499192 | 85218.9688 | 85218.9688 | 105553.2628 | 105553.2628 |  |  | 367067 | 82457.7078 | 82457.7078 | 85924.8595 | 85924.8595 |  |  | 359947 | 67995.0849 | 67995.0849 | 78699.7743 | 78699.7743 |  |  | 360000 | 61871.5271 | 61871.5271 | 78274.4968 | 78274.4968 |  |  | 360000
Asset inspection | Asset Management & Inspections | 7.3.4.9.2 | Other discretionary inspection of distribution electric lines and equipment, beyond inspections mandated by rules and regulations | IN-5 | Equipment failure | Other contact with object | 2019 | See IN-1.1 | See IN-1.1 | See IN-1.1 | See IN-1.1 | See IN-1.1 |  | NA | [6 empty] | 642.6569 | 642.6569 |  |  | 449 | 0 | 0 | 402.545 | 402.545 |  |  | 268 |  |  | 149.3921 | 149.3921 |  |  | 238 |  |  | 70 | 70 |  |  | 190 |  |  | 68.8622 | 68.8622 |  |  | 190
Asset inspection | Asset Management & Inspections | 7.3.4.10 | Other discretionary inspection of transmission electric lines and | IN-1.2 | Equipment failure | Other contact with object | 2018 | Transmission Ground: 1,076 Transmission Aerial: 579 | N/A | N/A | Transmission Ground: 1,045 Transmission Aerial: 572 | Transmission Ground: 1,117 Transmission Aerial: 583 |  | Previously FRMMA; GSRPBA; Currently WMPMA |  |  |  |  | 52990 | 52990 | 58418.4023 | 58418.4023 |  |  | 89581 | 35934.3099 | 35934.3099 | 51820.2961 | 51820.2961 |  |  | 66942 | 13380.4806 | 13380.4806 | 24801.6854 | 24801.6854 |  |  | 41614 | 21962.6197 | 21962.6197 | 22559.69 | 22559.69 |  |  | 38000 | 11952.8662 | 11952.8662 | 21044.8234 | 21044.8234 |  |  | 37994.6685
Asset inspection | Asset Management & Inspections | 7.3.4.11 | Patrol inspections of distribution electric lines and equipment |  |  |  | NA | N/A | N/A | N/A | N/A | N/A | [8 empty] | 23849 | [6 empty] | 25218 | [6 empty] | 27315
Asset inspection | Asset Management & Inspections | 7.3.4.12 | Patrol inspections of transmission electric lines and equipment |  |  |  |  | N/A | N/A | N/A | N/A | N/A | [8 empty] | 2733 | [6 empty] | 3567 | [6 empty] | 4561
Asset inspection | Asset Management & Inspections | 7.3.4.13 | Pole loading assessment program to determine safety factor |  |  |  | NA | N/A | N/A | N/A | N/A | N/A |  | PLP Balancing Account | [6 empty] | 21259.9617 |  |  |  | 189565 |  |  | 15132.5628 |  |  |  | 125714 |  |  | 3741.5518 |  |  |  | 20066 |  |  | 496.5345 |  |  |  | 2000
Asset inspection | Asset Management & Inspections | 7.3.4.14 | Quality assurance / quality control of inspections |  |  |  |  | N/A | N/A | N/A | N/A | N/A | [5 empty] | Costs for this initiative are included as part of 7.3.4.9.1 and 7.3.4.10
Asset inspection | Asset Management & Inspections | 7.3.4.15 | Substation inspections |  |  |  | NA | N/A | N/A | N/A | N/A | N/A |  | NA | [6 empty] | 5452 | [6 empty] | 5704 | [6 empty] | 4209
Vegetation management project | Vegetation Management & Inspections | 7.3.5.1 | Additional efforts to manage community and environmental impacts |  |  |  |  | N/A | N/A | N/A | N/A | N/A | [13 empty] | 0 | 0 | 0 | 0 | [5 empty] | 20598.7345 | 20598.7345 | [5 empty] | 16709.557 | 16709.557 | [5 empty] | 16641.4651 | 16641.4651
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.2 | Detailed inspections and management practices for vegetation clearances around distribution electrical lines and equipment. |  |  |  | NA | N/A | N/A | N/A | N/A | N/A |  | Previously Na, Currently VMBA | [6 empty] | 58597.893 | [6 empty] | 25755.7217 | 16432.1505 |  |  | 470k (Trees in HFTD) |  |  | 24943.457 | 15913.9256 |  |  | 600k (Trees in HFTD) |  |  | 23241.523 | 14828.0917 |  |  | 600k (Trees in HFTD) |  |  | 23740.1568 | 15146.22 |  |  | 600k (Trees in HFTD)
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.3 | Detailed inspections and management practices for vegetation clearances around transmission electrical lines and equipment |  |  |  | NA | N/A | N/A | N/A | N/A | N/A |  | Previously Na, Currently VMBA | [6 empty] | 34355.169 | [6 empty] | 1773.7554 | 1131.6559 |  |  | 180k (Trees in HFTD) |  |  | 1100 | 701.8 |  |  | 190k (Trees in HFTD) |  |  | 4675.155 | 2982.7489 |  |  | 100k (Trees in HFTD) |  |  | 4594.117 | 2931.0466 |  |  | 100k (Trees in HFTD)
Vegetation management project | Vegetation Management & Inspections | 7.3.5.4 | Emergency response vegetation management due to red flag warning or other urgent weather conditions |  |  |  |  | N/A | N/A | N/A | N/A | N/A | [5 empty] | This activity is not individually tracked. Associated costs and units are captured in VM-2
Vegetation management project | Vegetation Management & Inspections | 7.3.5.5.1 | Fuel management (including all wood management) and management of “slash” from vegetation management activities | VM-2 | Contact with vegetation | Equipment failure | 2019 | 6166.3314 | N/A | N/A | 6232.686 | 6127.2228 |  | Previously WMPMA, Currently VMBA |  |  |  | Cost forecasts also include some transmission poles |  |  | 1654.651 | 1654.651 |  |  | 160000 | 0 | 0 | 7459.0831 | 7459.0831 |  |  | 230000 |  |  | 11026.1923 | 11026.1923 |  |  | 163100 |  |  | 20589 | 20589 |  |  | 170k Exempt Distribution Poles, 55k Non-Exempt Distribution Poles |  |  | 21240 | 21240 |  |  | 170k Exempt Distribution Poles, 55k Non-Exempt Distribution Poles
Vegetation management project | Vegetation Management & Inspections | 7.3.5.5.2 | Fuel management (including all wood management) and management of “slash” from vegetation management activities | VM-3 | Contact with vegetation |  | 2019 | 0.023026 | N/A | N/A | 0.0056821 | 0.031321 |  | Previously FHPMA, Currently VMBA | [11 empty] | 0 | 0 | 0 | 0 |  |  | 61 |  |  | 349.1998 | 349.1998 |  |  | 62 |  |  | 1185 | 1185 |  |  | 32 |  |  | 280.3676 | 280.3676
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.6 | Improvement of inspections |  |  |  |  | N/A | N/A | N/A | N/A | N/A
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.7 | Remote sensing inspections of vegetation around distribution electric lines and equipment. |  |  |  |  | N/A | N/A | N/A | N/A | N/A | [22 empty] | 1180.9259 | 1180.9259 |  |  | 90 Circuit Miles |  |  | 3182 | 3182 |  |  | 500 Circuit Miles |  |  | 3224.1885 | 3224.1885 |  |  | 500 Circuit Miles
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.8 | Remote sensing inspections of vegetation around transmission electric lines and equipment |  |  |  | 2019 | N/A | N/A | N/A | N/A | N/A |  | Previously WMPMA, Currently VMBA | [6 empty] | 4532.306 | 4532.306 |  |  | 1570 Circuit Miles | 0 | 0 | 4092.2315 | 4092.2315 |  | 1227 | 1700 Circuit Miles |  |  | 3180.2748 | 3180.2748 |  |  | 1590 Circuit Miles |  |  | 2048.254 | 2048.254 |  |  | 1600 Circuit Miles |  |  | 1902.8011 | 1902.8011 |  |  | 1600 Circuit Miles
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.9 | Other discretionary inspections of vegetation around distribution electric lines and equipment |  |  |  |  | N/A | N/A | N/A | N/A | N/A
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.10 | Other discretionary inspections of vegetation around transmission electric lines and equipment |  |  |  |  | N/A | N/A | N/A | N/A | N/A
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.11 | Patrol inspections of vegetation around distribution electric lines and equipment |  |  |  |  | N/A | N/A | N/A | N/A | N/A |  | Previously Na, Currently VMBA | [27 empty] | 18283.2 | 18283.2 | [5 empty] | 18831.7 | 18831.7
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.12 | Patrol inspections of vegetation around transmission electric lines and equipment |  |  |  |  | N/A | N/A | N/A | N/A | N/A |  | Previously Na, Currently VMBA | [27 empty] | 962.27 | 962.27 | [5 empty] | 991.14 | 991.14
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.13 | Quality assurance / quality control of vegetation management |  |  |  | 2019 | [6 empty] | Previously WMPMA, Currently VMBA | [6 empty] | 989.08 | 989.08 |  |  |  | 0 | 0 | 3966.0336 | 3966.0336 |  | 14000 |  |  |  | 3221.2003 | 3221.2003 | [5 empty] | 6158.977 | 6158.977 |  |  | 8000 Circuit Miles |  |  | 6571.2834 | 6571.2834 |  |  | 8000 Circuit Miles
Vegetation management project | Vegetation Management & Inspections | 7.3.5.14 | Recruiting and training of vegetation management personnel |  |  |  |  | N/A | N/A | N/A | N/A | N/A | [5 empty] | Recruiting costs for Vegetation Management activities are captured in general labor.
Vegetation management project | Vegetation Management & Inspections | 7.3.5.15 | Identification and remediation of “at-risk species” |  |  |  |  | N/A | N/A | N/A | N/A | N/A
Vegetation management project | Vegetation Management & Inspections | 7.3.5.16.1 | Removal and remediation of trees with strike potential to electric lines and equipment | VM-1 | Contact with vegetation |  | 2018 | 2818.4725 | N/A | N/A | 2944.4437 | 2568.3354 |  | Previously GSRPBA, Currently VMBA | [6 empty] | 15271.118 | 15271.118 |  |  | 130,000 trees assessed | 0 | 0 | 46684.7626 | 46684.7626 |  |  | 100,000 trees assessed |  |  | 32431.8218 | 32431.8218 |  |  | 131,400 trees assessed |  |  | 42636.0585 | 42636.0585 |  |  | 330 circuits assessed |  |  | 45358.9017 | 45358.9017 |  |  | 200 circuits assessed
Vegetation management project | Vegetation Management & Inspections | 7.3.5.16.2 | Removal and remediation of trees with strike potential to electric lines and equipment | VM-4 | Contact with vegetation |  | NA | 8915.2333 | N/A | N/A | 9307.0233 | 8805.5321 | [8 empty] | 31157.755 | 30413.385 |  |  | 13,500 removals identified | 0 | 0 | 37604 | 37604 |  |  | 9,000 removals identified |  |  | 16165.0627 | 16165.0627 |  |  | 1,301 circuits assessed |  |  | 31257.625 | 31257.625 |  |  | 900 circuits assessed |  |  | 36212.075 | 36212.075 |  |  | 900 circuits assessed
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.17 | Substation inspection |  |  |  |  | N/A | N/A | N/A | N/A | N/A
Vegetation management project | Vegetation Management & Inspections | 7.3.5.18 | Substation vegetation management |  |  |  |  | N/A | N/A | N/A | N/A | N/A | [5 empty] | Associated costs are captured in 7.3.5.2 | [27 empty] | 169 Substations Inspected
Vegetation management project | Vegetation Management & Inspections | 7.3.5.19 | Vegetation management enterprise system | VM-6 |  |  | 2021 | Enabling | Enabling | Enabling | Enabling | Enabling |  | Previously WMPMA; GSRPBA, Currently VMBA |  |  |  |  | 4219 | 4219 | [5 empty] | 16127.8644 | 16127.8644 | 1055.6305 | 1055.6305 |  |  |  | 11005.183 | 11005.183 | 634.5483 | 634.5483 |  |  |  | 6800 | 6800 | 3500 | 3500 |  |  |  | 2300 | 2300 | 3800 | 3800
Vegetation management project | Vegetation Management & Inspections | 7.3.5.20 | Vegetation management to achieve clearances around electric lines and equipment |  | Contact with vegetation |  | NA | 269.7944 | N/A | N/A | 280.9216 | 262.7166 |  | Previously FHPMA, Currently VMBA | [6 empty] | 169222.954 | 167414.3362 | [5 empty] | 326799.0489 | 216020.7285 | [5 empty] | 359961.8426 | 229769.8426 | [5 empty] | 379262.2695 | 238421.2695 | [5 empty] | 347246.4857 | 217453.4857
Vegetation management project | Vegetation Management & Inspections | 7.3.5.21 | Vegetation management activities post-fire |  |  |  |  | N/A | N/A | N/A | N/A | N/A
Other | Grid Operations & Operating Protocols | 7.3.6.1 | Automatic recloser operations |  |  |  |  | N/A | N/A | N/A | N/A | N/A | [6 empty] | 1488 | [6 empty] | 957 | [6 empty] | 2239
Other | Grid Operations & Operating Protocols | 7.3.6.2 | Protective equipment and device settings. |  |  |  |  | N/A | N/A | N/A | N/A | N/A |  | NA
Other | Grid Operations & Operating Protocols | 7.3.6.3 | Crew-accompanying ignition prevention and suppression resources and services |  |  |  |  | N/A | N/A | N/A | N/A | N/A
Other | Grid Operations & Operating Protocols | 7.3.6.4 | Personnel work procedures and training in conditions of elevated fire risk |  |  |  |  | N/A | N/A | N/A | N/A | N/A
Other | Grid Operations & Operating Protocols | 7.3.6.5 | Protocols for PSPS re-energization |  |  |  |  | N/A | N/A | N/A | N/A | N/A | [8 empty] | 1375.062 | 1375.062 |  |  |  | 0 | 0 | 111.1972 | 111.1972 | [5 empty] | 393.8326 | 393.8326 | [5 empty] | 708.984 | 708.984 | [5 empty] | 737.9008 | 737.9008
Other | Grid Operations & Operating Protocols | 7.3.6.6 | PSPS events and mitigation of PSPS impacts | PSPS-2 | PSPS - for sectionalization, etc. |  | 2018 | 211 Partnership: 35 Rebates: 4 CCBB: 2 CRC/CCV: 1 | 211 Partnership: 31 Rebates: 4 CCBB: 3 CRC/CCV: 1 | N/A | 211 Partnership: 35 Rebates: 5 CCBB: 2 CRC/CCV: 1 | 211 Partnership: 38 Rebates: 3 CCBB: 2 CRC/CCV: 1 |  | Previously GSRPBA; FRMMA; WMPMA, Currently FRMMA; WMPMA |  |  |  |  | 585 | 585 | 1905.71 | 1905.71 |  |  | 13 CRCs | 6843.2439 | 6843.2439 | 11092.3173 | 11092.3173 |  | 14000 | 56 CRCs, 720 CCBB Batteries, 1041 Rebates | 3284.8591 | 3284.8591 | 25537.0603 | 25537.0603 |  |  | 64 CRCs, 6021 CCBB Batteries, 2427 Rebates | 7560 | 7560 | 28130.8715 | 28130.8715 |  |  | 2,750 CCBB Customers, 4,000 Battery Rebates |  |  | 22894.2379 | 22894.2379 |  |  | 2,750 CCBB Customers, 4,000 Battery Rebates
Other | Grid Operations & Operating Protocols | 7.3.6.6.1 | PSPS Incident Management Team | [10 empty] | NA | [6 empty] | 5774.3076 | 5774.3076 |  |  |  | 0 | 0 | 8934.7569 | 8934.7569 |  |  |  | 11217.1415 | 11217.1415 | 14811.9333 | 14811.9333 |  |  |  | 12650 | 12650 | 14952.5984 | 14952.5984 |  |  |  | 4550 | 4550 | 15986.77 | 15986.77
Other | Grid Operations & Operating Protocols | 7.3.6.6.2.1.2 | Customer Resiliency Programs | [10 empty] | NA | [6 empty] | 0 | 0 | [12 empty] | 37.4229 | 37.4229
Other | Grid Operations & Operating Protocols | 7.3.6.6.2.1.3 | Customer Resiliency Equipment | [10 empty] | NA | [6 empty] | 11.2441 | 11.2441 |  |  |  | 0 | 0 | 4.0456 | 4.0456 | [5 empty] | 4138.2079 | 4138.2079 | [5 empty] | 2595.461 | 2595.461 | [5 empty] | 1999.707 | 1999.707
Other | Grid Operations & Operating Protocols | 7.3.6.7 | Stationed and on-call ignition prevention and suppression resources and services |  |  |  |  | N/A | N/A | N/A | N/A | N/A
Other | Data Governance | 7.3.7.1 | Centralized repository for data | DG-1 |  |  | 2021 | Enabling | Enabling | Enabling | Enabling | Enabling |  | Previously GSRPBA, Currently WMPMA |  |  |  |  | 1181 | 1181 | 0 | 0 |  |  |  | 1796.1108 | 1796.1108 | 0 | 0 |  | 14000 |  | 24.319 | 24.319 | [5 empty] | 16487 | 16487 | 4132 | 4132 |  |  |  | 8115 | 8115 | 5660 | 5660
Other | Data Governance | 7.3.7.2 | Collaborative research on utility ignition and/or wildfire |  |  |  |  | N/A | N/A | N/A | N/A | N/A
Other | Data Governance | 7.3.7.3 | Documentation and disclosure of wildfire-related data and algorithms |  |  |  |  | N/A | N/A | N/A | N/A | N/A
Other | Data Governance | 7.3.7.4 | Tracking and analysis of near miss data |  |  |  |  | N/A | N/A | N/A | N/A | N/A
Other | Resource Allocation Methodology | 7.3.8.1 | Allocation methodology development and application |  |  |  |  | N/A | N/A | N/A | N/A | N/A |  | Previously FRMMA; WMPMA, Currently WMPMA | [6 empty] | 42643.8299 | 42643.8299 |  |  |  | 0 | 0 | 32860.3867 | 32860.3867 |  | 14000 |  |  |  | 13245.9608 | 13245.9608 | [5 empty] | 10371.72 | 10371.72 | [5 empty] | 10644.1792 | 10644.1792
Other | Resource Allocation Methodology | 7.3.8.2 | Risk reduction scenario development and analysis |  |  |  | 2018 | N/A | N/A | N/A | N/A | N/A
Other | Resource Allocation Methodology | 7.3.8.3 | Risk spend efficiency analysis |  |  |  |  | N/A | N/A | N/A | N/A | N/A
Other | Emergency Planning & Preparedness | 7.3.9.1 | Adequate and trained workforce for service restoration | DEP-2 | PSPS - for sectionalization, etc. |  | 2018 | UAS: 2,119 IMT/ Field Training: 262 | UAS: 2,322 IMT/ Field Training: 236 | N/A | UAS: 3,225 IMT/ Field Training: 263 | UAS: 1,872 IMT/ Field Training: 285 |  | WMPMA | [6 empty] | 1444.9391 | 1444.9391 |  |  |  | 0 | 0 | 615.6675 | 615.6675 |  |  | 44 UAS Operators Trained |  |  | 376.5885 | 376.5885 |  |  | 60 UAS Operators Trained |  |  | 1776.801 | 1776.801 |  |  | 50 UAS Operators Trained |  |  | 1862.7654 | 1862.7654 |  |  | 50 UAS Operators Trained
Other | Emergency Planning & Preparedness | 7.3.9.2 | Community outreach, public awareness, and communications efforts |  |  |  |  | N/A | N/A | N/A | N/A | N/A | [5 empty] | Costs included in 7.3.10.1.2
Other | Emergency Planning & Preparedness | 7.3.9.3 | Customer support in emergencies |  |  |  |  | N/A | N/A | N/A | N/A | N/A | [5 empty] | Costs included in 7.3.10.1.2
Other | Emergency Planning & Preparedness | 7.3.9.4 | Disaster and emergency preparedness plan |  |  |  |  | N/A | N/A | N/A | N/A | N/A | [5 empty] | Costs included in 7.3.6.6.1
Other | Emergency Planning & Preparedness | 7.3.9.5 | Preparedness and planning for service restoration |  |  |  | 2018 | N/A | N/A | N/A | N/A | N/A |  | Previously GSRPBA, Currently WMPMA | [6 empty] | 9414.0643 | 9414.0643 |  |  |  | 0 | 0 | 5327.909 | 5327.909 |  | 14000 |  |  |  | 3529.6374 | 3529.6374 | [5 empty] | 7336.548 | 7336.548 | [5 empty] | 7386.3799 | 7386.3799
Other | Emergency Planning & Preparedness | 7.3.9.6 | Protocols in place to learn from wildfire events |  |  |  |  | N/A | N/A | N/A | N/A | N/A
Other | Stakeholder Cooperation & Community Engagement | 7.3.10.1.1 | Community engagement | DEP-1.2 |  |  | 2018 | Enabling | Enabling | Enabling | Enabling | Enabling |  | Previously GSRPBA, Currently WMPMA | [6 empty] | 754.5978 | 754.5978 |  |  | 13 | 0 | 0 | 141.9413 | 141.9413 |  |  | 9 |  |  | 10.7665 | 10.7665 |  |  | 11 |  |  | 109.9585 | 109.9585 |  |  | 9 |  |  | 111.9378 | 111.9378 |  |  | 9
Other | Stakeholder Cooperation & Community Engagement | 7.3.10.1.2 | Community engagement | DEP-1.3 |  |  | 2018 | Enabling | Enabling | Enabling | Enabling | Enabling |  | Previously FRMMA; GSRPBA, Currently WMPMA | [6 empty] | 4515.6467 | 4515.6467 |  |  |  | 0 | 0 | 5489.5082 | 5489.5082 |  | 14000 |  |  |  | 9194.8015 | 9194.8015 | [5 empty] | 11443.008 | 11443.008 | [5 empty] | 11489.2529 | 11489.2529
Other | Stakeholder Cooperation & Community Engagement | 7.3.10.1.3 | Community engagement | DEP-4 |  |  | 2018 | N/A | N/A | N/A | N/A | N/A |  | Previously FRMMA, Currently WMPMA | [6 empty] | -650.8003 | -650.8003 |  |  |  | 0 | 0 | 0 | 0 |  |  | 5 |  |  | 856.0773 | 856.0773 |  |  | 9 |  |  | 6038.135 | 6038.135 |  |  | 6 |  |  | 6298.9579 | 6298.9579 |  |  | 6
Other | Stakeholder Cooperation & Community Engagement | 7.3.10.2 | Cooperation and best practice sharing with agencies outside CA |  |  |  |  | N/A | N/A | N/A | N/A | N/A
Other | Stakeholder Cooperation & Community Engagement | 7.3.10.3 | Cooperation with suppression agencies | DEP-5 |  |  | 2020 | 8478.0353 | N/A | N/A | 6557.2567 | 9845.9764 |  | WMPMA | [6 empty] | 0 | 0 |  |  |  | 0 | 0 | 2158 | 2158 |  |  | 1 MOU |  |  | 17545 | 17545 |  |  | 3 MOUs |  |  | 18000 | 18000 |  |  | 3 MOUs |  |  | 17707.43 | 17707.43 |  |  | 3 MOUs
Other | Stakeholder Cooperation & Community Engagement | 7.3.10.4 | Forest service and fuel reduction cooperation and joint roadmap |  |  |  |  | N/A | N/A | N/A | N/A | N/A
Other | Alternative Technologies | 7.1.E | Alternative Technology Pilot Programs |  | Wire-to-wire contact | Equipment failure | 2018 | 9169.466 | N/A | N/A | 7058.7556 | 10321.2707 |  | Previously GSRPBA; Currently WMPMA |  |  |  | Drivers and RSEs reflective of Early Fault Detection only |  |  | 1.0507 | 1.0507 |  |  |  | 0 | 0 | 158.9205 | 158.9205 |  | 14000 |  | 2014.7525 | 2014.7525 | 2.4257 | 2.4257 |  |  |  | 6984.997 | 6984.997
[21 empty] | 119990 | 76281.4516