## Quarterly Submission Guide
| Yes | No | <-- for dropdowns
Wildfire Safety Division Attachment 2.3
Wildifire Mitigation Plan Quarterly report - non-spatial data template
Resolution WSD-011 Attachment 2.3
Instructions for use
1 | Fill out the tan cells (color represented here) starting with the cell below (D17: Utility). The Utility name will populate the Table tabs to follow. Date modified will vary by table.
2 | Cells will only accept valid entries. For most cells, this is positive numbers
3 | For each Table tab, after a modification is made, denote the date of the change in cell C4 for each Table tab.
4 | Some columns have an additional header in row 5 to serve as clarification for several columns. With the exception of projected data, row 5 will be highlighted in blue (color represented here)
5 | Some required metrics are future projections. For these, row 5, above the projections will be highlighted light green (color represented here)
In future submissions, report updated projected numbers if / when projections have changed, and report actuals once the quarter / year has passed.
6 | For data required annually rather than quarterly (see Tables 7.3 - 10), report for entire year even if part of the year is projected. Once year has passed, update cell with actuals
7 | Some tables will have additional instructions provided in a Notes box located in cells D2 - D4
Notes will explain terms, signal where projections are required, and provide other useful information.
8 | For the initial quarterly submission, utilities are required to submit data on annual metrics for 2015 - 2020, which should represent the most updated data from the 2020 WMP for years 2015-2019
* | Do not add or manipulate the template for any of the tabs
Update the below table to establish which year, quarter of the WMP cycle this submission this represents.
Utility |  | Southern California Edison Company
First year of 3-year WMP cycle |  | 2020
Submission year |  | 2021
Submission quarter |  | Q1
Date Modified |  | 2021-05-03

## Table 1
Utility | Southern California Edison Company | Notes:
Table No. | 1 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.
Date Modified | 2021-05-03
Note: These columns are placeholders for future QR submissions.
Table 1: Recent performance on progress metrics | [7 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Progress metric name | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
1. Grid condition findings from inspection - Distribution lines in HFTD | 1.a. | Number of circuit miles inspected from patrol inspections in HFTD - Distribution lines | 9729.4195 | 9733.9282 | 9737.8945 | 9750.7764 | 9813.8301 | 1: 1587.2237; 2: 6954.0747; 3: 1249.9205; 4: 233.1291; 1: 3783.3223 | # circuit miles | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected.
| 1.b. | Number of circuit miles inspected from detailed inspections in HFTD - Distribution lines (Total) | 1986.0213 | 2425.4308 | 2048.6343 | 2549.7076 | 15215.0893 | 1: 3099.7897; 2: 4768.8521; 3: 4748.9489; 4: 3831.949; 1: 3852.0711 | # circuit miles | This row is the sum of the four detailed inspection programs below it
|  | Overhead Detailed Inspections | 1986.0213 | 2425.4308 | 2048.6343 | 1617.9709 | 1905.8482 | 1: 518.43; 2: 1351.7556; 3: 47.7649; 4: 3.5595; 1: 652.7072 |  | From 2015-2019, the number represents the completed detailed inspections completed in circuit miles. Starting in 2020, the numbers represent completed compliance-due detailed inspections by circuit miles. SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected.
|  | Enhanced Overhead Inspections | NA | NA | NA | 931.7367 | 9448.0509 | [13 empty] | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. | bar: 1 to 1
|  | High Fire Risk Informed Inspections | NA | NA | NA | NA | NA | 1: 154.1097; 2: 989.8465; 3: 2273.9341; 4: 1401.1395; 1: 2984.0322 |  | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected.
|  | Aerial Inspections | NA | NA | NA | NA | 3861.1902 | 1: 2427.25; 2: 2427.25; 3: 2427.25; 4: 2427.25; 1: 215.3317 |  | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. Additionally, for 2020, SCE tracked the completed asset inspected by the year and in order to represent the 2020 completed asset inspection in circuit mile by quarter, SCE evenly distributed the completed inspections to each of the four quarters in 2020.
| 1.c. | Number of circuit miles inspected from other inspections (list types of "other" inspections in comments) in HFTD - Distribution lines (total) | NA | NA | NA | 12604.6982 | 5662.5399 | 1: 1382.4783; 2: 1382.4783; 3: 1382.4783; 4: 1382.4783; 1: 2547.919 | # circuit miles | This row is the sum of the two programs below that are considered as "other"
|  | Infrared Scan | NA | NA | NA | 11775 | 4962 | 1: 1111.5; 2: 1111.5; 3: 1111.5; 4: 1111.5; 1: 2465 |  | For 2020, SCE tracks the completed asset inspected by year and in order to represent the 2020 completed asset inspection by quarter, SCE evenly distributed the completed inspections to each of the four quarters in 2020.
|  | Intrusive Pole Inspections | NA | NA | NA | 829.6982 | 700.5399 | 1: 270.9783; 2: 270.9783; 3: 270.9783; 4: 270.9783; 1: 82.919 |  | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. Additionally, for 2020, SCE tracked the completed asset inspected by year and in order to represent the 2020 completed asset inspection by quarter, SCE evenly distributed the completed inspections to each of the four quarters in 2020.
| 1.d. | Level 1 findings in HFTD for patrol inspections - Distribution lines | 0 | 0 | 3 | 1 | 17 | 1: 0; 2: 18; 3: 0; 4: 1; 1: 5 | # findings | Historical data was updated as an error was found in the logic that summed up the numbers for each type of inspection method
| 1.e. | Level 1 findings in HFTD for detailed inspections - Distribution lines | 2163 | 3146 | 3114 | 2834 | 4144 | 1: 797; 2: 716; 3: 706; 4: 739; 1: 778 | # findings | Historical data was updated as an error was found in the logic that summed up the numbers for each type of inspection method
| 1.f. | Level 1 findings in HFTD for other inspections (list types of "other" inspections in comments) - Distribution lines | 246 | 773 | 325 | 167 | 617 | 1: 91; 2: 115; 3: 306; 4: 261; 1: 90 | # findings | Historical data was updated as an error was found in the logic that summed up the numbers for each type of inspection method
| 1.g. | Level 2 findings in HFTD for patrol inspections - Distribution lines | 6392 | 5124 | 3781 | 3730 | 6498 | 1: 1028; 2: 1513; 3: 1227; 4: 1054; 1: 1509 | # findings | Historical data was updated as an error was found in the logic that summed up the numbers for each type of inspection method
| 1.h. | Level 2 findings in HFTD for detailed inspections - Distribution lines | 7297 | 7751 | 5841 | 16646 | 71791 | 1: 9890; 2: 9045; 3: 5647; 4: 3807; 1: 9174 | # findings | Historical data was updated as an error was found in the logic that summed up the numbers for each type of inspection method
| 1.i. | Level 2 findings in HFTD for other inspections (list types of "other" inspections in comments) - Distribution lines | 4448 | 4167 | 3934 | 3348 | 5304 | 1: 1463; 2: 1737; 3: 534; 4: 1924; 1: 1166 | # findings | Historical data was updated as an error was found in the logic that summed up the numbers for each type of inspection method
| 1.j. | Level 3 findings in HFTD for patrol inspections - Distribution lines | 43 | 10 | 33 | 51 | 228 | 1: 117; 2: 6; 3: 0; 4: 2; 1: 26 | # findings | Historical data was updated as an error was found in the logic that summed up the numbers for each type of inspection method
| 1.k. | Level 3 findings in HFTD for detailed inspections - Distribution lines | 14301 | 18081 | 12647 | 13725 | 108873 | 1: 8982; 2: 9381; 3: 9536; 4: 824; 1: 13987 | # findings | Historical data was updated as an error was found in the logic that summed up the numbers for each type of inspection method
| 1.l. | Level 3 findings in HFTD for other inspections (list types of "other" inspections in comments) - Distribution lines | 256 | 142 | 206 | 214 | 1563 | 1: 1267; 2: 1136; 3: 138; 4: 298; 1: 471 | # findings | Historical data was updated as an error was found in the logic that summed up the numbers for each type of inspection method
1. Grid condition findings from inspection - Distribution lines total | 1.a.ii. | Number of total circuit miles inspected from patrol inspections - Distribution lines | 39125.4729 | 39138.8683 | 39128.8517 | 39192.8387 | 39463.8565 | 1: 1011.3532; 2: 23406.411; 3: 10640.7673; 4: 2691.4004; 1: 5336.2758 | # circuit miles | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected.
| 1.b.ii. | Number of total circuit miles inspected from detailed inspections - Distribution lines (Total) | 8346.744 | 8199.9627 | 8006.8655 | 8813.1697 | 21245.4518 | 1: 3377.8482; 2: 5605.1526; 3: 6441.5106; 4: 6935.0176; 1: 3891.0255 | # circuit miles | This row is the sum of the four detailed inspection programs below it
|  | Overhead Detailed Inspections | 8346.744 | 8199.9627 | 8006.8655 | 7881.433 | 7936.2107 | 1: 796.4885; 2: 2188.0561; 3: 1740.3265; 4: 3106.6282; 1: 839.4555 |  | From 2015-2019, the number represents the completed detailed inspections completed in circuit miles. Starting in 2020, the numbers represent completed compliance-due detailed inspections by circuit miles. SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected.
|  | Enhanced Overhead Inspections | NA | NA | NA | 931.7367 | 9448.0509 | [13 empty] | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. | bar: 1 to 1
|  | High fire Risk Informed Inspections | NA | NA | NA | NA | NA | 1: 154.1097; 2: 989.8465; 3: 2273.9341; 4: 1401.1395; 1: 3188 |  | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected.
|  | Aerial Inspections | NA | NA | NA | NA | 3861.1902 | 1: 2427.25; 2: 2427.25; 3: 2427.25; 4: 2427.25; 1: 215.3317 |  | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. Additionally, for 2020, SCE tracked the completed asset inspected by the year and in order to represent the 2020 completed asset inspection in circuit mile by quarter, SCE evenly distributed the completed inspections to each of the four quarters in 2020.
| 1.c.ii. | Number of total circuit miles inspected from other inspections (list types of "other" inspections in comments) - Distribution lines | 4320.0487 | 4509.1094 | 4092.7155 | 29901.545 | 8886.6749 | 1: 2106.4005; 2: 2106.4005; 3: 2106.4005; 4: 2106.4005; 1: 3457.7552 | # circuit miles | This row is the sum of the two programs below that are considered as "other"
|  | Infrared Scan | NA | NA | NA | 26055 | 4962 | 1: 1111.5; 2: 1111.5; 3: 1111.5; 4: 1111.5; 1: 2465 |  | For 2020, SCE tracks the completed asset inspected by the year and in order to represent the 2020 completed asset inspection by quarter, SCE just evenly distributed the completed inspections to each of the four quarters in 2020.
|  | Intrusive Pole Inspections | 4320.0487 | 4509.1094 | 4092.7155 | 3846.545 | 3924.6749 | 1: 994.9005; 2: 994.9005; 3: 994.9005; 4: 994.9005; 1: 992.7552 |  | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. Additionally, for 2020, SCE tracked the completed asset inspected by the year and in order to represent the 2020 completed asset inspection by quarter, SCE just evenly distributed the completed inspections to each of the four quarters in 2020.
| 1.d.ii. | Level 1 findings for patrol inspections - Distribution lines | 5 | 2 | 4 | 10 | 28 | 1: 0; 2: 76; 3: 3; 4: 19; 1: 19 | # findings
| 1.e.ii. | Level 1 findings for detailed inspections - Distribution lines | 17812 | 19726 | 21832 | 19482 | 21320 | 1: 4300; 2: 4923; 3: 6308; 4: 5039; 1: 4918 | # findings
| 1.f.ii. | Level 1 findings for other inspections (list types of "other" inspections in comments) - Distribution lines | 1742 | 2636 | 1762 | 1506 | 2680 | 1: 557; 2: 596; 3: 682; 4: 576; 1: 370 | # findings
| 1.g.ii. | Level 2 findings for patrol inspections - Distribution lines | 26406 | 17649 | 15545 | 30305 | 83237 | 1: 8457; 2: 4779; 3: 4808; 4: 3665; 1: 4551 | # findings
| 1.h.ii. | Level 2 findings for detailed inspections - Distribution lines | 51016 | 48323 | 41641 | 39640 | 40771 | 1: 8510; 2: 13463; 3: 13300; 4: 15593; 1: 13769 | # findings
| 1.i.ii. | Level 2 findings for other inspections (list types of "other" inspections in comments) - Distribution lines | 14687 | 13466 | 12071 | 12873 | 26158 | 1: 6250; 2: 6497; 3: 4403; 4: 6114; 1: 3411 | # findings
| 1.j.ii. | Level 3 findings for patrol inspections - Distribution lines | 328 | 64 | 128 | 7790 | 35237 | 1: 142; 2: 12; 3: 4; 4: 17; 1: 26 | # findings
| 1.k.ii. | Level 3 findings for detailed inspections - Distribution lines | 84111 | 76240 | 63267 | 62133 | 62271 | 1: 11811; 2: 16961; 3: 18740; 4: 19548; 1: 17760 | # findings
| 1.l.ii. | Level 3 findings for other inspections (list types of "other" inspections in comments) - Distribution lines | 1149 | 753 | 1013 | 2851 | 92092 | 1: 2428; 2: 2514; 3: 1240; 4: 1510; 1: 664 | # findings
1. Grid condition findings from inspection - Transmission lines in HFTD | 1.a.iii. | Number of circuit miles inspected from patrol inspections in HFTD - Transmission lines | 4437.829 | 4437.829 | 4437.829 | 4437.829 | 4437.829 | 1: 1109.4572; 2: 1109.4572; 3: 1109.4572; 4: 1109.4572; 1: 433.7562 | # circuit miles | For 2015-2017, patrol inspections doubled as detailed inspections being completed on every transmission asset in the service territory. Beginning in 2018, the recorded inspection numbers estimate the patrol type inspections in circuit miles being completed. Additionally, SCE tracks completed inspections by "Grids". SCE's complete transmission line network is broken out into large areas called "Grids" and all execution and tracking are recorded at the grid level. The number being represented uses the current transmission circuit mile counts in HFTD for each year. 2020 in particular, evenly distributes the current transmission mile circuit counts into each quarter.
| 1.b.iii. | Number of circuit miles inspected from detailed inspections in HFTD - Transmission lines | NA | NA | NA | 1479.2763 | 6628.9815 | 1: 2327.2769; 2: 2327.2769; 3: 2327.2769; 4: 2327.2769; 1: 1824 | # circuit miles | This row is the sum of the three detailed inspection programs below it. An updated historical number for detailed inspections occurred requiring a new summation of the programs below.
|  | Detailed Inspections | NA | NA | NA | 1479.2763 | 1479.2763 | 1: 369.8191; 2: 369.8191; 3: 369.8191; 4: 369.8191; 1: 311.41 |  | For 2015-2017, patrol inspections doubled as detailed inspections being completed on every transmission asset in the service territory. Beginning in 2018 the recorded inspection numbers estimate the detail inspections in circuit miles being completed. Additionally, the detailed inspection program completes inspections of 1/3 of all SCE transmission assets per year. The completed inspections are tracked by "Grids". SCE's complete transmission line network is broken out into large areas called "Grids" and all execution and tracking are recorded at the grid level. The number being represented uses 1/3rd of the current transmission circuit mile counts in HFTD for each year. 2020 in particular, evenly distributes the 1/3rd of the current transmission mile circuit counts into each quarter. An error was found in the calculation methodology for the historical years, therefore the outlined methodology was properly applied and the historical numbers were updated.
|  | High Fire Inspections | NA | NA | NA | NA | 519.6602 | 1: 1089.4224; 2: 1089.4224; 3: 1089.4224; 4: 1089.4224; 1: 966.1856 |  | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected.
|  | Aerial Inspections | NA | NA | NA | NA | 4630.0451 | 1: 868.0355; 2: 868.0355; 3: 868.0355; 4: 868.0355; 1: 546 |  | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. Additionally, for 2020, SCE tracked the completed asset inspected by the year and in order to represent the 2020 completed asset inspection by quarter, just evenly distributed the completed inspections to each of the four quarters in 2020.
| 1.c.iii | Number of total circuit miles inspected from other inspections (list types of "other" inspections in comments) - Transmission lines | NA | NA | NA | 102.6371 | 5003.1049 | 1: 283.7137; 2: 283.7137; 3: 283.7137; 4: 283.7137; 1: 43.4117 |  | This row is the sum of the two programs below that are considered as "other"
|  | IR Corona | NA | NA | NA | NA | 4901 | 1: 251.25; 2: 251.25; 3: 251.25; 4: 251.25; 1: 0 |  | For 2020, SCE tracked the completed inspections by the year. In order to represent the 2020 completed inspection by quarter, SCE evenly distributed the completed inspections to each of the four quarters evenly in 2020.
|  | Intrusive Pole Inspections | NA | NA | NA | 102.6371 | 102.1049 | 1: 32.4637; 2: 32.4637; 3: 32.4637; 4: 32.4637; 1: 43.4117 |  | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. Additionally, for 2020, SCE tracked the completed asset inspected by the year and in order to represent the 2020 completed asset inspection by quarter, SCE just evenly distributed the completed inspections to each of the four quarters in 2020.
| 1.d.iii. | Level 1 findings in HFTD for patrol inspections - Transmission lines | 50 | 82 | 40 | 32 | 108 | 1: 12; 2: 23; 3: 54; 4: 63; 1: 11 | # findings
| 1.e.iii. | Level 1 findings in HFTD for detailed inspections - Transmission lines | 0 | 0 | 0 | 1 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; 1: 18 | # findings
| 1.f.iii. | Level 1 findings in HFTD for other inspections (list types of "other" inspections in comments) - Transmission lines | 0 | 0 | 0 | 0 | 0 | 1: 6; 2: 0; 3: 0; 4: 0; 1: 0 | # findings
| 1.g.iii. | Level 2 findings in HFTD for patrol inspections - Transmission lines | 697 | 855 | 977 | 1215 | 15029 | 1: 1245; 2: 2522; 3: 549; 4: 138; 1: 319 | # findings
| 1.h.iii. | Level 2 findings in HFTD for detailed inspections - Transmission lines | 3 | 1 | 2 | 1 | 14 | 1: 609; 2: 4400; 3: 1783; 4: 961; 1: 537 | # findings
| 1.i.iii. | Level 2 findings in HFTD for other inspections (list types of "other" inspections in comments) - Transmission lines | 278 | 128 | 408 | 419 | 456 | 1: 15; 2: 46; 3: 45; 4: 85; 1: 24 | # findings
| 1.j.iii. | Level 3 findings in HFTD for patrol inspections - Transmission lines | 935 | 735 | 719 | 382 | 2545 | 1: 130; 2: 437; 3: 166; 4: 48; 1: 166 | # findings
| 1.k.iii. | Level 3 findings in HFTD for detailed inspections - Transmission lines | 0 | 2 | 0 | 4 | 3 | 1: 44; 2: 309; 3: 366; 4: 186; 1: 207 | # findings
| 1.l.iii. | Level 3 findings in HFTD for other inspections (list types of "other" inspections in comments) - Distribution lines | 0 | 0 | 0 | 0 | 103 | 1: 3; 2: 1; 3: 0; 4: 3; 1: 0 | # findings
1. Grid condition findings from inspection - Transmission lines total | 1.a.iv. | Number of total circuit miles inspected from patrol inspections - Transmission lines | 13068.2957 | 13068.2957 | 13068.2957 | 13068.2957 | 13068.2957 | 1: 3267.0739; 2: 3267.0739; 3: 3267.0739; 4: 3267.0739; 1: 1712.7809 | # circuit miles | For 2015-2017, patrol inspections doubled as detailed inspections being completed on every transmission asset in the service territory. Beginning in 2018, the recorded inspection numbers estimate the patrol type inspections in circuit miles being completed. Additionally, SCE tracks completed inspections by "Grids". SCE's complete transmission line network is broken out into large areas called "Grids" and all execution and tracking are recorded at the grid level. The number being represented uses the current transmission circuit mile counts in HFTD for each year. 2020 in particular, evenly distributes the current transmission mile circuit counts into each quarter.
| 1.b.iv. | Number of total circuit miles inspected from detailed inspections - Transmission lines | NA | NA | NA | 4210.1468 | 6389.3901 | 1: 2697.3468; 2: 3189.092; 3: 3230.0707; 4: 2984.1981; 1: 3957.6742 | # circuit miles | This row is the sum of the three detailed inspection programs below it
|  | Detailed Inspections | NA | NA | NA | 4210.1468 | 4760.2727 | 1: 696.639; 2: 1188.3841; 3: 1229.3629; 4: 983.4903; 1: 823.0246 |  | For 2015-2017, patrol inspections doubled as detailed inspections being completed on every transmission asset in the service territory. Beginning in 2018 the recorded inspection numbers estimate the detail inspections in circuit miles being completed. Additionally, the detailed inspection program completes inspections of 1/3 of all SCE transmission assets per year. The completed inspections are tracked by "Grids". SCE's complete transmission line network is broken out into large areas called "Grids" and all execution and tracking are recorded at the grid level. The number being represented uses 1/3rd of the current transmission circuit mile counts in HFTD for each year. 2020 in particular, evenly distributes the 1/3rd of the current transmission mile circuit counts into each quarter.
|  | High Fire Inspections | NA | NA | NA | NA | 519.6602 | 1: 1089.4224; 2: 1089.4224; 3: 1089.4224; 4: 1089.4224; 1: 966.1856 |  | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected.
|  | Aerial Inspections | NA | NA | NA | NA | 1109.4572 | 1: 911.2855; 2: 911.2855; 3: 911.2855; 4: 911.2855; 1: 546 |  | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. Additionally, for 2020, SCE tracked the completed asset inspected by the year and in order to represent the 2020 completed asset inspection by quarter, just evenly distributed the completed inspections to each of the four quarters in 2020.
| 1.c.iv. | Number of total circuit miles inspected from other inspections (list types of "other" inspections in comments) - Transmission lines | 6460.1372 | 4592.4297 | 6226.3202 | 7309.138 | 5528.6405 | 1: 1594.0568; 2: 1594.0568; 3: 1594.0568; 4: 1594.0568; 1: 266.8565 | # circuit miles | This row is the sum of the two programs below that are considered as "other"
|  | IR Corona | 0 | 0 | 0 | 0 | 0 | 1: 43.25; 2: 43.25; 3: 43.25; 4: 43.25; 1: 0 |  | For 2020, SCE tracked the completed inspections by the year. In order to represent the 2020 completed inspection by quarter, SCE evenly distributed the completed inspections to each of the four quarters evenly in 2020.
|  | Intrusive Pole Inspections | 6460.1372 | 4592.4297 | 6226.3202 | 7309.138 | 5528.6405 | 1: 1594.0568; 2: 1594.0568; 3: 1594.0568; 4: 1594.0568; 1: 266.8565 |  | SCE tracks completed inspections by tracking the counts of assets inspected instead of tracking by circuit miles. In order to present completed inspections in the requested format, SCE used a calculated average span length multiplied by the number of structures inspected. Additionally, for 2020, SCE tracked the completed asset inspected by the year and in order to represent the 2020 completed asset inspection by quarter, SCE just evenly distributed the completed inspections to each of the four quarters in 2020.
| 1.d.iv. | Level 1 findings for patrol inspections - Transmission lines | 241 | 252 | 211 | 178 | 304 | 1: 51; 2: 51; 3: 106; 4: 108; 1: 48 | # findings
| 1.e.iv. | Level 1 findings for detailed inspections - Transmission lines | 0 | 1 | 0 | 1 | 0 | 1: 0; 2: 0; 3: 1; 4: 0; 1: 19 | # findings
| 1.f.iv. | Level 1 findings for other inspections (list types of "other" inspections in comments) - Transmission lines | 1 | 2 | 2 | 1 | 1 | 1: 7; 2: 0; 3: 1; 4: 0; 1: 0 | # findings
| 1.g.iv. | Level 2 findings for patrol inspections - Transmission lines | 3912 | 4600 | 5393 | 5871 | 22007 | 1: 2536; 2: 3644; 3: 1200; 4: 802; 1: 1486 | # findings
| 1.h.iv. | Level 2 findings for detailed inspections - Transmission lines | 10 | 8 | 7 | 4 | 37 | 1: 628; 2: 4494; 3: 1889; 4: 1072; 1: 553 | # findings
| 1.i.iv. | Level 2 findings for other inspections (list types of "other" inspections in comments) - Transmission lines | 1428 | 583 | 999 | 1150 | 1003 | 1: 101; 2: 140; 3: 245; 4: 375; 1: 131 | # findings
| 1.j.iv. | Level 3 findings for patrol inspections - Transmission lines | 7020 | 3350 | 3060 | 1732 | 5049 | 1: 744; 2: 904; 3: 475; 4: 383; 1: 371 | # findings
| 1.k.iv. | Level 3 findings for detailed inspections - Transmission lines | 4 | 2 | 1 | 10 | 3 | 1: 44; 2: 312; 3: 388; 4: 210; 1: 209 | # findings
| 1.l.iv. | Level 3 findings for other inspections (list types of "other" inspections in comments) - Transmission lines | 1 | 1 | 4 | 3 | 136 | 1: 3; 2: 2; 3: 0; 4: 3; 1: 0 | # findings
2. Vegetation clearance findings from inspection - total | 2.a.i | Number of spans inspected where at least some vegetation was found in non-compliant condition - total | NA | NA | NA | NA | 2430.3495 | 1: 121.5159; 2: 522.2705; 3: 1388.8559; 4: 849.1441; 1: 370.1468 | # of spans inspected with noncompliant clearance based on applicable rules and regulations at the time of inspection | Prior to July 2019, SCE's work management system did not track the reason why a tree was trimmed, just that trimming was required. In other words, a tree may have been trimmed because it was nearing the regulatory clearance distance (RCD) or because it was inside the RCD. Starting in July of 2019, SCE implemented a new work management system that required inspectors to document whether the tree was found inside the RCD, or other SCE program distances related to clearance which exceed RCD clearance. The historical numbers were updated as a calculation error was discovered.
| 2.a.ii | Number of spans inspected for vegetation compliance - total | NA | NA | NA | NA | 120314.3297 | 1: 34718.8397; 2: 53842.3244; 3: 64298.8821; 4: 67392.387; 1: 61691.1342 | # of spans inspected for vegetation compliance | SCE tracks completed vegetation compliance inspections by circuit miles. In order to present completed vegetation compliance inspections in the requested format, SCE divided the recorded circuit miles inspected by the calculated average span length. The historical numbers were updated as a calculation error was discovered.
2. Vegetation clearance findings from inspection - in HFTD | 2.b.i | Number of spans inspected where at least some vegetation was found in non-compliant condition in HFTD | NA | NA | NA | NA | 530 | 1: 32; 2: 135; 3: 306; 4: 242; 1: 103.7226 | # of spans inspected with noncompliant clearance based on applicable rules and regulations at the time of inspection | SCE tracks findings by count and does not record specific data that associate the findings to a specific span. Therefore SCE is unable to understand how many findings are on each span. The number being presented are just the counts of findings.
| 2.b.ii | Number of spans inspected for vegetation compliance in HFTD | NA | NA | NA | NA | 25479.0069 | 1: 8995.5634; 2: 13089.0502; 3: 12870.0571; 4: 18168.0059; 1: 15186.3304 | # of spans inspected for vegetation compliance | SCE tracks completed vegetation compliance inspections by circuit miles. In order to present completed vegetation compliance inspections in the requested format, SCE divided the recorded circuit miles inspected by the calculated average span length.
3. Customer outreach metrics | 3.a. | # Customers in an evacuation zone for utility-ignited wildfire | NA | NA | NA | NA | NA | [12 empty] | # customers (if customer was in an evacuation zone for multiple wildfires, count the customer for each relevant wildfire) | SCE has no jurisdiction over evacuation orders. SCE diligently requested and followed up with local governments and law enforcement, and was only able to obtain information from one county. Even then, the information provided included high-level estimations of evacuation counts estimated by the local government and law enforcement entity for a limited amount of fires. Because of this, SCE is unable to obtain the requested data, analyze it, and report on evacuation related requirements in this table. SCE anticipates this to be a recurring challenge going forward. | bar: 1 to 1
| 3.b. | # Customers notified of evacuation orders | NA | NA | NA | NA | NA | [12 empty] | # customers (count customer multiple times for each unique wildfire of which they were notified) | SCE has no jurisdiction over evacuation orders. SCE diligently requested and followed up with local governments and law enforcement, and was only able to obtain information from one county. Even then, the information provided included high-level estimations of evacuation counts estimated by the local government and law enforcement entity for a limited amount of fires. Because of this, SCE is unable to obtain the requested data, analyze it, and report on evacuation related requirements in this table. SCE anticipates this to be a recurring challenge going forward. | bar: 1 to 1
| 3.c. | % of customers notified of evacuation in evacuation zone of a utility-ignited wildfire | NA | NA | NA | NA | NA | [12 empty] | Percentage of customers notified of evacuation | SCE has no jurisdiction over evacuation orders. SCE diligently requested and followed up with local governments and law enforcement, and was only able to obtain information from one county. Even then, the information provided included high-level estimations of evacuation counts estimated by the local government and law enforcement entity for a limited amount of fires. Because of this, SCE is unable to obtain the requested data, analyze it, and report on evacuation related requirements in this table. SCE anticipates this to be a recurring challenge going forward. | bar: 1 to 1

## Table 2
Utility | Southern California Edison Company | Notes:
Table No. | 2 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.
Date Modified | 2021-05-03
Note: These columns are placeholders for future QR submissions.
Table 2: Recent performance on outcome metrics | [7 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Outcome metric name | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
1. Risk events | 1.a. | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | 12337 | 12406 | 13243 | 14635 | 16794 | 1: 2902; 2: 3368; 3: 5077; 4: 3178; 1: 3577.9926 | Number per year
| 1.b. | Number of wires down (total) | 1532 | 1865 | 1639 | 1217 | 1524 | 1: 391; 2: 537; 3: 523; 4: 593; 1: 503.0485 | Number of wires down per year
| 1.c. | Number of outage events not caused by contact with vegetation (total) | 11930 | 11833 | 12621 | 14211 | 16260 | 1: 2798; 2: 3298; 3: 5051; 4: 3062; 1: 3554 | Number of outage events per year
| 1.d. | Number of outage events caused by contact with vegetation (total) | 407 | 573 | 622 | 424 | 534 | 1: 104; 2: 70; 3: 26; 4: 116; 1: 95 | Number of outage events per year
2. Utility inspection findings - Distribution | 2.a. | Number of Level 1 findings (distribution - total) | 19559 | 22364 | 23598 | 20998 | 24028 | 1: 4857; 2: 5595; 3: 6993; 4: 5634; 1: 5307 | # findings
| 2.b. | Number of Level 2 findings (distribution - total) | 92109 | 79438 | 69257 | 82818 | 150166 | 1: 23217; 2: 24739; 3: 22511; 4: 25372; 1: 21731 | # findings
| 2.c. | Number of Level 3 findings (distribution - total) | 85588 | 77057 | 64408 | 72774 | 189600 | 1: 14381; 2: 19487; 3: 19984; 4: 21075; 1: 18450 | # findings
| 2.d. | Number of distribution circuit miles inspected | 51792.2657 | 51847.9404 | 51228.4327 | 77907.5534 | 69595.9832 | 1: 6495.602; 2: 31117.9641; 3: 19188.6784; 4: 11732.8186; 1: 12685 | # circuit miles | This total is a summation of all the completed distribution inspection program circuit miles, therefore will be a significantly larger number than the circuit miles of the distribution system.
2. Utility inspection findings - Transmission | 2.a.ii | Number of Level 1 findings (transmission - total) | 242 | 255 | 213 | 180 | 305 | 1: 58; 2: 51; 3: 108; 4: 108; 1: 67 | # findings | Transmission lines for faults and wire downs are typically 65kV and above, but may include some lower voltages (such as 55kV and 33kV).
| 2.b.ii | Number of Level 2 findings (transmission - total) | 5350 | 5191 | 6399 | 7025 | 23047 | 1: 3265; 2: 8278; 3: 3334; 4: 2249; 1: 2170 | # findings
| 2.c.ii | Number of Level 3 findings (transmission - total) | 7025 | 3353 | 3065 | 1745 | 5188 | 1: 791; 2: 1218; 3: 863; 4: 596; 1: 580 | # findings
| 2.d.ii | Number of transmission circuit miles inspected | 19528.4329 | 17660.7254 | 19294.6159 | 24587.5806 | 24986.3263 | 1: 7558.4775; 2: 8050.2227; 3: 8091.2014; 4: 7845.3288; 1: 5937 | # circuit miles | This total is a summation of all the completed transmission inspection program circuit miles, therefore will be a significantly larger number than the circuit miles of the transmission system.
3. Utility ignited wildfire fatalities | 3.a. | Fatalities due to utility-ignited wildfire (total) | 0 | 0 | 2 | 3 | 1 | 1: 0; 2: 0; 3: 0; 4: 0; 1: 0 | Number of fatalities per year | The information provided in conjunction with the “utility-ignited” wildfire statistics should not be construed as an admission of any wrongdoing or liability by SCE. SCE further notes that the damages metrics provided may be tracked by other agencies and thus, SCE does not guarantee the accuracy of such information. Additionally, in many instances the cause of wildfires are still under investigation and even where an Authority Having Jurisdiction (AHJ) has issued a report on the cause, SCE may dispute the conclusions of such report. Data provided includes wildfires reported in SCE’s Fire Incident Data Report, Electric Incident Safety Report and fatalities data from CAL FIRE. Thomas and Woosley CAL FIRE data contributed to the entirety of the 2017 and 2018 values.
| 3.b. | Injuries due to utility-ignited wildfire (total) | 0 | 3 | 2 | 3 | 3 | 1: 0; 2: 0; 3: 6; 4: 2; 1: 0 | Number of injuries per year | The information provided in conjunction with the “utility-ignited” wildfire statistics should not be construed as an admission of any wrongdoing or liability by SCE. SCE further notes that the damages metrics provided may be tracked by other agencies and thus, SCE does not guarantee the accuracy of such information. Additionally, in many instances the cause of wildfires are still under investigation and even where an Authority Having Jurisdiction (AHJ) has issued a report on the cause, SCE may dispute the conclusions of such report. Data provided includes wildfires reported in SCE’s Fire Incident Data Report and Electric Incident Safety Report.
4. Value of assets destroyed by utility-ignited wildfire, listed by asset type | 4.a. | Value of assets destroyed by utility-ignited wildfire (total) | 21944989 | 483632927 | 1601205795 | 3342821539 | 21714000 | 1: 150400; 2: 300800; 3: 120688284; 4: 12082300; 1: 169200 | Dollars of damage or destruction per year | The information provided in conjunction with the “utility-ignited” wildfire statistics should not be construed as an admission of any wrongdoing or liability by SCE. SCE further notes that the damages metrics provided may be tracked by other agencies and thus, SCE does not guarantee the accuracy of such information. Additionally, in many instances the cause of wildfires are still under investigation and even where an Authority Having Jurisdiction (AHJ) has issued a report on the cause, SCE may dispute the conclusions of such report. Asset type listed is either SCE or Third Party. Asset per the WSD guidance is utility electrical equipment or third party property. SCE asset value using a per unit cost based on the identified equipment failure for each CPUC reportable ignition. Data provided includes wildfires reported in SCE’s Fire Incident Data Report, Electric Incident Safety Report and asset value data from CAL FIRE and the California Department of Insurance. Where third party source of information was unavailable, SCE applied a proxy cost per structure destroyed of $819,472 based on its methodology used in its RAMP report. The California Department of Insurance and proxy cost data use information from insured claims.
5. Structures damaged or destroyed by utility-ignited wildfire | 5.a. | Number of structures destroyed by utility-ignited wildfire (total) | 45 | 290 | 1072 | 1667 | 26 | 1: 0; 2: 0; 3: 47; 4: 13; 1: 0 | Number of structures destroyed per year | The information provided in conjunction with the “utility-ignited” wildfire statistics should not be construed as an admission of any wrongdoing or liability by SCE. SCE further notes that the damages metrics provided may be tracked by other agencies and thus, SCE does not guarantee the accuracy of such information. Additionally, in many instances the cause of wildfires are still under investigation and even where an Authority Having Jurisdiction (AHJ) has issued a report on the cause, SCE may dispute the conclusions of such report. Structure is defined as a dwelling, per WSD guidance. Data provided includes wildfires reported in SCE’s Fire Incident Data Report and Electric Incident Safety Reports and structures destroyed data from CAL FIRE.
| 5.b. | Critical infrastructure damaged/destroyed by utility-ignited wildfire (total) | NA | NA | 36 | 31 | NA | [12 empty] | Number of critical infrastructure damaged/destroyed per year | The information provided in conjunction with the “utility-ignited” wildfire statistics should not be construed as an admission of any wrongdoing or liability by SCE. SCE further notes that the damages metrics provided may be tracked by other agencies and thus, SCE does not guarantee the accuracy of such information. Additionally, in many instances the cause of wildfires are still under investigation and even where an Authority Having Jurisdiction (AHJ) has issued a report on the cause, SCE may dispute the conclusions of such report. Data was drawn from available subrogation claims. These numbers may be updated as more information becomes available. | bar: 1 to 1
6. Acreage burned by utility-ignited wildfire | 6.a. | Acreage burned by utility-ignited wildfire (total) | 15711 | 82897 | 292051 | 97240 | 22784 | 1: 4; 2: 574; 3: 115871; 4: 12863; 1: 12 | Acres burned per year | The information provided in conjunction with the “utility-ignited” wildfire statistics should not be construed as an admission of any wrongdoing or liability by SCE. SCE further notes that the damages metrics provided may be tracked by other agencies and thus, SCE does not guarantee the accuracy of such information. Additionally, in many instances the cause of wildfires are still under investigation and even where an Authority Having Jurisdiction (AHJ) has issued a report on the cause, SCE may dispute the conclusions of such report. Data provided includes wildfires reported in SCE’s Fire Incident Data Report and Electric Incident Safety Reports and acreage burned data from CAL FIRE.
7. Number of utility wildfire ignitions | 7.a. | Number of ignitions (total) according to existing ignition data reporting requirement | 107 | 96 | 105 | 110 | 124 | 1: 16; 2: 56; 3: 45; 4: 32; 1: 28 | Number per year | Data are from SCE's CPUC reportable ignitions data set. Historical numbers were updated due to a tabulation error.
| 7.b. | Number of ignitions in HFTD (subtotal) | 45 | 41 | 32 | 37 | 35 | 1: 3; 2: 21; 3: 17; 4: 9; 1: 7 | Number in HFTD per year
| 7.c. | Number of ignitions in HFTD Zone 1 | 0 | 0 | 0 | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; 1: 0 | Number in HFTD Zone 1 per year
| 7.c.ii. | Number of ignitions in HFTD Tier 2 | 13 | 12 | 9 | 15 | 13 | 1: 1; 2: 5; 3: 6; 4: 3; 1: 1 | Number in HFTD Tier 2 per year
| 7.c.iii. | Number of ignitions in HFTD Tier 3 | 32 | 29 | 23 | 22 | 22 | 1: 2; 2: 16; 3: 11; 4: 6; 1: 6 | Number in HFTD Tier 3 per year
|  | Number of ignitions in Non-CPUC HFTD | 1 | 0 | 3 | 1 | 3 | 1: 0; 2: 0; 3: 0; 4: 0; 1: 0 | Number in Non-CPUC HFTD
| 7.d. | Number of ignitions in non-HFTD (subtotal) | 61 | 55 | 70 | 72 | 86 | 1: 13; 2: 35; 3: 28; 4: 23; 1: 21 | Number in non-HFTD per year
8. Fatalities resulting from utility wildfire mitigation initiatives | 8.a. | Fatalities due to utility wildfire mitigation activities (total) - "activities" defined as all activities accounted for in the 2020 WMP proposed WMP spend | 0 | 0 | 0 | 0 | 0 | 1: 1; 2: 0; 3: 0; 4: 0; 1: 0 | Number of fatalities per year | By providing this data, SCE is not admitting that 1) any responsibility or liability for any incident reported herein or 2) that a wildfire mitigation activity caused a fatality.
9. OSHA-reportable injuries from utility wildfire mitigation initiatives | 9.a. | OSHA-reportable injuries due to utility wildfire mitigation activities (total) - "activities" defined as all activities accounted for in the 2020 WMP proposed WMP spend | 0 | 0 | 0 | 0 | 1 | 1: 0; 2: 1; 3: 3; 4: 0; 1: 0 | Number of OSHA-reportable injuries per year | By providing this data, SCE is not admitting that 1) any responsibility or liability for any incident reported herein or 2) that a wildfire mitigation activity caused an injury.

## Table 3
Utility | Southern California Edison Company
Table No. | 3
Date Modified | 2021-05-03
Note: These columns are placeholders for future QR submissions.
Table 3: List and description of additional metrics | [9 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric | Definition | Purpose | Assumptions made to connect metric to purpose | Third-party validation (if any) | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
CPUC reportable ignitions in High Fire Risk Areas (HFRA) | Events meeting reportable ignition status per Decision 14-02-015 and falling within BL322, HFTD Zone 1 HFTD Tier 2 and 200 ft. Outer Buffer, and HFTD Tier 3 and 200 ft. Outer Buffer areas | To measure changes in rate of ignitions between years | Factors outside of SCE's control (e.g., wind, live fuel moisture) have a significant effect on CPUC reportable ignition counts in HFRA. | Annual submission of CPUC reportable ignition totals to CPUC | 46 | 41 | 35 | 37 | 38 | 1: 3; 2: 22; 3: 16; 4: 9; 1: 7 | Number of reportable ignitions in HFRA | HFRA includes HFTD Tier 3, HFTD Tier 2, HFTD Zone 1, and BL322 (non-CPUC HFRA)
Faults in HFRA | Events in which electrical current deviates from the anticpated path via SCE facilities within BL322, HFTD Zone 1 HFTD Tier 2 and 200 ft. Outer Buffer, and HFTD Tier 3 and 200 ft. Outer Buffer areas | To measure changes in rate of fault events which are a pre-cursor both ignition and safety events | Number of faults in HFRA based on cause. These metrics may help to provide insight on controllable and uncontrollable risks or help plan future activities to focus on a particular type of fault or outage that may be of wildfire risk. | Deep-dive audits of select portions of utility grid | 3723 | 4004 | 4286 | 4558 | 6578 | 1: 1011; 2: 1147; 3: 1436; 4: 1132; 1: 912 | Number of faults in HFRA | HFRA includes HFTD Tier 3, HFTD Tier 2, HFTD Zone 1, and BL322 (non-CPUC HFRA). Note: SCE is incorporating additional Transmission outage data as an improvement to its outage reporting. Historical reporting has been revised to reflect the additional Transmission outage data.
Wire Down Incidents in HFRA | Events in which SCE overhead conductors (energized or de-energized) fall within 8ft above ground or lower, within BL322, HFTD Tier 2 and 200 ft. Outer Buffer, and HFTD Tier 3 and 200 ft. Outer Buffer areas | To measure changes in rate of wire down events which are a pre-cursor both ignition and safety events | Number of wire down incidents in HFRA based on cause. These metrics may help to provide insight on controllable and uncontrollable risks or help plan future activities to focus on a particular type of fault or outage that may be of wildfire risk. | Deep-dive audits of select portions of utility grid | 245 | 338 | 304 | 199 | 303 | 1: 72; 2: 86; 3: 77; 4: 85; 1: 116 | Number of wire downs per year in HFRA | HFRA includes HFTD Tier 3, HFTD Tier 2, HFTD Zone 1, and BL322 (non-CPUC HFRA)
Number of customers and average duration of Public Safety Power Shutoff (PSPS) events
Total # of customers de-energized | Count of customers de-energized, with duplicates, per year | To measure the scale of impact of outages due to PSPS to customers, with duplicates | Not Applicable | Not Applicable | Refer to Table 11, # 4.a. | Refer to Table 11, # 4.a. | Refer to Table 11, # 4.a. | Refer to Table 11, # 4.a. | Refer to Table 11, # 4.a. | 1: Refer to Table 11, # 4.a.; 2: Refer to Table 11, # 4.a.; 3: Refer to Table 11, # 4.a.; 4: Refer to Table 11, # 4.a.; 1: Refer to Table 11, # 4.a. | Number of customers | None
Average duration of de-energization across all customers. | Average outage duration experienced by PSPS de-energization per customer de-energized | Of the customers de-energized due to PSPS, to measure the magnitude of the effect of the PSPS de-energization | Not Applicable | Not Applicable | N/A | N/A | 30.3 | 23.2 | 27 | 1: N/A; 2: N/A; 3: 2.2; 4: 18.3; 1: 23.9 | Hours | Applies to each instance of a customer being de-energized due to PSPS
Timeliness and accuracy of PSPS notifications
% of customers notified prior to a PSPS event impacting them | # of customers notified prior to initiation of PSPS event who were impacted by PSPS/ # of customers impacted by PSPS (if multiple PSPS events impact the same customer, count each event as a separate customer) | To measure success rate of notification for the customers who were impacted by de-energization | Not Applicable | Not Applicable | Refer to Table 11, # 4.e. | Refer to Table 11, # 4.e. | Refer to Table 11, # 4.e. | Refer to Table 11, # 4.e. | Refer to Table 11, # 4.e. | 1: Refer to Table 11, # 4.e.; 2: Refer to Table 11, # 4.e.; 3: Refer to Table 11, # 4.e.; 4: Refer to Table 11, # 4.e.; 1: Refer to Table 11, # 4.e. | Percentage | None
% of customers notified prior to a PSPS event that did not impact them | % of customers notified of potential de-energization that were not de-energized for that PSPS event (on a total customer basis) 1 - (# of total customers de-energized / # of imminent de-energization notifications sent) | To measure the occurrence of PSPS notifications and de-energizations | Not Applicable | Not Applicable | N/A | N/A | N/A | N/A | N/A | 1: N/A; 2: 100%; 3: 39%; 4: 61%; 1: 64.6% | % of customers notified of imminent potential de-energization that were not de-energized for that PSPS event (on a total customer basis) | This data was not recorded prior to 2020.

## Table 4
Utility | Southern California Edison Company
Table No. | 4
Date Modified | 2021-05-03
Note: These columns are placeholders for future QR submissions.
Table 4: Fatalities due to utility wildfire mitigation initiatives | [7 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Outcome metric name | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
1. Fatalities - Full-time Employee | 1.a. | Fatalities due to utility inspection - Full-time employee | 0 | 0 | 0 | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; 1: 0 | # fatalities
| 1.b. | Fatalities due to vegetation management - Full-time employee | 0 | 0 | 0 | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; 1: 0 | # fatalities
| 1.c. | Fatalities due to utility fuel management - Full-time employee | 0 | 0 | 0 | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; 1: 0 | # fatalities
| 1.d. | Fatalities due to grid hardening - Full-time employee | 0 | 0 | 0 | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; 1: 0 | # fatalities
| 1.e. | Fatalities due to other - Full-time employee | 0 | 0 | 0 | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; 1: 0 | # fatalities
2. Fatalities - Contractor | 2.a. | Fatalities due to utility inspection - Contractor | 0 | 0 | 0 | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; 1: 0 | # fatalities
| 2.b. | Fatalities due to vegetation management - Contractor | 0 | 0 | 0 | 0 | 0 | 1: 1; 2: 0; 3: 0; 4: 0; 1: 0 | # fatalities | By providing this data, SCE is not admitting: 1) any responsibility or liability for any incident reported herein or 2) that a wildfire mitigation activity caused a fatality.
| 2.c. | Fatalities due to utility fuel management - Contractor | 0 | 0 | 0 | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; 1: 0 | # fatalities
| 2.d. | Fatalities due to grid hardening - Contractor | 0 | 0 | 0 | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; 1: 0 | # fatalities
| 2.e. | Fatalities due to other - Contractor | 0 | 0 | 0 | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; 1: 0 | # fatalities
3. Fatalities - Member of public | 3.a. | Fatalities due to utility inspection - Public | 0 | 0 | 0 | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; 1: 0 | # fatalities
| 3.b. | Fatalities due to vegetation management - Public | 0 | 0 | 0 | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; 1: 0 | # fatalities
| 3.c. | Fatalities due to utility fuel management - Public | 0 | 0 | 0 | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; 1: 0 | # fatalities
| 3.d. | Fatalities due to grid hardening - Public | 0 | 0 | 0 | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; 1: 0 | # fatalities
| 3.e. | Fatalities due to other - Public | 0 | 0 | 0 | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; 1: 0 | # fatalities

## Table 5
Utility | Southern California Edison Company
Table No. | 5
Date Modified | 2021-05-03
Note: These columns are placeholders for future QR submissions.
Table 5: OSHA-reportable injuries due to utility wildfire mitigation initiatives | [7 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Outcome metric name | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
1. OSHA injuries - Full-time Employee | 1.a. | OSHA injuries due to utility inspection - Full-time employee | 0 | 0 | 0 | 0 | 1 | 1: 0; 2: 0; 3: 0; 4: 0; 1: 0 | # OSHA-reportable injuries | SCE's 2020 WMP inadvertantly excluded an injury that an employee incurred during the course of asset inspections.
| 1.b. | OSHA injuries due to vegetation management - Full-time employee | 0 | 0 | 0 | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; 1: 0 | # OSHA-reportable injuries
| 1.c. | OSHA injuries due to utility fuel management - Full-time employee | 0 | 0 | 0 | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; 1: 0 | # OSHA-reportable injuries
| 1.d. | OSHA injuries due to grid hardening - Full-time employee | 0 | 0 | 0 | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; 1: 0 | # OSHA-reportable injuries | In a data request response to WSD dated August 14, 2020, SCE inadvertently classified a serious injury to an employee as incurred during performance of a wildfire mitigation initiative. That employee was replacing a deteriorated pole, which is not a wildfire mitigation initiative and as such, that incident is not included in this data. By providing this data, SCE is not admitting that 1) any responsibility or liability for any incident reported herein or 2) that a wildfire mitigation activity caused an injury.
| 1.e. | OSHA injuries due to other - Full-time employee | 0 | 0 | 0 | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; 1: 0 | # OSHA-reportable injuries
2. OSHA injuries - Contractor | 2.a. | OSHA injuries due to utility inspection - Contractor | 0 | 0 | 0 | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; 1: 0 | # OSHA-reportable injuries
| 2.b. | OSHA injuries due to vegetation management - Contractor | 0 | 0 | 0 | 0 | 0 | 1: 0; 2: 1; 3: 0; 4: 0; 1: 0 | # OSHA-reportable injuries | In a data request response to WSD dated August 14, 2020, SCE inadvertently classified an injury to a contractor as OSHA-reportable when it actually did not meet that definition and as such, that incident is not included in this data. By providing this data, SCE is not admitting that 1) any responsibility or liability for any incident reported herein or 2) that a wildfire mitigation activity caused an injury.
| 2.c. | OSHA injuries due to utility fuel management - Contractor | 0 | 0 | 0 | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; 1: 0 | # OSHA-reportable injuries
| 2.d. | OSHA injuries due to grid hardening - Contractor | 0 | 0 | 0 | 0 | 0 | 1: 0; 2: 0; 3: 3; 4: 0; 1: 0 | # OSHA-reportable injuries | In a data request response to WSD dated August 14, 2020, SCE inadvertently classified a serious injury to a contractor as incurred during performance of a wildfire mitigation initiative. That contractor was replacing a deteriorated pole, which is not a wildfire mitigation initiative and as such, that incident is not included in this data. By providing this data, SCE is not admitting that 1) any responsibility or liability for any incident reported herein or 2) that a wildfire mitigation activity caused an injury.
| 2.e. | OSHA injuries due to other - Contractor | 0 | 0 | 0 | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; 1: 0 | # OSHA-reportable injuries
3. OSHA injuries - Member of public | 3.a. | OSHA injuries due to utility inspection - Public | 0 | 0 | 0 | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; 1: 0 | # OSHA-reportable injuries
| 3.b. | OSHA injuries due to vegetation management - Public | 0 | 0 | 0 | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; 1: 0 | # OSHA-reportable injuries
| 3.c. | OSHA injuries due to utility fuel management - Public | 0 | 0 | 0 | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; 1: 0 | # OSHA-reportable injuries
| 3.d. | OSHA injuries due to grid hardening - Public | 0 | 0 | 0 | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; 1: 0 | # OSHA-reportable injuries
| 3.e. | OSHA injuries due to other - Public | 0 | 0 | 0 | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; 1: 0 | # OSHA-reportable injuries

## Table 6
Utility | Southern California Edison Company
Table No. | 6
Date Modified | 2021-05-03
Note: These columns are placeholders for future QR submissions.
Table 6: Weather patterns | [7 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Outcome metric name | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
1. Red Flag Warning Overhead circuit mile Days | 1.a. | Red Flag Warning Overhead circuit mile days - entire utility territory | 80503.67 | 286326.53 | 476404.26 | 283806.28 | 201423 | 1: 0; 2: 24844.84; 3: 62241.17; 4: 162421.73; 1: 58515.1798 | Sum of overhead circuit miles of utility grid subject to Red Flag Warning each day within a given time period, calculated as the number of overhead circuit miles that were under an RFW multiplied by the number of days those circuit miles were under said RFW. For example, if 100 overhead circuit miles were under an RFW for 1 day, and 10 of those miles were under RFW for an additional day, then the total RFW OH circuit mile days would be 110. | GIS systems are used in order to overlay the locational information of each red flag warning. GIS models are updated frequently with changes within SCE's service territroy and does not have the ability to analyze and calculate information in previous years. As such, the overhead lengths of distribution and transmission circuits are based on 2020 circuit mile information for the calculation of historical years 2015-2019. Additionally, this overall number may be slightly different than the 2020 WMP filing due to the use of the 2020 GIS information. Historical information was re-calculated as high fire threat district break outs are new requirements in the 2021 WMP.
| 1.b. | Red Flag Warning Overhead circuit mile days - HFTD Zone 1 | 0.75 | 8.01 | 4.14 | 2.78 | 1.74 | 1: 0; 2: 0.39; 3: 1.25; 4: 1.65; 1: 0.59552 | Red Flag Warning Overhead circuit mile days, see above for definition | GIS systems are used in order to overlay the locational information of each red flag warning. GIS models are updated frequently with changes within SCE's service territroy and does not have the ability to analyze and calculate information in previous years. As such, the overhead lengths of distribution and transmission circuits are based on 2020 circuit mile information for the calculation of historical years 2015-2019. Additionally, this overall number may be slightly different than the 2020 WMP filing due to the use of the 2020 GIS information. Historical information was re-calculated as high fire threat district break outs are new requirements in the 2021 WMP.
| 1.c. | Red Flag Warning Overhead circuit mile days - HFTD Tier 2 | 9213.87 | 31921.01 | 50038.98 | 31294.57 | 21597.87 | 1: 0; 2: 4391.03; 3: 10010.96; 4: 17964.31; 1: 7002.8517 | Red Flag Warning Overhead circuit mile days, see above for definition | GIS systems are used in order to overlay the locational information of each red flag warning. GIS models are updated frequently with changes within SCE's service territroy and does not have the ability to analyze and calculate information in previous years. As such, the overhead lengths of distribution and transmission circuits are based on 2020 circuit mile information for the calculation of historical years 2015-2019. Additionally, this overall number may be slightly different than the 2020 WMP filing due to the use of the 2020 GIS information. Historical information was re-calculated as high fire threat district break outs are new requirements in the 2021 WMP.
| 1.d. | Red Flag Warning Overhead circuit mile days - HFTD Tier 3 | 25523.13 | 88117.02 | 127005.19 | 82216.16 | 57321.44 | 1: 0; 2: 4030.7; 3: 13919.77; 4: 36805.02; 1: 17403.5949 | Red Flag Warning Overhead circuit mile days, see above for definition | GIS systems are used in order to overlay the locational information of each red flag warning. GIS models are updated frequently with changes within SCE's service territroy and does not have the ability to analyze and calculate information in previous years. As such, the overhead lengths of distribution and transmission circuits are based on 2020 circuit mile information for the calculation of historical years 2015-2019. Additionally, this overall number may be slightly different than the 2020 WMP filing due to the use of the 2020 GIS information. Historical information was re-calculated as high fire threat district break outs are new requirements in the 2021 WMP.
| 1.e. | Red Flag Warning Overhead circuit mile days - Non-HFTD | 45765.92 | 166280.5 | 299355.96 | 170292.77 | 122501.95 | 1: 0; 2: 16422.72; 3: 38309.19; 4: 107650.74; 1: 34108.1376 | Red Flag Warning Overhead circuit mile days, see above for definition | GIS systems are used in order to overlay the locational information of each red flag warning. GIS models are updated frequently with changes within SCE's service territroy and does not have the ability to analyze and calculate information in previous years. As such, the overhead lengths of distribution and transmission circuits are based on 2020 circuit mile information for the calculation of historical years 2015-2019. Additionally, this overall number may be slightly different than the 2020 WMP filing due to the use of the 2020 GIS information. Historical information was re-calculated as high fire threat district break outs are new requirements in the 2021 WMP.
2. Wind conditions | 2.a. | High wind warning overhead circuit mile days | 78964.76 | 116378.06 | 144820.11 | 133880.48 | 95208.03 | 1: 61544.8; 2: 9235.36; 3: 61.99; 4: 57071.56; 1: 78100.9077 | Sum of overhead circuit miles of utility grid subject to High Wind Warnings (HWW, as defined by the National Weather Service) each day within a given time period, calculated as the number of overhead circuit miles that were under an HWW multiplied by the number of days those miles were under said HWW. For example, if 100 overhead circuit miles were under an HWW for 1 day, and 10 of those miles were under HWW for an additional day, then the total HWW OH circuit mile days would be 110. | GIS systems are used in order to overlay the locational information of each red flag warning. GIS models are updated frequently with changes within SCE's service territroy and does not have the ability to analyze and calculate information in previous years. As such, the overhead lengths of distribution and transmission circuits are based on 2020 circuit mile information for the calculation of historical years 2015-2019. Additionally, this overall number may be slightly different than the 2020 WMP filing due to the use of the 2020 GIS information. Historical information was re-calculated as high fire threat district break outs are new requirements in the 2021 WMP.
3. Other | 3.a. | Other relevant weather pattern metrics tracked (add additional rows as needed) | bar: 1 to 4

## Table 7.1
Utility | Southern California Edison Company | Notes:
Table No. | 7.1 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV. Transmission lines for faults and wire downs are typically 65kV and above, but may include some lower voltages (such as 55kV and 33kV).
Date Modified | 2021-05-03 | Data from 2015 - 2020 Q2 should be actual numbers. 2020 Q3 - 2023 should be projected. In future submissions update projected numbers with actuals
[5 empty] | Number of risk events | [9 empty] | Projected risk events
Table 7.1: Key recent and projected drivers of risk events | [9 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Risk Event category | Cause category | # | Sub-cause category | Are risk events tracked for ignition driver? (yes / no) | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
Wire down event - Distribution | 1. Contact from object - Distribution | 1.a. | Veg. contact- Distribution | Yes | 279 | 357 | 384 | 158 | 308 | 86 | 105 | 82 | 151 | 114 | 72.9981 | 77.8571 | 88.4194 | 76.9038 | 72.1144 | 76.9201 | 87.3666 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 1.b. | Animal contact- Distribution | Yes | 74 | 57 | 53 | 48 | 38 | 10 | 19 | 29 | 12 | 11 | 13.4125 | 13.6581 | 13.6495 | 13.208 | 12.9111 | 13.1485 | 13.1402 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 1.c. | Balloon contact- Distribution | Yes | 115 | 112 | 115 | 134 | 98 | 22 | 47 | 27 | 12 | 24 | 42.9125 | 21.2905 | 10.7955 | 22.6209 | 40.9078 | 20.2242 | 10.1847 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 1.d. | Vehicle contact- Distribution | Yes | 227 | 349 | 248 | 267 | 269 | 76 | 121 | 88 | 98 | 79 | 70.0874 | 72.2034 | 71.5684 | 76.1991 | 68.9633 | 71.0486 | 70.4228 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 1.e. | Other contact from object - Distribution | Yes | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.11898 | 0.11977 | 0.11979 | 0.11412 | 0.11359 | 0.11435 | 0.11436 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 2. Equipment / facility failure - Distribution | 2.a. | Connector damage or failure- Distribution | Yes | 84 | 106 | 81 | 75 | 68 | 25 | 36 | 38 | 23 | 21.0485 | 22.2205 | 22.3268 | 22.2585 | 21.0485 | 22.2205 | 22.3268 | 22.2585 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 2.b. | Splice damage or failure — Distribution | Yes | 35 | 28 | 24 | 24 | 28 | 3 | 9 | 10 | 7 | 10 | 6.977 | 7.0029 | 6.9862 | 6.9463 | 6.977 | 7.0029 | 6.9862 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 2.c. | Crossarm damage or failure - Distribution | Yes | 31 | 26 | 26 | 25 | 35 | 10 | 10 | 6 | 9 | 15 | 9.8325 | 5.878 | 8.8487 | 9.6278 | 9.6803 | 5.7835 | 8.7109 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 2.d. | Insulator damage or failure- Distribution | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 2.e. | Lightning arrestor damage or failure- Distribution | Yes | 0 | 0 | 3 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0.24934 | 0.24999 | 0.24956 | 0.24791 | 0.24934 | 0.24999 | 0.24956 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 2.f. | Tap damage or failure - Distribution | Yes | 0 | 0 | 4 | 5 | 12 | 4 | 3 | 1 | 2 | 5 | 1.9947 | 2.0006 | 1.9968 | 1.9872 | 1.9947 | 2.0006 | 1.9968 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 2.g. | Tie wire damage or failure - Distribution | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 2.h. | Other - Distribution | Yes | 685 | 824 | 667 | 423 | 607 | 144 | 171 | 198 | 238 | 104 | 169.6758 | 170.4964 | 165.3543 | 173.1122 | 169.6758 | 170.4964 | 165.3543 | # risk events (excluding ignitions) | The total of all sub-cause category types
|  |  | Pole damage or failure - Distribution | Yes | 13 | 12 | 28 | 39 | 37 | 9 | 24 | 20 | 20 | 14 | NA | NA | NA | NA | NA | NA | NA | # risk events (excluding ignitions) | This is a new sub-cause category type added to increase transparency of wire-down events. New sub-cause categories were forecasted as an aggregate rather as individual line items and forecast data is not included for these categories.
|  |  | Pothead damage or failure - Distribution | Yes | 0 | 0 | 3 | 8 | 6 | 3 | 2 | 5 | 1 | 1 | NA | NA | NA | NA | NA | NA | NA | # risk events (excluding ignitions) | This is a new sub-cause category type added to increase transparency of wire-down events. New sub-cause categories were forecasted as an aggregate rather as individual line items and forecast data is not included for these categories.
|  |  | Fuse failure damage or failure - Distribution | Yes | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 2 | 1 | 1 | NA | NA | NA | NA | NA | NA | NA | # risk events (excluding ignitions) | This is a new sub-cause category type added to increase transparency of wire-down events. New sub-cause categories were forecasted as an aggregate rather as individual line items and forecast data is not included for these categories.
|  |  | Guy damage or failure - Distribution | Yes | 0 | 0 | 1 | 3 | 5 | 1 | 0 | 0 | 0 | 0 | NA | NA | NA | NA | NA | NA | NA | # risk events (excluding ignitions) | This is a new sub-cause category type added to increase transparency of wire-down events. New sub-cause categories were forecasted as an aggregate rather as individual line items and forecast data is not included for these categories.
|  |  | Conductor failure damage or failure - Distribution | Yes | 0 | 0 | 28 | 44 | 120 | 33 | 51 | 63 | 57 | 49 | NA | NA | NA | NA | NA | NA | NA | # risk events (excluding ignitions) | This is a new sub-cause category type added to increase transparency of wire-down events. New sub-cause categories were forecasted as an aggregate rather as individual line items and forecast data is not included for these categories.
|  |  | Various other damage or failure - Distribution | Yes | 672 | 812 | 607 | 328 | 437 | 98 | 93 | 108 | 159 | 39 | NA | NA | NA | NA | NA | NA | NA | # risk events (excluding ignitions) | This is a new sub-cause category type added to increase transparency of wire-down events. New sub-cause categories were forecasted as an aggregate rather as individual line items and forecast data is not included for these categories.
| 3. Wire-to-wire contact - Distribution | 3.a. | Wire-to-wire contact / contamination- Distribution | Yes | 0 | 0 | 1 | 2 | 1 | 0 | 4 | 2 | 1 | 4 | 0.98485 | 0.98581 | 0.98553 | 0.97597 | 0.97222 | 0.97317 | 0.97289 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 4. Contamination - Distribution | 4.a. | Contamination - Distribution | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 5. Utility work / Operation | 5.a. | Utility work / Operation | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 6. Vandalism / Theft - Distribution | 6.a. | Vandalism / Theft - Distribution | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 7. Other- Distribution | 7.a. | All Other- Distribution | Yes | 0 | 0 | 33 | 53 | 54 | 11 | 11 | 41 | 39 | 116 | 38.6968 | 38.7886 | 38.7602 | 39.0761 | 38.6968 | 38.7886 | 38.7602 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 8. Unknown- Distribution | 8.a. | Unknown - Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
Wire down event - Transmission | 9. Contact from object - Transmission | 9.a. | Veg. contact- Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 9.b. | Animal contact- Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 9.c. | Balloon contact- Transmission | Yes | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0092728 | 0.0025735 | 0.0025762 | 0.0025736 | 0.0092728 | 0.0025735 | 0.0025762 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 9.d. | Vehicle contact- Transmission | Yes | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0.24478 | 0.21667 | 0.21924 | 0.2802 | 0.24478 | 0.21667 | 0.21924 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 9.e. | Other contact from object - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 10. Equipment / facility failure - Transmission | 10.a. | Connector damage or failure- Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 10.b. | Splice damage or failure — Transmission | Yes | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0.039633 | 0.02925 | 0.032184 | 0.016175 | 0.039633 | 0.02925 | 0.032184 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 10.c. | Crossarm damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 10.d. | Insulator damage or failure- Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 10.e. | Lightning arrestor damage or failure- Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 10.f. | Tap damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 10.g. | Tie wire damage or failure - Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 10.h. | Other - Transmission | Yes | 1 | 3 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0.37881 | 0.34527 | 0.3547 | 0.30383 | 0.37881 | 0.34527 | 0.3547 | # risk events (excluding ignitions) | The total of all sub-cause category types
|  |  | Pole damage or failure - Transmission | Yes | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | NA | NA | NA | NA | # risk events (excluding ignitions) | This is a new sub-cause category type added to increase transparency of wire-down events. New sub-cause categories were forecasted as an aggregate rather as individual line items and forecast data is not included for these categories.
|  |  | Pothead damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | NA | NA | NA | NA | # risk events (excluding ignitions) | This is a new sub-cause category type added to increase transparency of wire-down events. New sub-cause categories were forecasted as an aggregate rather as individual line items and forecast data is not included for these categories.
|  |  | Fuse failure damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | NA | NA | NA | NA | # risk events (excluding ignitions) | This is a new sub-cause category type added to increase transparency of wire-down events. New sub-cause categories were forecasted as an aggregate rather as individual line items and forecast data is not included for these categories.
|  |  | Guy damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | NA | NA | NA | NA | # risk events (excluding ignitions) | This is a new sub-cause category type added to increase transparency of wire-down events. New sub-cause categories were forecasted as an aggregate rather as individual line items and forecast data is not included for these categories.
|  |  | Conductor failure damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | NA | NA | NA | NA | # risk events (excluding ignitions) | This is a new sub-cause category type added to increase transparency of wire-down events. New sub-cause categories were forecasted as an aggregate rather as individual line items and forecast data is not included for these categories.
|  |  | Various other damage or failure - Transmission | Yes | 1 | 2 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | NA | NA | NA | NA | # risk events (excluding ignitions) | This is a new sub-cause category type added to increase transparency of wire-down events. New sub-cause categories were forecasted as an aggregate rather as individual line items and forecast data is not included for these categories.
| 11. Wire-to-wire contact - Transmission | 11.a. | Wire-to-wire contact / contamination- Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 12. Contamination - Transmission | 12.a. | Contamination - Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 13. Utility work / Operation | 13.a. | Utility work / Operation | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 14. Vandalism / Theft - Transmission | 14.a. | Vandalism / Theft - Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 15. Other- Transmission | 15.a. | All Other- Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 16. Unknown- Transmission | 16.a. | Unknown - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
Outage - Distribution | 17. Contact from object - Distribution | 17.a. | Veg. contact- Distribution | Yes | 395 | 557 | 609 | 416 | 527 | 104 | 70 | 25 | 112 | 93 | 38.1287 | 22.1882 | 101.299 | 103.2495 | 31.8643 | 18.222 | 99.3271 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 17.b. | Animal contact- Distribution | Yes | 655 | 598 | 622 | 648 | 686 | 122 | 201 | 169 | 163 | 79 | 195.9688 | 153.2431 | 152.5971 | 110.9656 | 191.3751 | 140.6244 | 145.8163 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 17.c. | Balloon contact- Distribution | Yes | 758 | 785 | 911 | 975 | 776 | 178 | 348 | 275 | 191 | 247 | 320.6408 | 222.5546 | 152.6477 | 220.0694 | 306.7499 | 209.2246 | 143.5466 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 17.d. | Vehicle contact- Distribution | Yes | 508 | 586 | 528 | 647 | 517 | 116 | 113 | 153 | 132 | 145 | 133.5399 | 131.1206 | 131.2175 | 132.4642 | 129.9164 | 123.5194 | 125.3218 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 17.e. | Other contact from object - Distribution | Yes | 870 | 393 | 289 | 369 | 449 | 44 | 28 | 35 | 43 | 64 | 79.447 | 105.8822 | 110.4794 | 106.8642 | 79.2186 | 105.4885 | 109.7027 | # risk events (excluding ignitions) | The total of all sub-cause category types below. An additional sub-cause category type was added below requiring a new summation for the total.
|  |  | Ice/Snow - Distribution | Yes | 4 | 15 | 19 | 9 | 3 | 0 | 0 | 0 | 0 | 1 | NA | NA | NA | NA | NA | NA | NA | # risk events (excluding ignitions) | This is a new sub-cause category type added to increase transparency of outage events. New sub-cause categories were forecasted as an aggregate rather as individual line items and forecast data is not included for these categories.
|  |  | Lightning - Distribution | Yes | 757 | 264 | 167 | 225 | 323 | 20 | 2 | 15 | 27 | 29 | NA | NA | NA | NA | NA | NA | NA | # risk events (excluding ignitions) | This is a new sub-cause category type added to increase transparency of outage events. The new sub-cause categories were originally forecasted under "23. Other- Distribution" and now has been moved to "17. Contact from object - Distribution"
|  |  | Various other contact from object - Distribution | Yes | 109 | 114 | 103 | 135 | 123 | 24 | 26 | 20 | 16 | 34 | NA | NA | NA | NA | NA | NA | NA | # risk events (excluding ignitions) | This is a new sub-cause category type added to increase transparency of outage events. New sub-cause categories were forecasted as an aggregate rather as individual line items and forecast data is not included for these categories.
| 18. Equipment / facility failure - Distribution | 18.a. | Capacitor bank damage or failure- Distribution | Yes | 319 | 309 | 425 | 376 | 457 | 128 | 160 | 73 | 44 | 111 | 94.2875 | 91.8356 | 94.5912 | 88.2857 | 94.1513 | 91.7541 | 94.5912 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 18.b. | Conductor damage or failure — Distribution | Yes | 463 | 594 | 654 | 713 | 1116 | 205 | 143 | 211 | 250 | 277 | 224.8348 | 179.6551 | 146.1158 | 132.6306 | 194.8874 | 148.8054 | 84.6661 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 18.c. | Fuse damage or failure - Distribution | Yes | 232 | 195 | 245 | 508 | 1245 | 169 | 176 | 316 | 167 | 180 | 166.3801 | 132.4833 | 165.8352 | 168.3709 | 166.3579 | 132.4567 | 165.8346 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 18.d. | Lightning arrestor damage or failure- Distribution | Yes | 105 | 127 | 99 | 105 | 216 | 27 | 21 | 26 | 25 | 12 | 31.2647 | 29.5828 | 31.234 | 31.3598 | 31.2646 | 29.5828 | 31.234 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 18.e. | Switch damage or failure- Distribution | Yes | 51 | 46 | 45 | 67 | 78 | 17 | 11 | 16 | 18 | 14.5447 | 14.5232 | 14.4021 | 14.5296 | 14.5404 | 14.5137 | 14.3962 | 14.5301 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 18.f. | Pole damage or failure - Distribution | Yes | 98 | 126 | 130 | 207 | 541 | 57 | 36 | 31 | 41 | 32 | 40.9031 | 38.2312 | 40.9086 | 41.0991 | 40.8877 | 38.1883 | 40.9079 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 18.g. | Insulator and brushing damage or failure - Distribution | Yes | 42 | 75 | 79 | 123 | 121 | 28 | 14 | 11 | 43 | 30 | 16.7551 | 15.161 | 31.1615 | 24.2761 | 16.4622 | 15.1041 | 31.0259 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 18.h. | Crossarm damage or failure - Distribution | Yes | 127 | 143 | 138 | 354 | 834 | 98 | 45 | 29 | 45 | 39 | 74.5362 | 60.2414 | 74.1561 | 75.2788 | 74.5053 | 60.2414 | 74.1099 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 18.i. | Voltage regulator / booster damage or failure - Distribution | Yes | 1 | 2 | 1 | 2 | 4 | 0 | 0 | 1 | 1 | 0 | 0.49994 | 0.49774 | 0.49992 | 0.50009 | 0.49994 | 0.49774 | 0.49992 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 18.j. | Recloser damage or failure - Distribution | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 18.k. | Anchor / guy damage or failure - Distribution | Yes | 17 | 20 | 18 | 17 | 20 | 3 | 3 | 3 | 4 | 3 | 3.8785 | 1.6262 | 5.8321 | 5.9347 | 3.8785 | 1.6262 | 5.8321 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 18.l. | Sectionalizer damage or failure - Distribution | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 18.m. | Connection device damage or failure - Distribution | Yes | 386 | 490 | 406 | 501 | 500 | 123 | 111 | 86 | 97 | 110.869 | 111.7491 | 109.6329 | 111.7103 | 110.869 | 111.7491 | 109.6329 | 111.7103 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 18.n. | Transformer damage or failure - Distribution | Yes | 1889 | 1649 | 1978 | 2594 | 2489 | 416 | 559 | 1894 | 536 | 403 | 762.342 | 1153.6373 | 712.1476 | 670.9959 | 757.1656 | 1141.2964 | 709.1214 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 18.o. | Other - Distribution | Yes | 96 | 147 | 116 | 173 | 291 | 37 | 40 | 51 | 60 | 49 | 58.848 | 57.0437 | 59.0701 | 59.4109 | 58.1214 | 56.5531 | 58.9276 | # risk events (excluding ignitions) | The total of all sub-cause category types
|  |  | Pole Top Sub damage or failure - Distribution | Yes |  |  |  |  | 1 |  | 1 |  |  | 0 | NA | NA | NA | NA | NA | NA | NA | # risk events (excluding ignitions) | This is a new sub-cause category type added to increase transparency of outage events. New sub-cause categories were forecasted as an aggregate rather as individual line items and forecast data is not included for these categories.
|  |  | Pothead damage or failure - Distribution | Yes | 91 | 143 | 109 | 155 | 128 | 24 | 27 | 27 | 40 | 28 | NA | NA | NA | NA | NA | NA | NA | # risk events (excluding ignitions) | This is a new sub-cause category type added to increase transparency of outage events. New sub-cause categories were forecasted as an aggregate rather as individual line items and forecast data is not included for these categories.
|  |  | Tower damage or failure - Distribution | Yes | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | NA | NA | NA | NA | # risk events (excluding ignitions) | This is a new sub-cause category type added to increase transparency of outage events. New sub-cause categories were forecasted as an aggregate rather as individual line items and forecast data is not included for these categories.
|  |  | Various other damage or failure - Distribution | Yes | 5 | 4 | 7 | 18 | 160 | 13 | 12 | 24 | 20 | 21 | NA | NA | NA | NA | NA | NA | NA | # risk events (excluding ignitions) | This is a new sub-cause category type added to increase transparency of outage events. New sub-cause categories were forecasted as an aggregate rather as individual line items and forecast data is not included for these categories.
| 19. Wire-to-wire contact - Distribution | 19.a. | Wire-to-wire contact / contamination- Distribution | Yes | 46 | 78 | 64 | 41 | 13 | 6 | 5 | 8 | 7 | 3 | 6.8816 | 6.7337 | 6.8577 | 6.9896 | 6.7278 | 6.4899 | 6.7572 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 20. Contamination - Distribution | 20.a. | Contamination - Distribution | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 21. Utility work / Operation | 21.a. | Utility work / Operation | Yes | 149 | 117 | 99 | 94 | 67 | 32 | 15 | 18 | 10 | 16.4736 | 16.449 | 16.3984 | 16.4692 | 16.4736 | 16.449 | 16.3984 | 16.4692 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 22. Vandalism / Theft - Distribution | 22.a. | Vandalism / Theft - Distribution | Yes | 78 | 80 | 78 | 102 | 103 | 23 | 21 | 21 | 15 | 8 | 21.6938 | 21.6817 | 21.7011 | 21.702 | 21.6862 | 21.6792 | 21.7006 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 23. Other- Distribution | 23.a. | All Other- Distribution | Yes | 2010 | 2251 | 2359 | 3147 | 3125 | 481 | 586 | 977 | 453 | 377 | 650.7179 | 958.6047 | 615.3783 | 574.4454 | 650.7179 | 958.6047 | 615.3783 | # risk events (excluding ignitions) | The total of all sub-cause category types. A sub-cause category type was removed below requiring a new summation for the total.
|  |  | De-Energize - Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | NA | NA | NA | NA | NA | NA | NA | # risk events (excluding ignitions) | This is a new sub-cause category type added to increase transparency of outage events. New sub-cause categories were forecasted as an aggregate rather as individual line items and forecast data is not included for these categories.
|  |  | Dig In - Distribution | Yes | 42 | 51 | 57 | 83 | 48 | 10 | 7 | 18 | 13 | 15 | NA | NA | NA | NA | NA | NA | NA | # risk events (excluding ignitions) | This is a new sub-cause category type added to increase transparency of outage events. New sub-cause categories were forecasted as an aggregate rather as individual line items and forecast data is not included for these categories.
|  |  | Source Lost - Distribution | Yes | 5 | 2 | 26 | 49 | 96 | 12 | 14 | 14 | 4 | 15 | NA | NA | NA | NA | NA | NA | NA | # risk events (excluding ignitions) | This is a new sub-cause category type added to increase transparency of outage events. New sub-cause categories were forecasted as an aggregate rather as individual line items and forecast data is not included for these categories.
|  |  | Substation - Distribution | Yes | 10 | 18 | 30 | 61 | 106 | 16 | 24 | 22 | 18 | 29 | NA | NA | NA | NA | NA | NA | NA | # risk events (excluding ignitions) | This is a new sub-cause category type added to increase transparency of outage events. New sub-cause categories were forecasted as an aggregate rather as individual line items and forecast data is not included for these categories.
|  |  | Underground Equipment - Distribution | Yes | 1949 | 2166 | 2234 | 2944 | 2846 | 442 | 531 | 909 | 409 | 318 | NA | NA | NA | NA | NA | NA | NA | # risk events (excluding ignitions) | This is a new sub-cause category type added to increase transparency of outage events. New sub-cause categories were forecasted as an aggregate rather as individual line items and forecast data is not included for these categories.
|  |  | Various other - Distribution | Yes | 4 | 14 | 12 | 10 | 29 | 1 | 10 | 13 | 9 | 0 | NA | NA | NA | NA | NA | NA | NA | # risk events (excluding ignitions) | This is a new sub-cause category type added to increase transparency of outage events. New sub-cause categories were forecasted as an aggregate rather as individual line items and forecast data is not included for these categories.
| 24. Unknown- Distribution | 24.a. | Unknown - Distribution | Yes | 2142 | 2141 | 2408 | 1741 | 1883 | 364 | 466 | 513 | 558 | 603 | 529.9954 | 525.4369 | 495.9689 | 550.621 | 529.9954 | 525.4369 | 495.9689 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
Outage - Transmission | 25. Contact from object - Transmission | 25.a. | Veg. contact- Transmission | Yes | 12 | 16 | 13 | 8 | 7 | 0 | 0 | 1 | 4 | 2 | 2.4597 | 2.5086 | 2.4945 | 3.004 | 2.4597 | 2.5086 | 2.4944 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 25.b. | Animal contact- Transmission | Yes | 80 | 75 | 67 | 67 | 31 | 7 | 19 | 4 | 8 | 4 | 7.0419 | 7.708 | 7.6697 | 8.0918 | 6.3501 | 7.5096 | 7.6036 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 25.c. | Balloon contact- Transmission | Yes | 23 | 39 | 55 | 36 | 24 | 2 | 13 | 5 | 8 | 9 | 9.8691 | 7.9105 | 8.4538 | 7.6811 | 9.8691 | 7.9105 | 8.4538 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 25.d. | Vehicle contact- Transmission | Yes | 36 | 37 | 40 | 29 | 18 | 3 | 5 | 5 | 3 | 7 | 3.9934 | 4.0692 | 4.0497 | 4.0791 | 3.9934 | 4.0692 | 4.0497 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 25.e. | Other contact from object - Transmission | Yes | 75 | 36 | 35 | 18 | 28 | 7 | 4 | 5 | 3 | 1 | 7.3485 | 8.0128 | 7.8423 | 8.0995 | 7.3485 | 8.0128 | 7.8423 | # risk events (excluding ignitions) | The total of all sub-cause category types below. An additional sub-cause category type was added below requiring a new summation for the total.
|  |  | Ice/Snow - Transmission | Yes |  | 2 | 2 | 0 | 3 | 0 | 2 | 0 | 0 | 0 | NA | NA | NA | NA | NA | NA | NA | # risk events (excluding ignitions) | This is a new sub-cause category type added to increase transparency of outage events. New sub-cause categories were forecasted as an aggregate rather as individual line items and forecast data is not included for these categories.
|  |  | Lighting - Transmission | Yes | 64 | 22 | 28 | 33 | 21 | 4 | 1 | 5 | 2 | 0 | NA | NA | NA | NA | NA | NA | NA | # risk events (excluding ignitions) | This is a new sub-cause category type added to increase transparency of outage events. The new sub-cause categories were originally forecasted under "31. Other- Transmission" and now has been moved to "25. Contact from object - Transmission"
|  |  | Various other contact from object - Transmission | Yes | 11 | 12 | 5 | 5 | 4 | 3 | 1 | 0 | 1 | 1 | NA | NA | NA | NA | NA | NA | NA | # risk events (excluding ignitions) | This is a new sub-cause category type added to increase transparency of outage events. New sub-cause categories were forecasted as an aggregate rather as individual line items and forecast data is not included for these categories.
| 26. Equipment / facility failure - Transmission | 26.a. | Capacitor bank damage or failure- Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.00010929 | 0 | 1.2096e-05 | 0 | 0.00010929 | 0 | 1.2096e-05 | 0 | # risk events (excluding ignitions) | Note that due to certain enhancements made to determining cause sub-categories of events, figures in this table may not tie exactly to those provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 26.b. | Conductor damage or failure — Transmission | Yes | 22 | 15 | 89 | 44 | 36 | 5 | 2 | 13 | 7 | 10 | 9.2946 | 9.736 | 9.6123 | 10.1192 | 9.2946 | 9.736 | 9.6123 | # risk events (excluding ignitions) | Note that due to certain enhancements made to determining cause sub-categories of events, figures in this table may not tie exactly to those provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 26.c. | Fuse damage or failure - Transmission | Yes | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.00010929 | 0 | 1.2096e-05 | 0 | 0.00010929 | 0 | 1.2096e-05 | 0 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 26.d. | Lightning arrestor damage or failure- Transmission | Yes | 2 | 5 | 2 | 4 | 1 | 0 | 0 | 1 | 1 | 0 | 0.66451 | 0.66681 | 0.66617 | 0.66878 | 0.66451 | 0.66681 | 0.66617 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 26.e. | Switch damage or failure- Transmission | Yes | 5 | 3 | 4 | 5 | 2 | 3 | 2 | 0 | 0 | 1.0022 | 0.99777 | 1.0001 | 0.99948 | 1.0022 | 0.99777 | 1.0001 | 0.99948 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 26.f. | Pole damage or failure - Transmission | Yes | 12 | 12 | 17 | 7 | 14 | 3 | 0 | 1 | 3 | 2 | 2.863 | 2.8758 | 2.8722 | 2.8869 | 2.863 | 2.8758 | 2.8722 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 26.g. | Insulator and brushing damage or failure - Transmission | Yes | 10 | 13 | 21 | 4 | 9 | 2 | 3 | 1 | 1 | 0 | 2.4196 | 2.5192 | 2.558 | 2.2297 | 2.4196 | 2.5192 | 2.558 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 26.h. | Crossarm damage or failure - Transmission | Yes | 11 | 7 | 7 | 6 | 8 | 2 | 1 | 1 | 0 | 0 | 1.7868 | 1.792 | 1.7905 | 1.7965 | 1.7868 | 1.792 | 1.7905 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 26.i. | Voltage regulator / booster damage or failure - Transmission | Yes | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00010929 | 0 | 1.2096e-05 | 0 | 0.00010929 | 0 | 1.2096e-05 | 0 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 26.j. | Recloser damage or failure - Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 26.k. | Anchor / guy damage or failure - Transmission | Yes | 3 | 8 | 8 | 1 | 4 | 0 | 1 | 2 | 4 | 0 | 1.2847 | 1.2921 | 1.2901 | 1.2985 | 1.2847 | 1.2921 | 1.2901 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 26.l. | Sectionalizer damage or failure - Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 26.m. | Connection device damage or failure - Transmission | Yes | 1 | 1 | 3 | 1 | 2 | 0 | 0 | 0 | 0 | 0.33392 | 0.33272 | 0.33337 | 0.33319 | 0.33392 | 0.33272 | 0.33337 | 0.33319 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 26.n. | Transformer damage or failure - Transmission | Yes | 0 | 1 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0.00070004 | 0 | 7.7477e-05 | 0 | 0.00070004 | 0 | 7.7477e-05 | 0 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 26.o. | Other - Transmission | Yes | 14 | 26 | 10 | 19 | 41 | 3 | 8 | 6 | 8 | 9 | 5.5887 | 5.6235 | 5.6166 | 5.6609 | 5.5887 | 5.6216 | 5.6166 | # risk events (excluding ignitions) | The total of all sub-cause category types
|  |  | Pole Tops Sub damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | NA | NA | NA | NA | # risk events (excluding ignitions) | This is a new sub-cause category type added to increase transparency of outage events. New sub-cause categories were forecasted as an aggregate rather as individual line items and forecast data is not included for these categories.
|  |  | Pothead damage or failure - Transmission | Yes | 6 | 4 | 0 | 12 | 5 | 0 | 0 | 1 | 0 | 0 | NA | NA | NA | NA | NA | NA | NA | # risk events (excluding ignitions) | This is a new sub-cause category type added to increase transparency of outage events. New sub-cause categories were forecasted as an aggregate rather as individual line items and forecast data is not included for these categories.
|  |  | Tower damage or failure - Transmission | Yes | 0 | 2 | 1 | 2 | 0 | 1 | 1 | 2 | 0 | 0 | NA | NA | NA | NA | NA | NA | NA | # risk events (excluding ignitions) | This is a new sub-cause category type added to increase transparency of outage events. New sub-cause categories were forecasted as an aggregate rather as individual line items and forecast data is not included for these categories.
|  |  | Various other - Transmission | Yes | 8 | 20 | 9 | 5 | 36 | 2 | 7 | 3 | 8 | 9 | NA | NA | NA | NA | NA | NA | NA | # risk events (excluding ignitions) | This is a new sub-cause category type added to increase transparency of outage events. New sub-cause categories were forecasted as an aggregate rather as individual line items and forecast data is not included for these categories.
| 27. Wire-to-wire contact - Transmission | 27.a. | Wire-to-wire contact / contamination- Transmission | Yes | 14 | 17 | 15 | 19 | 42 | 9 | 10 | 1 | 3 | 0 | 5.3519 | 5.3987 | 5.3882 | 5.4243 | 5.3519 | 5.3987 | 5.3882 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 28. Contamination - Transmission | 28.a. | Contamination - Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 29. Utility work / Operation | 29.a. | Utility work / Operation | Yes | 10 | 15 | 8 | 9 | 8 | 0 | 1 | 1 | 1 | 2.0601 | 2.1951 | 2.2016 | 2.2002 | 2.0601 | 2.1951 | 2.2016 | 2.2002 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 30. Vandalism / Theft - Transmission | 30.a. | Vandalism / Theft - Transmission | Yes | 4 | 7 | 2 | 10 | 2 | 0 | 0 | 1 | 1 | 0 | 1.1185 | 1.1232 | 1.1221 | 1.1258 | 1.1185 | 1.1232 | 1.1221 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 31. Other- Transmission | 31.a. | All Other- Transmission | Yes | 194 | 238 | 240 | 242 | 193 | 40 | 67 | 47 | 54 | 52 | 66.5006 | 46.8611 | 53.7804 | 40.0592 | 66.5006 | 46.8611 | 53.7804 | # risk events (excluding ignitions) | The total of all sub-cause category types. A sub-cause category type was removed below requiring a new summation for the total.
|  |  | De-energized - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | NA | NA | NA | NA | # risk events (excluding ignitions) | This is a new sub-cause category type added to increase transparency of outage events. New sub-cause categories were forecasted as an aggregate rather as individual line items and forecast data is not included for these categories.
|  |  | Dig In - Transmission | Yes | 1 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | NA | NA | NA | NA | # risk events (excluding ignitions) | This is a new sub-cause category type added to increase transparency of outage events. New sub-cause categories were forecasted as an aggregate rather as individual line items and forecast data is not included for these categories.
|  |  | Source Lost - Transmission | Yes | 7 | 2 | 21 | 38 | 36 | 5 | 3 | 7 | 7 | 3 | NA | NA | NA | NA | NA | NA | NA | # risk events (excluding ignitions) | This is a new sub-cause category type added to increase transparency of outage events. New sub-cause categories were forecasted as an aggregate rather as individual line items and forecast data is not included for these categories.
|  |  | Substation - Transmission | Yes | 179 | 221 | 208 | 188 | 146 | 35 | 63 | 39 | 47 | 39 | NA | NA | NA | NA | NA | NA | NA | # risk events (excluding ignitions) | This is a new sub-cause category type added to increase transparency of outage events. New sub-cause categories were forecasted as an aggregate rather as individual line items and forecast data is not included for these categories.
|  |  | Underground Equipment | Yes | 5 | 4 | 7 | 14 | 7 | 0 | 1 | 1 | 0 | 1 | NA | NA | NA | NA | NA | NA | NA | # risk events (excluding ignitions) | This is a new sub-cause category type added to increase transparency of outage events. New sub-cause categories were forecasted as an aggregate rather as individual line items and forecast data is not included for these categories.
|  |  | Various other - Transmission | Yes | 2 | 10 | 4 | 0 | 4 | 0 | 0 | 0 | 0 | 9 | NA | NA | NA | NA | NA | NA | NA | # risk events (excluding ignitions) | This is a new sub-cause category type added to increase transparency of outage events. New sub-cause categories were forecasted as an aggregate rather as individual line items and forecast data is not included for these categories.
| 32. Unknown- Transmission | 32.a. | Unknown - Transmission | Yes | 371 | 326 | 306 | 160 | 266 | 38 | 60 | 39 | 54 | 50 | 49.7684 | 52.823 | 52.1393 | 54.5018 | 49.7684 | 52.823 | 52.1393 | # risk events (excluding ignitions) | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
Ignition - Distribution | 33. Contact from object - Distribution | 33.a. | Veg. contact- Distribution | Yes | 13 | 12 | 16 | 15 | 13 | 0 | 2 | 3 | 2 | 3 | 3.2091 | 3.3712 | 2.1472 | 1.8191 | 2.9539 | 3.0632 | 2.1226 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 33.b. | Animal contact- Distribution | Yes | 9 | 8 | 6 | 12 | 18 | 0 | 8 | 3 | 4 | 2 | 6.6984 | 5.5929 | 4.5894 | 2.8526 | 6.5831 | 5.3839 | 4.4905 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 33.c. | Balloon contact- Distribution | Yes | 12 | 10 | 18 | 30 | 15 | 0 | 7 | 1 | 2 | 3 | 9.4637 | 6.3196 | 2.7153 | 0.40133 | 9.1856 | 6.1392 | 2.5835 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 33.d. | Vehicle contact- Distribution | Yes | 11 | 6 | 6 | 13 | 10 | 0 | 2 | 1 | 0 | 1 | 3.1939 | 3.0652 | 1.6851 | 1.5075 | 3.0964 | 2.9638 | 1.6133 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 33.e. | Other contact from object - Distribution | Yes | 3 | 6 | 5 | 0 | 6 | 0 | 0 | 3 | 1 | 3 | 1.1527 | 1.1873 | 0.78401 | 0.6283 | 1.1404 | 1.1726 | 0.77391 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 34. Equipment / facility failure - Distribution | 34.a. | Capacitor bank damage or failure- Distribution | Yes | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.070087 | 0.074979 | 0.047747 | 0.013598 | 0.065852 | 0.071607 | 0.046224 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 34.b. | Conductor damage or failure — Distribution | Yes | 2 | 19 | 15 | 5 | 11 | 3 | 6 | 8 | 6 | 5 | 5.7003 | 6.1084 | 3.8455 | 3.3525 | 5.1057 | 5.5005 | 3.3115 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 34.c. | Fuse damage or failure - Distribution | Yes | 1 | 1 | 1 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0.26349 | 0.28269 | 0.21607 | 0.1669 | 0.26287 | 0.28207 | 0.21601 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 34.d. | Lightning arrestor damage or failure- Distribution | Yes | 2 | 0 | 2 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 0.32938 | 0.35075 | 0.27801 | 0.22344 | 0.32936 | 0.35075 | 0.27805 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 34.e. | Switch damage or failure- Distribution | Yes | 0 | 0 | 0 | 1 | 2 | 1 | 1 | 1 | 2 | 1 | 1.5253 | 1.5984 | 1.6154 | 1.3945 | 1.5245 | 1.5973 | 1.6157 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 34.f. | Pole damage or failure - Distribution | Yes | 1 | 2 | 1 | 0 | 1 | 0 | 1 | 0 | 2 | 0 | 0.31926 | 0.33685 | 0.27075 | 0.22403 | 0.31763 | 0.33532 | 0.27055 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 34.g. | Insulator and brushing damage or failure - Distribution | Yes | 1 | 2 | 2 | 1 | 2 | 3 | 1 | 2 | 1 | 0 | 1.0706 | 1.0866 | 0.96935 | 0.90066 | 1.0435 | 1.0569 | 0.9607 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 34.h. | Crossarm damage or failure - Distribution | Yes | 1 | 2 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0.15975 | 0.16427 | 0.11654 | 0.047437 | 0.15544 | 0.15972 | 0.11455 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 34.i. | Voltage regulator / booster damage or failure - Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 34.j. | Recloser damage or failure - Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 34.k. | Anchor / guy damage or failure - Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 34.l. | Sectionalizer damage or failure - Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 34.m. | Connection device damage or failure - Distribution | Yes | 4 | 4 | 3 | 1 | 7 | 0 | 0 | 2 | 1 | 0.65681 | 1.0175 | 1.1049 | 0.81493 | 0.65681 | 1.0175 | 1.1049 | 0.81493 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 34.n. | Transformer damage or failure - Distribution | Yes | 3 | 2 | 2 | 10 | 3 | 1 | 3 | 3 | 3 | 0 | 1.7962 | 1.8535 | 1.607 | 1.7456 | 1.773 | 1.8324 | 1.593 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 34.o. | Other - Distribution | Yes | 6 | 7 | 1 | 7 | 2 | 0 | 2 | 2 | 0 | 2 | 1.0847 | 1.1482 | 1.2444 | 0.91791 | 1.0585 | 1.1305 | 1.2354 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 35. Wire-to-wire contact - Distribution | 35.a. | Wire-to-wire contact / contamination- Distribution | Yes | 1 | 1 | 3 | 3 | 8 | 0 | 2 | 2 | 1 | 3 | 1.188 | 1.2537 | 0.77925 | 0.48115 | 1.1492 | 1.2107 | 0.74911 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 36. Contamination - Distribution | 36.a. | Contamination - Distribution | Yes | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0.17035 | 0.17702 | 0.14868 | 0.11641 | 0.17033 | 0.17701 | 0.1487 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 37. Utility work / Operation | 37.a. | Utility work / Operation | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 38. Vandalism / Theft - Distribution | 38.a. | Vandalism / Theft - Distribution | Yes | 3 | 0 | 0 | 1 | 6 | 2 | 1 | 2 | 1 | 1 | 1.2723 | 1.1273 | 0.76177 | 0.73439 | 1.2718 | 1.1269 | 0.76159 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 39. Other- Distribution | 39.a. | All Other- Distribution | Yes | 4 | 0 | 1 | 0 | 4 | 1 | 3 | 1 | 2 | 2 | 0.92169 | 0.37473 | 0.35283 | 0.53958 | 0.92169 | 0.37473 | 0.35283 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 40. Unknown- Distribution | 40.a. | Unknown - Distribution | Yes | 21 | 5 | 12 | 6 | 1 | 0 | 2 | 0 | 1 | 1 | 2.4913 | 2.8132 | 1.5945 | 1.1076 | 2.4913 | 2.8132 | 1.5945 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
Ignition - Transmission | 41. Contact from object - Transmission | 41.a. | Veg. contact- Transmission | Yes | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.029832 | 0.016758 | 0.0044676 | 0 | 0.028042 | 0.015997 | 0.0043823 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 41.b. | Animal contact- Transmission | Yes | 3 | 2 | 3 | 0 | 2 | 1 | 1 | 1 | 0 | 0 | 0.6615 | 0.51666 | 0.39277 | 0.41045 | 0.59697 | 0.47337 | 0.37388 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 41.c. | Balloon contact- Transmission | Yes | 1 | 1 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.2745 | 0.24541 | 0.21767 | 0.172 | 0.2745 | 0.24541 | 0.21767 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 41.d. | Vehicle contact- Transmission | Yes | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14393 | 0.074151 | 0.06782 | 0.050487 | 0.14393 | 0.074151 | 0.06782 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 41.e. | Other contact from object - Transmission | Yes | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.11156 | 0.092766 | 0.073236 | 0.026121 | 0.11156 | 0.092766 | 0.073236 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 42. Equipment / facility failure - Transmission | 42.a. | Capacitor bank damage or failure- Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034361 | 0.038408 | 0.032496 | 0.010465 | 0.034361 | 0.038408 | 0.032496 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 42.b. | Conductor damage or failure — Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 42.c. | Fuse damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 42.d. | Lightning arrestor damage or failure- Transmission | Yes | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.016889 | 0.019027 | 0.015407 | 0.0026401 | 0.016889 | 0.019027 | 0.015407 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 42.e. | Switch damage or failure- Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 42.f. | Pole damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 42.g. | Insulator and brushing damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 42.h. | Crossarm damage or failure - Transmission | Yes | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016889 | 0.019027 | 0.015407 | 0.0026401 | 0.016889 | 0.019027 | 0.015407 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 42.i. | Voltage regulator / booster damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 42.j. | Recloser damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 42.k. | Anchor / guy damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 42.l. | Sectionalizer damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 42.m. | Connection device damage or failure - Transmission | Yes | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0.0026401 | 0.016889 | 0.019027 | 0.015407 | 0.0026401 | 0.016889 | 0.019027 | 0.015407 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 42.n. | Transformer damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 42.o. | Other - Transmission | Yes | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0029519 | 0.0050941 | 0.0014688 | 0 | 0.0029519 | 0.0050941 | 0.0014688 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 43. Wire-to-wire contact - Transmission | 43.a. | Wire-to-wire contact / contamination- Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 44. Contamination - Transmission | 44.a. | Contamination - Transmission | Yes | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.0025247 | 0.0040373 | 0.0010493 | 0 | 0.0021319 | 0.0035104 | 0.00096766 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 45. Utility work / Operation | 45.a. | Utility work / Operation | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 46. Vandalism / Theft - Transmission | 46.a. | Vandalism / Theft - Transmission | Yes | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0029519 | 0.0050941 | 0.0014688 | 0 | 0.0029519 | 0.0050941 | 0.0014688 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 47. Other- Transmission | 47.a. | All Other- Transmission | Yes | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0.031314 | 0.034111 | 0.026489 | 0.0046547 | 0.029128 | 0.032196 | 0.025609 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 48. Unknown- Transmission | 48.a. | Unknown - Transmission | Yes | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16254 | 0.17137 | 0.15761 | 0.094688 | 0.16254 | 0.17137 | 0.15761 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.

## Table 7.2
Utility | Southern California Edison Company | Notes:
Table No. | 7.2 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.
Date Modified | 2021-05-03 | Data from 2015 - 2019 should be actual numbers. 2020 - 2023 should be projected. In future submissions update projected numbers with actuals
[5 empty] | Number of ignitions by HFTD tier | [29 empty] | Projected ignitions by HFTD tier
Table 7.2: Key recent and projected drivers of ignitions by HFTD region |  |  |  |  | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-CPUC HFTD | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-CPUC HFTD | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-CPUC HFTD | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-CPUC HFTD | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-CPUC HFTD | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-CPUC HFTD | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-CPUC HFTD | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-CPUC HFTD
| Metric type | # | Ignition driver | Are ignitions tracked for ignition driver? (yes / no) | 2015 | 2015 | 2015 | 2015 | 2015 | 2016 | 2016 | 2016 | 2016 | 2016 | 2017 | 2017 | 2017 | 2017 | 2017 | 2018 | 2018 | 2018 | 2018 | 2018 | 2019 | 2019 | 2019 | 2019 | 2019 | 2020 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
Ignition - Distribution | 1. Contact from object - Distribution | 1.a. | Veg. contact- Distribution | Yes | 7 | 0 | 2 | 4 | 0 | 7 | 0 | 1 | 4 | 0 | 10 | 0 | 1 | 5 | 0 | 10 | 0 | 4 | 1 | 0 | 10 | 0 | 1 | 1 | 1 | 8 | 0 | 2 | 1 | 0 | 8.8409 | 0.027284 | 1.3154 | 0.41758 | 0 | 8.8409 | 0.019667 | 0.89293 | 0.20524 | 0 | # ignitions | Note that due to certain enhancements made to determining cause sub-categories of events, figures in this table may not tie exactly to those provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 1.b. | Animal contact- Distribution | Yes | 2 | 0 | 1 | 6 | 0 | 4 | 0 | 2 | 2 | 0 | 3 | 0 | 1 | 2 | 0 | 8 | 0 | 3 | 1 | 0 | 14 | 0 | 2 | 2 | 0 | 15 | 0 | 2 | 5 | 0 | 16.4166 | 0 | 1.5062 | 1.9158 | 0 | 16.4166 | 0 | 1.3232 | 1.5703 | 0 | # ignitions | Note that due to certain enhancements made to determining cause sub-categories of events, figures in this table may not tie exactly to those provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 1.c. | Balloon contact- Distribution | Yes | 10 | 0 | 0 | 2 | 0 | 7 | 0 | 0 | 3 | 0 | 11 | 0 | 3 | 4 | 0 | 24 | 0 | 1 | 5 | 0 | 10 | 0 | 2 | 3 | 0 | 10 | 0 | 2 | 5 | 0 | 13.9775 | 0 | 1.3202 | 3.6524 | 0 | 13.9775 | 0 | 1.1941 | 3.138 | 0 | # ignitions | Note that due to certain enhancements made to determining cause sub-categories of events, figures in this table may not tie exactly to those provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 1.d. | Vehicle contact- Distribution | Yes | 7 | 0 | 0 | 4 | 0 | 4 | 0 | 0 | 2 | 0 | 4 | 0 | 1 | 1 | 0 | 4 | 0 | 3 | 5 | 1 | 8 | 0 | 2 | 0 | 0 | 3 | 0 | 1 | 2 | 0 | 5.0779 | 0.027682 | 1.2683 | 3.1296 | 0 | 5.0779 | 0.027447 | 1.1973 | 2.8784 | 0 | # ignitions | Note that due to certain enhancements made to determining cause sub-categories of events, figures in this table may not tie exactly to those provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 1.e. | Other contact from object - Distribution | Yes | 1 | 0 | 1 | 1 | 0 | 3 | 0 | 1 | 2 | 0 | 3 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 2 | 0 | 4 | 0 | 1 | 0 | 0 | 3.1361 | 0.03083 | 0.52952 | 0.0598 | 0 | 3.1361 | 0.030476 | 0.49504 | 0.053657 | 0 | # ignitions | Note that due to certain enhancements made to determining cause sub-categories of events, figures in this table may not tie exactly to those provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 2. Equipment / facility failure - Distribution | 2.a. | Capacitor bank damage or failure- Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16535 | 0 | 0 | 0.041865 | 0 | 0.16535 | 0 | 0 | 0.03193 | 0 | # ignitions | Note that due to certain enhancements made to determining cause sub-categories of events, figures in this table may not tie exactly to those provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 2.b. | Conductor damage or failure — Distribution | Yes | 1 | 0 | 1 | 0 | 0 | 14 | 0 | 2 | 3 | 0 | 14 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 3 | 0 | 6 | 0 | 2 | 3 | 0 | 11 | 0 | 2 | 12 | 0 | 4.179 | 0 | 1.1186 | 14.2368 | 0 | 4.179 | 0 | 1.0182 | 12.0729 | 0 | # ignitions | Note that due to certain enhancements made to determining cause sub-categories of events, figures in this table may not tie exactly to those provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 2.c. | Fuse damage or failure - Distribution | Yes | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.91564 | 0 | 0 | 0.013508 | 0 | 0.91564 | 0 | 0 | 0.012209 | 0 | # ignitions | Note that due to certain enhancements made to determining cause sub-categories of events, figures in this table may not tie exactly to those provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 2.d. | Lightning arrestor damage or failure- Distribution | Yes | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 1.1816 | 0 | 0 | 0 | 0 | 1.1816 | 0 | 0 | 0 | 0 | # ignitions | Note that due to certain enhancements made to determining cause sub-categories of events, figures in this table may not tie exactly to those provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 2.e. | Switch damage or failure- Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 6.1352 | 0 | 0 | 0 | 0 | 6.132 | 0 | 0 | 0 | 0 | # ignitions | Note that due to certain enhancements made to determining cause sub-categories of events, figures in this table may not tie exactly to those provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 2.f. | Pole damage or failure - Distribution | Yes | 1 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 1 | 0 | 0 | 1.1116 | 0 | 0.020004 | 0.019268 | 0 | 1.1116 | 0 | 0.018445 | 0.017477 | 0 | # ignitions | Note that due to certain enhancements made to determining cause sub-categories of events, figures in this table may not tie exactly to those provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 2.g. | Insulator and brushing damage or failure - Distribution | Yes | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 5 | 0 | 1 | 1 | 0 | 3.7981 | 0 | 0.12708 | 0.10245 | 0 | 3.7981 | 0 | 0.098673 | 0.065024 | 0 | # ignitions | Note that due to certain enhancements made to determining cause sub-categories of events, figures in this table may not tie exactly to those provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 2.h. | Crossarm damage or failure - Distribution | Yes | 1 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45192 | 0 | 0 | 0.03647 | 0 | 0.45191 | 0 | 0 | 0.025238 | 0 | # ignitions | Note that due to certain enhancements made to determining cause sub-categories of events, figures in this table may not tie exactly to those provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 2.i. | Voltage regulator / booster damage or failure - Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Note that due to certain enhancements made to determining cause sub-categories of events, figures in this table may not tie exactly to those provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 2.j. | Recloser damage or failure - Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Note that due to certain enhancements made to determining cause sub-categories of events, figures in this table may not tie exactly to those provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 2.k. | Anchor / guy damage or failure - Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Note that due to certain enhancements made to determining cause sub-categories of events, figures in this table may not tie exactly to those provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 2.l. | Sectionalizer damage or failure - Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Note that due to certain enhancements made to determining cause sub-categories of events, figures in this table may not tie exactly to those provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 2.m. | Connection device damage or failure - Distribution | Yes | 1 | 0 | 1 | 2 | 0 | 1 | 0 | 2 | 1 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 4 | 0 | 0 | 2 | 1 | 3 | 0 | 0 | 0 | 0 | 2.2249 | 0 | 0.11553 | 1.2317 | 0.022103 | 2.2249 | 0 | 0.11553 | 1.2317 | 0.022103 | # ignitions | Note that due to certain enhancements made to determining cause sub-categories of events, figures in this table may not tie exactly to those provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 2.n. | Transformer damage or failure - Distribution | Yes | 2 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | 0 | 0 | 2 | 0 | 2 | 0 | 0 | 1 | 0 | 8 | 0 | 1 | 1 | 0 | 6.5743 | 0 | 0 | 0.45213 | 0 | 6.5743 | 0 | 0 | 0.36979 | 0 | # ignitions | Note that due to certain enhancements made to determining cause sub-categories of events, figures in this table may not tie exactly to those provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 2.o. | Other - Distribution | Yes | 4 | 0 | 0 | 2 | 0 | 4 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 1 | 0 | 6 | 0 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | 3.2291 | 0 | 0.012295 | 1.1811 | 0 | 3.2291 | 0 | 0.011588 | 1.1016 | 0 | # ignitions | Note that due to certain enhancements made to determining cause sub-categories of events, figures in this table may not tie exactly to those provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 3. Wire-to-wire contact - Distribution | 3.a. | Wire-to-wire contact / contamination- Distribution | Yes | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 1 | 0 | 2 | 0 | 0 | 6 | 0 | 1 | 1 | 0 | 4 | 0 | 0 | 1 | 0 | 3.0029 | 0 | 0.099217 | 0.62008 | 0 | 3.0029 | 0 | 0.089104 | 0.49808 | 0 | # ignitions | Note that due to certain enhancements made to determining cause sub-categories of events, figures in this table may not tie exactly to those provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 4. Contamination - Distribution | 4.a. | Contamination - Distribution | Yes | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58028 | 0 | 0.0322 | 0 | 0 | 0.58028 | 0 | 0.032172 | 0 | 0 | # ignitions | Note that due to certain enhancements made to determining cause sub-categories of events, figures in this table may not tie exactly to those provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 5. Utility work / Operation | 5.a. | Utility work / Operation | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Note that due to certain enhancements made to determining cause sub-categories of events, figures in this table may not tie exactly to those provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 6. Vandalism / Theft - Distribution | 6.a. | Vandalism / Theft - Distribution | Yes | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 4 | 0 | 1 | 1 | 0 | 4 | 0 | 0 | 2 | 0 | 1.1234 | 0 | 0 | 2.7726 | 0 | 1.1234 | 0 | 0 | 2.7712 | 0 | # ignitions | Note that due to certain enhancements made to determining cause sub-categories of events, figures in this table may not tie exactly to those provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 7. Other- Distribution | 7.a. | All Other- Distribution | Yes | 2 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 1 | 0 | 6 | 0 | 0 | 1 | 0 | 1.3018 | 0 | 0.4435 | 0.4435 | 0 | 1.3018 | 0 | 0.4435 | 0.4435 | 0 | # ignitions | Note that due to certain enhancements made to determining cause sub-categories of events, figures in this table may not tie exactly to those provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 8. Unknown- Distribution | 8.a. | Unknown - Distribution | Yes | 14 | 0 | 1 | 6 | 0 | 3 | 0 | 0 | 2 | 0 | 7 | 0 | 1 | 3 | 1 | 5 |  | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 3 | 0 | 0 | 0 | 0 | 7.6001 | 0.040151 | 0.11929 | 0.24705 | 0 | 7.6001 | 0.040151 | 0.11929 | 0.24705 | 0 | # ignitions | Note that due to certain enhancements made to determining cause sub-categories of events, figures in this table may not tie exactly to those provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
Ignition - Transmission | 9. Contact from object - Transmission | 9.a. | Veg. contact- Transmission | Yes | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028026 | 0 | 0 | 0.023032 | 0 | 0.028026 | 0 | 0 | 0.020396 | 0 | # ignitions | Note that due to certain enhancements made to determining cause sub-categories of events, figures in this table may not tie exactly to those provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 9.b. | Animal contact- Transmission | Yes | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0.36746 | 0 | 0.22921 | 1.4377 | 0 | 0.36746 | 0 | 0.2045 | 1.2827 | 0 | # ignitions | Note that due to certain enhancements made to determining cause sub-categories of events, figures in this table may not tie exactly to those provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 9.c. | Balloon contact- Transmission | Yes | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.69726 | 0 | 0.14489 | 0.067433 | 0 | 0.69726 | 0 | 0.14489 | 0.067433 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 9.d. | Vehicle contact- Transmission | Yes | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33639 | 0 | 0 | 0 | 0 | 0.33639 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 9.e. | Other contact from object - Transmission | Yes | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.10123 | 0 | 0.10123 | 0.10123 | 0 | 0.10123 | 0 | 0.10123 | 0.10123 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 10. Equipment / facility failure - Transmission | 10.a. | Capacitor bank damage or failure- Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11573 | 0 | 0 | 0 | 0 | 0.11573 | 0 | 0 | 0 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 10.b. | Conductor damage or failure — Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 10.c. | Fuse damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 10.d. | Lightning arrestor damage or failure- Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.053963 | 0 | 0 | 0 | 0 | 0.053963 | 0 | 0 | 0 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 10.e. | Switch damage or failure- Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 10.f. | Pole damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 10.g. | Insulator and brushing damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 10.h. | Crossarm damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.053963 | 0 | 0 | 0 | 0 | 0.053963 | 0 | 0 | 0 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 10.i. | Voltage regulator / booster damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 10.j. | Recloser damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 10.k. | Anchor / guy damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 10.l. | Sectionalizer damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 10.m. | Connection device damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.053963 | 0 | 0 | 0 | 0 | 0.053963 | 0 | 0 | 0 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 10.n. | Transformer damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
|  | 10.o. | Other - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0095148 | 0 | 0 | 0 | 0 | 0.0095148 | 0 | 0 | 0 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 11. Wire-to-wire contact - Transmission | 11.a. | Wire-to-wire contact / contamination- Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 12. Contamination - Transmission | 12.a. | Contamination - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0076113 | 0 | 0 | 0 | 0 | 0.0066099 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 13. Utility work / Operation | 13.a. | Utility work / Operation | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 14. Vandalism / Theft - Transmission | 14.a. | Vandalism / Theft - Transmission | Yes | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0095148 | 0 | 0 | 0 | 0 | 0.0095148 | 0 | 0 | 0 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 15. Other- Transmission | 15.a. | All Other- Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.053962 | 0 | 0 | 0.043016 | 0 | 0.053962 | 0 | 0 | 0.037626 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.
| 16. Unknown- Transmission | 16.a. | Unknown - Transmission | Yes | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23902 | 0.10817 | 0.23902 | 0 | 0 | 0.23902 | 0.10817 | 0.23902 | 0 | 0 | # ignitions | Note that SCE enhanced its mapping of outage data to faults; this may have shifted numbers in this table compared to the numbers provided in SCE's Remedial Compliance Plan SCE-2 - Determining Cause of Near Misses.

## Table 8
Utility | Southern California Edison Company
Table No. | 8
Date Modified | 2021-05-03
Note: These columns are placeholders for future QR submissions.
Table 8: State of service territory and utility equipment |  |  | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3
Metric type | # | Outcome metric name | 2015 | 2015 | 2015 | 2015 | 2016 | 2016 | 2016 | 2016 | 2017 | 2017 | 2017 | 2017 | 2018 | 2018 | 2018 | 2018 | 2019 | 2019 | 2019 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
1. State of service territory and equipment in urban areas | 1.a. | Circuit miles (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 17159.88 | 0.85 | 1126.19 | 1452.86 | 17052.6827 | 0.85 | 1035.1765 | 1428.4968 | [8 empty] | Circuit miles | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 1.b. | Circuit miles in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 3446.19 | 0.48 | 749.7 | 1363.52 | 3482.0979 | 0.48 | 674.3718 | 1339.4887 | [8 empty] | Circuit miles in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 1.c. | Number of critical facilities (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 36757 | 6 | 2550 | 3923 | 36911 | 6 | 2207 | 3917 | [8 empty] | Number of critical facilities | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. Furthermore, 2019 data included some locations outside of SCE’s service territory within California, whereas 2020 data solely includes critical facilities within SCE’s service territory within California. SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 1.d. | Number of critical facilities in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 7305 | 5 | 1676 | 3489 | 7502 | 5 | 1417 | 3489 | [8 empty] | Number of critical facilities in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. Furthermore, 2019 data included some locations outside of SCE’s service territory within California, whereas 2020 data solely includes critical facilities within SCE’s service territory within California. SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 1.e. | Number of customers (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 3790432 | 545 | 209126 | 323745 | 3790432 | 545 | 209126 | 323745 | [8 empty] | Number of customers | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 1.f. | Number of customers in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 778819 | 525 | 149646 | 294005 | 778819 | 525 | 149646 | 294005 | [8 empty] | Number of customers in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 1.g. | Number of customers belonging to access and functional needs populations (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 1032899 | 32 | 30783 | 44840 | 1032899 | 32 | 30783 | 44840 | [8 empty] | Number of customers belonging to access and functional needs populations | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 1.h. | Number of customers belonging to access and functional needs populations in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 206260 | 21 | 23970 | 41362 | 206260 | 21 | 23970 | 41362 | [8 empty] | Number of customers belonging to access and functional needs populations in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 1.i. | Circuit miles of overhead transmission lines (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 1953.85 | 0.08 | 217.92 | 223.98 | 1937.0513 | 0.08 | 203.8292 | 215.4523 | [8 empty] | Circuit miles of overhead transmission lines | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 1.j. | Circuit miles of overhead transmission lines in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 293.15 | 0 | 130.59 | 182.31 | 300.6119 | 0 | 120.9586 | 173.5481 | [8 empty] | Circuit miles of overhead transmission lines in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 1.k. | Circuit miles of overhead distribution lines (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 15206.04 | 0.77 | 908.27 | 1228.89 | 15115.6314 | 0.77 | 831.3473 | 1213.0444 | [8 empty] | Circuit miles of overhead distribution lines | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 1.l. | Circuit miles of overhead distribution lines in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 3153.05 | 0.48 | 619.12 | 1181.22 | 3181.4859 | 0.48 | 553.4132 | 1165.9407 | [8 empty] | Circuit miles of overhead distribution lines in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 1.m. | Number of substations (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 231 | 0 | 23 | 17 | 230 | 0 | 12 | 13 | [8 empty] | Number of substations | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. Furthermore, 2019 data included all substations, including those outside of California, whereas 2020 data solely includes substations within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 1.n | Number of substations in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 47 | 0 | 16 | 16 | 43 | 0 | 6 | 12 | [8 empty] | Number of substations in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. Furthermore, 2019 data included all substations, including those outside of California, whereas 2020 data solely includes substations within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
, | 1.o. | Number of weather stations (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 35 | 0 | 18 | 32 | 51 | 0 | 107 | 94 | [8 empty] | Number of weather stations | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 1.p. | Number of weather stations in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 20 | 0 | 11 | 31 | 29 | 0 | 63 | 89 | [8 empty] | Number of weather stations in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
2. State of service territory and equipment in rural areas | 2.a. | Circuit miles (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 8536.18 | 0.46 | 2127.05 | 3723.5 | 8543.3122 | 0.47 | 2011.53 | 3676.3 | [8 empty] | Circuit miles | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 2.b. | Circuit miles in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 3262.55 | 0.04 | 1491.89 | 2729.02 | 3306.7952 | 0.05 | 1407.8787 | 2695.1743 | [8 empty] | Circuit miles in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 2.c. | Number of critical facilities (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 7692 | 0 | 1456 | 2894 | 7744 | 0 | 1338 | 2890 | [8 empty] | Number of critical facilities | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. Furthermore, 2019 data included some locations outside of SCE’s service territory within California, whereas 2020 data solely includes critical facilities within SCE’s service territory within California. SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 2.d. | Number of critical facilities in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 2397 | 0 | 1036 | 2348 | 2460 | 0 | 940 | 2343 | [8 empty] | Number of critical facilities in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. Furthermore, 2019 data included some locations outside of SCE’s service territory within California, whereas 2020 data solely includes critical facilities within SCE’s service territory within California. SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 2.e. | Number of customers (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 225587 | 20 | 53624 | 92195 | 225587 | 20 | 53624 | 92195 | [8 empty] | Number of customers | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 2.f. | Number of customers in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 94950 | 16 | 44971 | 83235 | 94950 | 16 | 44971 | 83235 | [8 empty] | Number of customers in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 2.g. | Number of customers belonging to access and functional needs populations (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 37100 | 4 | 7741 | 9410 | 37100 | 4 | 7741 | 9410 | [8 empty] | Number of customers belonging to access and functional needs populations | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 2.h. | Number of customers belonging to access and functional needs populations in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 19384 | 1 | 6718 | 8676 | 19384 | 1 | 6718 | 8676 | [8 empty] | Number of customers belonging to access and functional needs populations in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 2.i. | Circuit miles of overhead transmission lines (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 1353.32 | 0.09 | 453.91 | 771.52 | 1348.1553 | 0.09 | 444.1284 | 756.8649 | [8 empty] | Circuit miles of overhead transmission lines | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 2.j. | Circuit miles of overhead transmission lines in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 333.8 | 0 | 283.81 | 419.23 | 336.3493 | 0 | 277.3478 | 410.3605 | [8 empty] | Circuit miles of overhead transmission lines in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 2.k. | Circuit miles of overhead distribution lines (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 7182.86 | 0.37 | 1673.14 | 2951.98 | 7195.1569 | 0.38 | 1567.4016 | 2919.435 | [8 empty] | Circuit miles of overhead distribution lines | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 2.l. | Circuit miles of overhead distribution lines in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 2928.75 | 0.04 | 1208.08 | 2309.79 | 2970.4459 | 0.05 | 1130.531 | 2284.8138 | [8 empty] | Circuit miles of overhead distribution lines in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 2.m. | Number of substations (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 125 | 0 | 18 | 32 | 112 | 0 | 13 | 29 | [8 empty] | Number of substations | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. Furthermore, 2019 data included all substations, including those outside of California, whereas 2020 data solely includes substations within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 2.n | Number of substations in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 25 | 0 | 10 | 26 | 21 | 0 | 6 | 24 | [8 empty] | Number of substations in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. Furthermore, 2019 data included all substations, including those outside of California, whereas 2020 data solely includes substations within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 2.o. | Number of weather stations (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 20 | 0 | 53 | 152 | 30 | 0 | 144 | 273 | [8 empty] | Number of weather stations | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 2.p. | Number of weather stations in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 9 | 0 | 39 | 119 | 14 | 0 | 105 | 216 | [8 empty] | Number of weather stations in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
3. State of service territory and equipment in highly rural areas | 3.a. | Circuit miles (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 12178.84 | 0.84 | 2757.67 | 2992.26 | 11688.2696 | 0.84 | 2645.3755 | 2916.0365 | [8 empty] | Circuit miles | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 3.b. | Circuit miles in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 93.66 | 0 | 34.64 | 43.6 | 94.0503 | 0 | 24.5049 | 44.4822 | [8 empty] | Circuit miles in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 3.c. | Number of critical facilities (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 21784 | 0 | 1767 | 2598 | 21728 | 0 | 1613 | 2560 | [8 empty] | Number of critical facilities | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. Furthermore, 2019 data included some locations outside of SCE’s service territory within California, whereas 2020 data solely includes critical facilities within SCE’s service territory within California. SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 3.d. | Number of critical facilities in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 98 | 0 | 22 | 32 | 99 | 0 | 18 | 29 | [8 empty] | Number of critical facilities in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. Furthermore, 2019 data included some locations outside of SCE’s service territory within California, whereas 2020 data solely includes critical facilities within SCE’s service territory within California. SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 3.e. | Number of customers (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 379812 | 8 | 24861 | 37774 | 379812 | 8 | 24861 | 37774 | [8 empty] | Number of customers | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 3.f. | Number of customers in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 2566 | 0 | 968 | 1578 | 2566 | 0 | 968 | 1578 | [8 empty] | Number of customers in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 3.g. | Number of customers belonging to access and functional needs populations (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 44535 | 0 | 2492 | 2674 | 44535 | 0 | 2492 | 2674 | [8 empty] | Number of customers belonging to access and functional needs populations | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 3.h. | Number of customers belonging to access and functional needs populations in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 342 | 0 | 54 | 100 | 342 | 0 | 54 | 100 | [8 empty] | Number of customers belonging to access and functional needs populations in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 3.i. | Circuit miles of overhead transmission lines (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 5161.27 | 0.02 | 1285.5 | 1399.53 | 4764.2274 | 0.03 | 1255.9612 | 1371.7135 | [8 empty] | Circuit miles of overhead transmission lines | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 3.j. | Circuit miles of overhead transmission lines in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 7.75 | 0 | 3.18 | 2.97 | 7.9707 | 0 | 3.3432 | 5.4962 | [8 empty] | Circuit miles of overhead transmission lines in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 3.k. | Circuit miles of overhead distribution lines (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 7017.57 | 0.81 | 1472.17 | 1592.74 | 6924.0422 | 0.81 | 1389.4144 | 1544.323 | [8 empty] | Circuit miles of overhead distribution lines | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 3.l. | Circuit miles of overhead distribution lines in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 85.92 | 0 | 31.46 | 40.63 | 86.0796 | 0 | 21.1617 | 38.9861 | [8 empty] | Circuit miles of overhead distribution lines in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. Furthermore, 2019 data included all circuit miles, including those outside of California, whereas 2020 data solely includes circuit miles within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 3.m. | Number of substations (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 420 | 0 | 62 | 49 | 322 | 0 | 49 | 40 | [8 empty] | Number of substations | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. Furthermore, 2019 data included all substations, including those outside of California, whereas 2020 data solely includes substations within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 3.n | Number of substations in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | [8 empty] | Number of substations in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. Furthermore, 2019 data included all substations, including those outside of California, whereas 2020 data solely includes substations within the state of California for assets SCE maintains (which does include some assets outside of SCE’s service territory). SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 3.o. | Number of weather stations (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 36 | 0 | 90 | 137 | 47 | 0 | 348 | 465 | [8 empty] | Number of weather stations | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.
| 3.p. | Number of weather stations in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | 3 | 0 | 0 | 0 | 10 | 4 | [8 empty] | Number of weather stations in WUI | GIS models are updated frequently to reflect changes within SCE's service area and for data clean-up. SCE does not have the ability to analyze and calculate information in previous years. As such, only 2020 information was obtained from GIS. 2015-2018 data is not available and 2019 data is the same as what was provided in SCE’s 2020 WMP filing. The 2019 transmission data was replicated for 2020 because SCE discovered data discrepancies completing the GIS Data Schema requirements. SCE is still conducting quality control review of all the data and will correct any errors once its review is complete.

## Table 9
Utility | Southern California Edison Company | Notes:
Table No. | 9 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV. Report net additions using positive numbers and net removals and undergrounding using negative numbers for circuit miles and numbers of substations. Only report changes expected within the target year.
Date Modified | 2021-02-05 | For example, if 20 net overhead circuit miles are planned for addition by 2023, with 15 being added by 2022 and 5 more added by 2023, then report “15” for 2022 and “5” for 2023. Do not report cumulative change across years. In this case, do not report “20” for 2023, but instead the number planned to be added for just that year, which is “5”.
|  |  | Actual |  |  |  | Projected
Table 9: Location of actual and planned utility equipment additions or removal year over year |  |  | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3
Metric type | # | Outcome metric name | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
1. Planned utility equipment net addition (or removal) year over year - in urban areas | 1.a. | Circuit miles of overhead transmission lines (including WUI and non-WUI) | 3.97 | 0 | 1.54 | 1.52 | 7.3 | 0 | 2.47 | 1.03 | 10.49 | 0 | 0 | 0 | Circuit miles | SCE does not routinely track planned additions, removals, or upgrades by circuit mile, population density, or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map all projects in GIS and subdivide as requested.
| 1.b. | Circuit miles of overhead distribution lines (including WUI and non-WUI) | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Circuit miles | SCE does not routinely track planned additions, removals, or upgrades by circuit mile, population density, or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map the distribution projects in GIS and subdivide as requested.
| 1.c. | Circuit miles of overhead transmission lines in WUI | 0.12 | 0 | 1.54 | 1.13 | 0.67 | 0 | 2.47 | 1.03 | 0.6 | 0 | 0 | 0 | Circuit miles in WUI | SCE does not routinely track planned additions, removals, or upgrades by circuit mile, population density, or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map all projects in GIS and subdivide as requested.
| 1.d. | Circuit miles of overhead distribution lines in WUI | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Circuit miles in WUI | SCE does not routinely track planned additions, removals, or upgrades by circuit mile, population density, or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map the distribution projects in GIS and subdivide as requested.
| 1.e. | Number of substations (including WUI and non-WUI) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of substations | SCE does not routinely track planned additions, removals, or upgrades by circuit mile, population density, or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map all projects in GIS and subdivide as requested.
| 1.f. | Number of substations in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of substations in WUI | SCE does not routinely track planned additions, removals, or upgrades by circuit mile, population density, or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map all projects in GIS and subdivide as requested.
| 1.g. | Number of weather stations (including WUI and non-WUI) | 16 | 0 | 89 | 62 | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Number of weather stations | SCE does not routinely track planned additions, removals, or upgrades by circuit mile, population density, or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map all projects in GIS and subdivide as requested.
| 1.h. | Number of weather stations in WUI | 9 | 0 | 52 | 58 | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Number of weather stations in WUI | SCE does not routinely track planned additions, removals, or upgrades by circuit mile, population density, or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map all projects in GIS and subdivide as requested.
2. Planned utility equipment net addition (or removal) year over year - in rural areas | 2.a. | Circuit miles of overhead transmission lines (including WUI and non-WUI) | 3.54 | 0 | 3.68 | 5.51 | 2.55 | 0 | 5.92 | 2.71 | 8.75 | 0 | 0 | 0 | Circuit miles | SCE does not routinely track planned additions, removals, or upgrades by circuit mile, population density, or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map all projects in GIS and subdivide as requested.
| 2.b. | Circuit miles of overhead distribution lines (including WUI and non-WUI) | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Circuit miles | SCE does not routinely track planned additions, removals, or upgrades by circuit mile, population density, or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map the distribution projects in GIS and subdivide as requested.
| 2.c. | Circuit miles of overhead transmission lines in WUI | 2.47 | 0 | 2.54 | 3.91 | 1.44 | 0 | 4.5 | 2.49 | 0 | 0 | 0 | 0 | Circuit miles in WUI | SCE does not routinely track planned additions, removals, or upgrades by circuit mile, population density, or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map all projects in GIS and subdivide as requested.
| 2.d. | Circuit miles of overhead distribution lines in WUI | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Circuit miles in WUI | SCE does not routinely track planned additions, removals, or upgrades by circuit mile, population density, or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map the distribution projects in GIS and subdivide as requested.
| 2.e. | Number of substations (including WUI and non-WUI) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of substations | SCE does not routinely track planned additions, removals, or upgrades by circuit mile, population density, or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map all projects in GIS and subdivide as requested.
| 2.f. | Number of substations in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of substations in WUI | SCE does not routinely track planned additions, removals, or upgrades by circuit mile, population density, or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map all projects in GIS and subdivide as requested.
| 2.g. | Number of weather stations (including WUI and non-WUI) | 10 | 0 | 91 | 121 | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Number of weather stations | SCE does not routinely track planned additions, removals, or upgrades by circuit mile, population density, or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map all projects in GIS and subdivide as requested.
| 2.h. | Number of weather stations in WUI | 5 | 0 | 66 | 97 | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Number of weather stations in WUI | SCE does not routinely track planned additions, removals, or upgrades by circuit mile, population density, or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map all projects in GIS and subdivide as requested.
3. Planned utility equipment net addition (or removal) year over year - in highly rural areas | 3.a. | Circuit miles of overhead transmission lines (including WUI and non-WUI) | 4.25 | 0 | 5.73 | 18.89 | 3.61 | 0 | 4.34 | 5.29 | 4.47 | 0 | 0 | 0 | Circuit miles | SCE does not routinely track planned additions, removals, or upgrades by circuit mile, population density, or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map all projects in GIS and subdivide as requested.
| 3.b. | Circuit miles of overhead distribution lines (including WUI and non-WUI) | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Circuit miles | SCE does not routinely track planned additions, removals, or upgrades by circuit mile, population density, or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map the distribution projects in GIS and subdivide as requested.
| 3.c. | Circuit miles of overhead transmission lines in WUI | 0 | 0 | 0 | 0.26 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Circuit miles in WUI | SCE does not routinely track planned additions, removals, or upgrades by circuit mile, population density, or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map all projects in GIS and subdivide as requested.
| 3.d. | Circuit miles of overhead distribution lines in WUI | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Circuit miles in WUI | SCE does not routinely track planned additions, removals, or upgrades by circuit mile, population density, or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map the distribution projects in GIS and subdivide as requested.
| 3.e. | Number of substations (including WUI and non-WUI) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of substations | SCE does not routinely track planned additions, removals, or upgrades by circuit mile, population density, or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map all projects in GIS and subdivide as requested.
| 3.f. | Number of substations in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of substations in WUI | SCE does not routinely track planned additions, removals, or upgrades by circuit mile, population density, or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map all projects in GIS and subdivide as requested.
| 3.g. | Number of weather stations (including WUI and non-WUI) | 11 | 0 | 91 | 102 | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Number of weather stations | SCE does not routinely track planned additions, removals, or upgrades by circuit mile, population density, or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map all projects in GIS and subdivide as requested.
| 3.h. | Number of weather stations in WUI | 0 | 0 | 2 | 2 | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Number of weather stations in WUI | SCE does not routinely track planned additions, removals, or upgrades by circuit mile, population density, or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map all projects in GIS and subdivide as requested.

## Table 10
Utility | Southern California Edison Company | Notes:
Table No. | 10 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.
Date Modified | 2021-02-05 | In future submissions update planned upgrade numbers with actuals
|  | In the comments column on the far-right, enter the relevant program target(s) associated | Actual |  |  |  | Projected
Table 10: Location of actual and planned utility infrastructure upgrades year over year |  |  | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3
Metric type | # | Outcome metric name | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
1. Planned utility infrastructure upgrades year over year - in urban areas | 1.a. | Circuit miles of overhead transmission lines planned for upgrades (including WUI and non-WUI) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Circuit miles
| 1.b. | Circuit miles of overhead distribution lines planned for upgrades (including WUI and non-WUI) | 4.71 | 0.03 | 16.43 | 46.17 | 32.25 | 0.02 | 63.91 | 252.59 | 35.2 | 0 | 73.49 | 149.41 | Circuit miles | SCE does not routinely track planned additions, removals, or upgrades by circuit mile, population density, or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map all projects in GIS and subdivide as requested.
| 1.c. | Circuit miles of overhead transmission lines planned for upgrades in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Circuit miles in WUI
| 1.d. | Circuit miles of overhead distribution lines planned for upgrades in WUI | 4.32 | 0.03 | 16.06 | 44.94 | 16.42 | 0.02 | 62.32 | 247.05 | 28.45 | 0 | 66.77 | 148.11 | Circuit miles in WUI | SCE does not routinely track planned additions, removals, or upgrades by circuit mile, population density, or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map all projects in GIS and subdivide as requested.
| 1.e. | Number of substations planned for upgrades (including WUI and non-WUI) | 1 | 0 | 6 | 1 | 4 | 0 | 1 | 2 | 5 | 0 | 0 | 2 | Number of substations | SCE does not routinely track planned additions, removals, or upgrades by circuit mile, population density, or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map all projects in GIS and subdivide as requested.
| 1.f. | Number of substations planned for upgrades in WUI | 1 | 0 | 4 | 1 | 1 | 0 | 1 | 2 | 2 | 0 | 0 | 2 | Number of substations in WUI | SCE does not routinely track planned additions, removals, or upgrades by circuit mile, population density, or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map all projects in GIS and subdivide as requested.
| 1.g. | Number of weather stations planned for upgrades (including WUI and non-WUI) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of weather stations
| 1.h. | Number of weather stations planned for upgrades in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of weather stations in WUI
2. Planned utility infrastructure upgrades year over year - in rural areas | 2.a. | Circuit miles of overhead transmission lines planned for upgrades (including WUI and non-WUI) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Circuit miles
| 2.b. | Circuit miles of overhead distribution lines planned for upgrades (including WUI and non-WUI) | 9.52 | 0 | 92.99 | 390.43 | 60.69 | 0 | 304.88 | 938.55 | 28.75 | 0 | 186.87 | 268.34 | Circuit miles | SCE does not routinely track planned additions, removals, or upgrades by circuit mile, population density, or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map all projects in GIS and subdivide as requested.
| 2.c. | Circuit miles of overhead transmission lines planned for upgrades in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Circuit miles in WUI
| 2.d. | Circuit miles of overhead distribution lines planned for upgrades in WUI | 7.36 | 0 | 58.52 | 296.18 | 47.94 | 0 | 247.84 | 763.86 | 19.87 | 0 | 132.5 | 202.15 | Circuit miles in WUI | SCE does not routinely track planned additions, removals, or upgrades by circuit mile, population density, or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map all projects in GIS and subdivide as requested.
| 2.e. | Number of substations planned for upgrades (including WUI and non-WUI) | 0 | 0 | 0 | 4 | 2 | 0 | 1 | 2 | 2 | 0 | 3 | 2 | Number of substations | SCE does not routinely track planned additions, removals, or upgrades by circuit mile, population density, or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map all projects in GIS and subdivide as requested.
| 2.f. | Number of substations planned for upgrades in WUI | 0 | 0 | 0 | 4 | 1 | 0 | 1 | 2 | 2 | 0 | 2 | 2 | Number of substations in WUI | SCE does not routinely track planned additions, removals, or upgrades by circuit mile, population density, or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map all projects in GIS and subdivide as requested.
| 2.g. | Number of weather stations planned for upgrades (including WUI and non-WUI) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of weather stations
| 2.h. | Number of weather stations planned for upgrades in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of weather stations in WUI
3. Planned utility infrastructure upgrades year over year - in highly rural areas | 3.a. | Circuit miles of overhead transmission lines planned for upgrades (including WUI and non-WUI) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Circuit miles
| 3.b. | Circuit miles of overhead distribution lines planned for upgrades (including WUI and non-WUI) | 2.98 | 0 | 121.22 | 88.83 | 30.93 | 0 | 109.61 | 381.79 | 19.21 | 0 | 108.52 | 149.68 | Circuit miles | SCE does not routinely track planned additions, removals, or upgrades by circuit mile, population density, or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map all projects in GIS and subdivide as requested.
| 3.c. | Circuit miles of overhead transmission lines planned for upgrades in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Circuit miles in WUI
| 3.d. | Circuit miles of overhead distribution lines planned for upgrades in WUI | 0.1 | 0 | 1.79 | 2.16 | 0.43 | 0 | 1.45 | 12.12 | 0.12 | 0 | 2.18 | 2.58 | Circuit miles in WUI | SCE does not routinely track planned additions, removals, or upgrades by circuit mile, population density, or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map all projects in GIS and subdivide as requested.
| 3.e. | Number of substations planned for upgrades (including WUI and non-WUI) | 5 | 0 | 1 | 3 | 1 | 0 | 2 | 2 | 8 | 0 | 8 | 5 | Number of substations | SCE does not routinely track planned additions, removals, or upgrades by circuit mile, population density, or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map all projects in GIS and subdivide as requested.
| 3.f. | Number of substations planned for upgrades in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of substations in WUI | SCE does not routinely track planned additions, removals, or upgrades by circuit mile, population density, or WUI. While SCE has a number of planned distribution projects over the next few years, they are not far enough along in the project lifecycle to have a complete list of affected structures (new or existing), circuit path/route geometries, and/or geospatial coordinates. Therefore, SCE is unable to map all projects in GIS and subdivide as requested.
| 3.g. | Number of weather stations planned for upgrades (including WUI and non-WUI) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of weather stations
| 3.h. | Number of weather stations planned for upgrades in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of weather stations in WUI

## Table 11
Utility | Southern California Edison Company | Notes:
Table No. | 11 | "PSPS" = Public Safety Power Shutoff
Date Modified | 2021-05-03 | In future submissions update planned upgrade numbers with actuals
|  |  | Actual | [9 empty] | Projected
Table 11: Recent use of PSPS and other PSPS metrics | [7 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Outcome metric name | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
1. Recent use of PSPS | 1.a. | Frequency of PSPS events (total) | 0 | 0 | 1 | 3 | 7 | 0 | 0 | 2 | 8 | 1 | 0 | Low 1 / High 3 | Low 3 / High 11 |  |  |  |  | Number of instances where utility operating protocol requires de-energization of a circuit or portion thereof to reduce ignition probability, per year. Only include events in which de-energization ultimately occurred | During 2020, SCE initiated 12 PSPS events (2 of which SCE did not de-energize, Table 11, Metric Type 5.a.) with 16 periods of concern, i.e., periods of time when de-energization was likely to occur due to forecast weather and fuel conditions, 16 relates to periods of concerns. For Q2-Q4 2021 time periods, SCE used 2020 recorded data adjusted for improvement expected based on SCE's planned wildfire mitigation activities to create a baseline. To factor in weather variability, which has significant impacts on PSPS events, SCE developed a range around the baseline. The range was based on an 18 year backcast analysis that analyzed how current PSPS triggers would have resulted in PSPS events when applied to historical weather data. For further details on calculating the range, please see section 8.5
| 1.b. | Scope of PSPS events (total) | 0 | 0 | 7 | 6 | 267 | 0 | 0 | 7 | 417 | 160 | 0 | Low 2 / High 7 | Low 147 / High 473 |  |  |  |  | Circuit-events, measured in number of events multiplied by number of circuits de-energized per year | SCE interprets this line item as de-energized circuit count. Additionally, the numbers being reported may not align with the ESRB-8 report because that report uses preliminary operations data that has not been fully validated. For Q2-Q4 2021 time periods, SCE used 2020 recorded data adjusted for improvement expected based on SCE's planned wildfire mitigation activities to create a baseline. To factor in weather variability, which has significant impacts on PSPS events, SCE developed a range around the baseline. The range was based on an 18 year backcast analysis that analyzed how current PSPS triggers would have resulted in PSPS events when applied to historical weather data. For further details on calculating the range, please see section 8.5
| 1.c. | Duration of PSPS events (total) | 0 | 0 | 87019 | 3570 | 5275193 | 0 | 0 | 3981 | 4451955 | 1953961.7833 | 0 | Low 1,129 / High 3,622 | Low 1,213,366 / High 3,893,102 |  |  |  |  | Customer hours per year | For Q2-Q4 2021 time periods, SCE used 2020 recorded data adjusted for improvement expected based on SCE's planned wildfire mitigation activities to create a baseline. To factor in weather variability, which has significant impacts on PSPS events, SCE developed a range around the baseline. The range was based on an 18 year backcast analysis that analyzed how current PSPS triggers would have resulted in PSPS events when applied to historical weather data. For further details on calculating the range, please see section 8.5
2. Customer hours of PSPS and other outages | 2.a. | Customer hours of planned outages including PSPS (total) | 0 | 11067181.7 | 10406441.7833 | 9556441.9167 | 10918480.1 | 1236490.8 | 770810.9833 | 1295679.4 | 6103854.7333 | 3778267.95 | 1729343 | 1830060 | 4539429 |  |  |  |  | Total customer hours of planned outages per year | SCE has not traditionally calculated reliability metrics tied to planned outages. Since 2019, SCE has been improving and refining its planned outage reliability reporting, therefore the years after 2018 reflect not only actual changes but changes due to the improved process. Further, SCE does not consider PSPS to be planned outages but has included PSPS metrics in this row as requested by WSD. Forecast is based on time-series forecast.
| 2.b. | Customer hours of unplanned outages, not including PSPS (total) | 8401612 | 9276813 | 7788697 | 6088158 | 7617913 | 1480964 | 1496752 | 2350456 | 2224812 | 1615913.3908 | 1496752 | 2350456 | 2224812 |  |  |  |  | Total customer hours of unplanned outages per year | Forecast is based on time-series forecast.
| 2.c. | System Average Interruption Duration Index (SAIDI) (including PSPS) | 100.1517 | 241.208 | 214.2783 | 183.0854 | 215.9119 | 31.4562 | 26.2485 | 42.2063 | 96.4095 | 63.0777 | 37.3397 | 48.3864 | 78.2912 |  |  |  |  | SAIDI index value = sum of all interruptions in time period where each interruption is defined as sum(duration of interruption * # of customer interruptions) / Total number of customers served | SCE has not traditionally calculated reliability metrics tied to planned outages. Since 2019, SCE has been improving and refining its planned outage reliability reporting, therefore the years after 2018 reflect not only actual changes but changes due to the improved process. Further, SCE does not consider PSPS to be planned outages but has included PSPS metrics in this row as requested by WSD. Forecast is based on time-series forecast.
| 2.d. | System Average Interruption Duration Index (SAIDI) (excluding PSPS) | 100.1517 | 241.208 | 213.2535 | 183.0436 | 154.4665 | 31.4562 | 26.2484 | 42.1602 | 44.8753 | 39.7594 | 34.17 | 46.75 | 41.68 |  |  |  |  | SAIDI index value = sum of all interruptions in time period where each interruption is defined as sum(duration of interruption * # of customer interruptions) / Total number of customers served | SCE has not traditionally calculated reliability metrics tied to planned outages. Since 2019, SCE has been improving and refining its planned outage reliability reporting, therefore the years after 2018 reflect not only actual changes but changes due to the improved process. Forecast is based on time-series forecast.
| 2.e. | System Average Interruption Frequency Index (SAIFI) (including PSPS) | 1.1639 | 1.3346 | 1.2033 | 1.029 | 1.1054 | 0.22238 | 0.21626 | 0.28152 | 0.32123 | 0.29281 | 0.277 | 0.31 | 0.279 |  |  |  |  | SAIFI index value = sum of all interruptions in time period where each interruption is defined as (total # of customer interruptions) / (total # of customers served) | SCE has not traditionally calculated reliability metrics tied to planned outages. Since 2019, SCE has been improving and refining its planned outage reliability reporting, therefore the years after 2018 reflect not only actual changes but changes due to the improved process. Further, SCE does not consider PSPS to be planned outages but has included PSPS metrics in this row as requested by WSD. Forecast is based on time-series forecast.
| 2.f. | System Average Interruption Frequency Index (SAIFI) (excluding PSPS) | 1.1639 | 1.3346 | 1.2027 | 1.029 | 1.0668 | 0.22238 | 0.21626 | 0.28147 | 0.27915 | 0.26995 | 0.277 | 0.309 | 0.278 |  |  |  |  | SAIFI index value = sum of all interruptions in time period where each interruption is defined as (total # of customer interruptions) / (total # of customers served) | Forecast is based on time-series forecast.
3. Critical infrastructure impacted by PSPS | 3.a. | Critical infrastructure impacted by PSPS | 0 | 0 | NA | NA | 5868 | 0 | 0 | 12 | 5123 | 2066 | 0 | Low 1 / High 4 | Low 1,658 / High 5,320 |  |  |  |  | Number of critical infrastructure (in accordance with D.19-05-042) locations impacted per hour multiplied by hours offline per year | The numbers being reported may not align with the ESRB-8 report because that report uses preliminary operations data that has not been fully validated. SCE also notes, that earlier PSPS events were not tracked and recorded in the same level of detail as it is now, therefore not all data is available. For Q2-Q4 2021 time periods, SCE used 2020 recorded data adjusted for improvement expected based on SCE's planned wildfire mitigation activities to create a baseline. To factor in weather variability, which has significant impacts on PSPS events, SCE developed a range around the baseline. The range was based on an 18 year backcast analysis that analyzed how current PSPS triggers would have resulted in PSPS events when applied to historical weather data. For further details on calculating the range, please see section 8.5 Historical data was updated as a typing error was discovered.
4. Community outreach of PSPS metrics | 4.a. | # of customers impacted by PSPS | 0 | 0 | 2861 | 112 | 198826 | 0 | 0 | 270 | 229530 | 116349 | 0 | Low 58 / High 185 | Low 67,220 / High 215,678 |  |  |  |  | # of customers impacted by PSPS (if multiple PSPS events impact the same customer, count each event as a separate customer) | The numbers being reported may not align with the ESRB-8 report because that report uses preliminary operations data that has not been fully validated. For Q2-Q4 2021 time periods, SCE used 2020 recorded data adjusted for improvement expected based on SCE's planned wildfire mitigation activities to create a baseline. To factor in weather variability, which has significant impacts on PSPS events, SCE developed a range around the baseline. The range was based on an 18 year backcast analysis that analyzed how current PSPS triggers would have resulted in PSPS events when applied to historical weather data. For further details on calculating the range, please see section 8.5
| 4.b. | # of medical baseline customers impacted by PSPS | 0 | 0 | NA | NA | 4043 | 0 | 0 | 11 | 7725 | 3415 | 0 | Low 4 / High 12 | Low 2,443 / High 7,837 |  |  |  |  | # of customers impacted by PSPS (if multiple PSPS events impact the same customer, count each event as a separate customer) | The numbers being reported may not align with the ESRB-8 report because that report uses preliminary operations data that has not been fully validated. SCE also notes, that earlier PSPS events were not tracked and recorded in the same level of detail as it is now, therefore not all data is available. For Q2-Q4 2021 time periods, SCE used 2020 recorded data adjusted for improvement expected based on SCE's planned wildfire mitigation activities to create a baseline. To factor in weather variability, which has significant impacts on PSPS events, SCE developed a range around the baseline. The range was based on an 18 year backcast analysis that analyzed how current PSPS triggers would have resulted in PSPS events when applied to historical weather data. For further details on calculating the range, please see section 8.5
| 4.c. | # of customers notified prior to initiation of PSPS event | 0 | 0 | NA | NA | 155824 | 0 | 0 | 232 | 143908 | 110217 | 0 | Low 36 / High 116 | Low 41,960 / High 134,628 |  |  |  |  | # of customers notified of PSPS event prior to initiation (if multiple PSPS events impact the same customer, count each event in which customer was notified as a separate customer) | The numbers being reported may not align with the ESRB-8 report because that report uses preliminary operations data that has not been fully validated. SCE also notes, that earlier PSPS events were not tracked and recorded in the same level of detail as it is now, therefore not all data is available.
| 4.d. | # of medical baseline customers notified prior to initiation of PSPS event | 0 | 0 | NA | NA | 3044 | 0 | 0 | 15 | 7531 | 3138 | 0 | Low 4 / High 12 | Low ,296 / High 7,367 |  |  |  |  | # of customers notified of PSPS event prior to initiation (if multiple PSPS events impact the same customer, count each event in which customer was notified as a separate customer) | The numbers being reported may not align with the ESRB-8 report because that report uses preliminary operations data that has not been fully validated. SCE also notes, that earlier PSPS events were not tracked and recorded in the same level of detail as it is now, therefore not all data is available.
| 4.e. | % of customers notified prior to a PSPS event impacting them | 0 | 0 | NA | NA | 78% | 0 | 0 | 84.67% | 62.42% | 94.73% | 0 | 62% | 62% |  |  |  |  | =4.c. / 4.a. | SCE also notes, that earlier PSPS events were not tracked and recorded in the same level of detail as it is now, therefore not all data is available.
| 4.f. | % of medical baseline customers notified prior to a PSPS event impacting them | 0 | 0 | NA | NA | 75% | 0 | 0 | 100% | 88.26% | 91.89% | 0 | 100% | 94% |  |  |  |  | =4.d. / 4.b. | SCE also notes, that earlier PSPS events were not tracked and recorded in the same level of detail as it is now, therefore not all data is available.
5. Other PSPS metrics | 5.a. | Number of PSPS events triggered where no de-energization occurred | 0 | 0 | NA | NA | 7 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 0 |  |  |  |  | Number of instances where utility notified the public of a potential PSPS event but no de-energization followed | SCE also notes, that earlier PSPS events were not tracked and recorded in the same level of detail as it is now, therefore not all data is available.
| 5.b. | Number of customers located on de-energized circuit | 0 | 0 | NA | NA | 237666 | 0 | 0 | 5820 | 407853 | 597448 | 0 | Low 1,226 / High 3,933 | Low 118,918 / High 381,552 |  |  |  |  | Number of customers | This data includes the number of customers on a circuit whether they were de-energized or not For Q2-Q4 2021 time periods, SCE used 2020 recorded data adjusted for improvement expected based on SCE's planned wildfire mitigation activities to create a baseline. To factor in weather variability, which has significant impacts on PSPS events, SCE developed a range around the baseline. The range was based on an 18 year backcast analysis that analyzed how current PSPS triggers would have resulted in PSPS events when applied to historical weather data. For further details on calculating the range, please see section 8.5 SCE also notes, that earlier PSPS events were not tracked and recorded in the same level of detail as it is now, therefore not all data is available.
| 5.c. | Customer hours of PSPS per RFW OH circuit mile day | 0 | 0 | NA | NA | NA | 0 | 0 | 17 | 434 | 875.0389 | 0 | L 6 / H1 8 | L 158 / H 507 |  |  |  |  | =1.c. / RFW OH circuit mile days in time period | For Q2-Q4 2021 time periods, SCE used 2020 recorded data adjusted for improvement expected based on SCE's planned wildfire mitigation activities to create a baseline. To factor in weather variability, which has significant impacts on PSPS events, SCE developed a range around the baseline. The range was based on an 18 year backcast analysis that analyzed how current PSPS triggers would have resulted in PSPS events when applied to historical weather data. For further details on calculating the range, please see section 8.5 SCE also notes, that earlier PSPS events were not tracked and recorded in the same level of detail as it is now, therefore not all data is available. Historical numbers were corrected as the original anlaysis methodology was found to be faulty. Additionally, Since historical numbers were adjusted, the forecast numbers were re-forecasted.
| 5.d. | Frequency of PSPS events (total) - High Wind Warning wind conditions | 0 | 0 | NA | NA | NA | 0 | 0 | 1 | 8 | 1 | 0 | L 0 / H 1 | L 3 / H 11 |  |  |  |  | Events over time period that overlapped with a High Wind Warning as defined by the National Weather Service | For Q2-Q4 2021 time periods, SCE used 2020 recorded data adjusted for improvement expected based on SCE's planned wildfire mitigation activities to create a baseline. To factor in weather variability, which has significant impacts on PSPS events, SCE developed a range around the baseline. The range was based on an 18 year backcast analysis that analyzed how current PSPS triggers would have resulted in PSPS events when applied to historical weather data. For further details on calculating the range, please see section 8.5 SCE also notes, that earlier PSPS events were not tracked and recorded in the same level of detail as it is now, therefore not all data is available. Historical numbers were corrected as the original anlaysis methodology was found to be faulty. Additionally, Since historical numbers were adjusted, the forecast numbers were re-forecasted.
| 5.e. | Scope of PSPS events (total) - High Wind Warning wind conditions | 0 | 0 | NA | NA | NA | 0 | 0 | 7 | 392 | 151 | 0 | L 2 / H 5 | L 104 / H 335 |  |  |  |  | Estimated customers impacted over time period that overlapped with a High Wind Warning as defined by the National Weather Service | For Q2-Q4 2021 time periods, SCE used 2020 recorded data adjusted for improvement expected based on SCE's planned wildfire mitigation activities to create a baseline. To factor in weather variability, which has significant impacts on PSPS events, SCE developed a range around the baseline. The range was based on an 18 year backcast analysis that analyzed how current PSPS triggers would have resulted in PSPS events when applied to historical weather data. For further details on calculating the range, please see section 8.5 SCE also notes, that earlier PSPS events were not tracked and recorded in the same level of detail as it is now, therefore not all data is available. SCE interprets this line item as de-energized circuit counts that overlap with High Wind Warnings. Historical numbers were corrected as the original anlaysis methodology was found to be faulty. Additionally, since historical numbers were adjusted, the forecast numbers were re-forecasted.
| 5.f. | Duration of PSPS events (total) - High Wind Warning wind conditions | 0 | 0 | NA | NA | NA | 0 | 0 | 3499.5 | 4298691.8 | 1826480 | 0 | L 910 / H 2,920 | L 1,175,242 / H 3,770,782 |  |  |  |  | Customer hours over time period that overlapped with a High Wind Warning as defined by the National Weather Service | For Q2-Q4 2021 time periods, SCE used 2020 recorded data adjusted for improvement expected based on SCE's planned wildfire mitigation activities to create a baseline. To factor in weather variability, which has significant impacts on PSPS events, SCE developed a range around the baseline. The range was based on an 18 year backcast analysis that analyzed how current PSPS triggers would have resulted in PSPS events when applied to historical weather data. For further details on calculating the range, please see section 8.5 SCE also notes, that earlier PSPS events were not tracked and recorded in the same level of detail as it is now, therefore not all data is available. Historical numbers were corrected as the original anlaysis methodology was found to be faulty. Additionally, Since historical numbers were adjusted, the forecast numbers were re-forecasted.

## Table 12
Utility | Southern California Edison Company | Notes:
Table No. | 12 | Risk-Spend-Efficiency (RSE) is defined as "An estimate of the cost-effectiveness of initiative, calculated by dividing the mitigation risk reduction benefit by the mitigation cost estimate based on the full set of risk reduction benefits estimated from the incurred costs."
Date Modified | 2021-05-03 | CAPEX = Capital expenditure; OPEX = Operating expenditure. In future submissions update planned spend, line miles treated, RSE, etc. with updated projections and actuals. Additional instructions can be found in QR information.
|  | All dollars shown are in nominal, thousands of dollars (000s). | [16 empty] | Actual | Actual | Actual | Actual | Projected | Projected | Projected | Projected | Projected | Projected | Projected | Projected
Table 12: Mitigation initiative financials | [18 empty] | CAPEX ($ thousands) | OPEX ($ thousands) | Line miles to be treated | Alternative units (if used) | CAPEX ($ thousands) | OPEX ($ thousands) | Line miles to be treated | Alternative units (if used) | CAPEX ($ thousands) | OPEX ($ thousands) | Line miles to be treated | Alternative units (if used)
Metric type | WMP Table # / Category | WMP Initiative # | Initative activity | WMP Identifier | Primary driver targeted | Secondary driver targeted | Year initiated | Estimated RSE in non-HFTD region | Estimated RSE in HFTD Zone 1 | Estimated RSE in HFTD Tier 2 | Estimated RSE in HFTD Tier 3 | If existing: most recent proceeding that has reviewed program | If new: memorandum account | Current compiance status - In / exceeding compliance with regulations | Associated rule(s) - if multiple, separate by semi-colon - ";" | If spend not disaggregated by this activity, note activity where relevant spend is tracked in or mark "general operations" | Alternative units in which initiative is reported (if not line miles); still required to report line miles | Comments | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022
Other | Risk Assessment & Mapping | 7.3.1.1. | A summarized risk map that shows the overall ignition probability and estimated wildfire consequence along the electric lines and equipment | NA | [8 empty] | GSRPBA |  |  | Costs included in SA-4 |  |  | 265.437 | 174.667 |  |  |  | 314.945 |  |  |  | 174.667
Other | Risk Assessment & Mapping | 7.3.1.2. | Climate-driven risk map and modelling based on various relevant weather scenarios | NA | [11 empty] | General operations
Other | Risk Assessment & Mapping | 7.3.1.3. | Ignition probability mapping showing the probability of ignition along the electric lines and equipment | NA | [8 empty] | GSRPBA |  |  | Costs included in SA-4 |  |  | 265.437 | 174.667 |  |  |  | 314.945 |  |  |  | 174.667
Other | Risk Assessment & Mapping | 7.3.1.4. | Initiative mapping and estimation of wildfire and PSPS risk-reduction impact | NA | [11 empty] | General operations
Other | Risk Assessment & Mapping | 7.3.1.5. | Match drop simulations showing the potential wildfire consequence of ignitions that occur along the electric lines and equipment | NA | [8 empty] | GSRPBA |  |  | Costs included in SA-4 |  |  | 265.437 | 174.667 |  |  |  | 314.945 |  |  |  | 174.667
Other | Situational Awareness & Forecasting | 7.3.2.1. | Advanced weather monitoring and weather stations | SA-1 |  |  | 2018 |  |  |  |  | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | GSRPBA | Exceeding compliance with regulations |  | NA | # of weather station installs |  | 7602.9462 | 4308.7145 |  | 593 | 5273.376 | 7359.5193 |  | 475 | 5273.375 | 7870.5835 |  | 475
Other | Situational Awareness & Forecasting | 7.3.2.2. | Continuous monitoring sensors | SA-9 | Equipment failure | Other contact with object | 2018 | 925.2316 |  | 4456.1205 | 2756.4505 | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | GSRPBA; WMPMA | Exceeding compliance with regulations |  | NA | # of devices |  | 260.4045 | 215.1821 |  |  | 9554.4118 | 251.5244 |  | 150 | 19608.6804 |  |  | 300
Other | Situational Awareness & Forecasting | 7.3.2.3. | Fault indicators for detecting faults on electric lines and equipment | NA |  |  | NA | [5 empty] | NA |  |  | General operations | # of installations (395 are in HFRA) | This activity is not considered by SCE to be a WMP activity and only units have been provided as the dollars are not disaggregated in SCE's accounting system at this level. Year initiated noted as "NA" as initiative started pre-GSRP/WMP. |  |  |  | 1566 |  |  |  | 1566 |  |  |  | 1566
Other | Situational Awareness & Forecasting | 7.3.2.4.1 | Forecast of a fire risk index, fire potential index, or similar | SA-2 | [11 empty] | Costs included with SA-3
Other | Situational Awareness & Forecasting | 7.3.2.4.2 | Forecast of a fire risk index, fire potential index, or similar | SA-5 |  |  | 2019 |  |  |  |  | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | FRMMA | Exceeding compliance with regulations |  | NA | # of square miles |  |  | 192.8959 |  |  |  | 320 |  | 6500 |  | 604.022 |  | 6500
Other | Situational Awareness & Forecasting | 7.3.2.4.3 | Forecast of a fire risk index, fire potential index, or similar | SA-7 |  |  | 2020 |  |  |  |  | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | WMPMA | Exceeding compliance with regulations |  | NA | [7 empty] | 1466.63 | 14000 |  |  | 1711.064 | 14000
Other | Situational Awareness & Forecasting | 7.3.2.4.4 | Forecast of a fire risk index, fire potential index, or similar | SA-8 |  |  | 2019 |  |  |  |  | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | WMPMA | Exceeding compliance with regulations |  | NA |  |  |  | 414.23 | 14000 |  |  | 891.109 | 14000 |  |  | 500 | 14000
Other | Situational Awareness & Forecasting | 7.3.2.5. | Personnel monitoring areas of electric lines and equipment in elevated fire risk conditions | NA |  |  | NA | [5 empty] | NA |  |  | General operations |  | This activity is not considered by SCE to be a WMP activity and dollars/units represent SCE's full service area, not just its HFRA. Year initiated noted as "NA" as initiative started pre-GSRP/WMP. |  | 25218.052 | 14000 |  |  | 24098.7909 | 14000 |  |  | 24782.3712 | 14000
Other | Situational Awareness & Forecasting | 7.3.2.6.1 | Weather forecasting and estimating impacts on electric lines and equipment | SA-3 |  |  | 2018 |  |  |  |  | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | GSRPBA; WMPMA | Exceeding compliance with regulations |  | NA | # of HPCCs in 2021 | Not intending to install new HPCCs in 2022 | 3309.6853 | 1133.6783 |  |  | 6552.4384 | 3727.819 |  | 2 | 700 | 3143.317
Other | Situational Awareness & Forecasting | 7.3.2.6.2 | Weather forecasting and estimating impacts on electric lines and equipment | SA-4 |  |  | 2018 |  |  |  |  | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | FRMMA | Exceeding compliance with regulations |  | NA |  |  |  | 1028.791 | 14000 |  |  | 1348.134 | 14000 |  |  | 827.788 | 14000
Grid hardening | Grid Design & System Hardening | 7.3.3.1. | Capacitor maintenance and replacement program | NA |  |  | NA | [5 empty] | NA | In compliance with regulations | GO 95; GO 165 | General operations | 2020: 112 OH Caps; 10 PM Caps; 23 Removals 2021: 41 OH Caps; 10 PM Caps; 6 Removals 2022: 55 OH Caps; 14 PM Caps; 8 Removals | This activity is not considered by SCE to be a WMP activity and dollars/units represent SCE's full service area, not just its HFRA. Year initiated noted as "NA" as initiative started pre-GSRP/WMP. | 5274.944 |  |  | 145 | 2444.4346 |  |  | 57 | 3413.4028 |  |  | 77
Grid hardening | Grid Design & System Hardening | 7.3.3.2. | Circuit breaker maintenance and installation to de-energize lines upon detecting a fault | SH-6 | Equipment failure | Other contact with object | 2018 |  |  | 1957.8119 | 3307.9782 | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | GSRPBA | Exceeding compliance with regulations | GO 95; GO 165 | NA | # of relays |  | 9785.6956 | -9.2988 |  | 109 | 12897.8392 |  |  | 86 | 8583.1597 |  |  | 113
Grid hardening | Grid Design & System Hardening | 7.3.3.3.1 | Covered conductor installation | SH-1 | Other contact with object | Wire-to-wire contact | 2018 |  |  | 3513.6466 | 4191.6824 | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | GSRPBA | Exceeding compliance with regulations | GO 95, Rule 31.1 | NA | # of miles of covered conductor installs | In 2020, there were 814 WCCP circuit miles and 151 non-WCCP circuit miles installed. | 546151.289 |  |  | 965 | 753659.2664 |  |  | 1400 | 883812.5928 |  |  | 1600
Grid hardening | Grid Design & System Hardening | 7.3.3.3.2 | Covered conductor installation | SH-10 | Other contact with object | Wire-to-wire contact | 2018 |  |  |  |  | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | GSRPBA | Exceeding compliance with regulations | GO 95, Rule 31.1 | NA | # of remediations | 405 tree attachments were remediated in 2020. The majority, 369, of these tree attachments were scoped for future years but were removed as a result of wildfires in the second half of the year. | 9653.5501 |  |  | 405 | 22230.7053 |  |  | 688.9 | 26090.0335 |  |  | 787.9
Grid hardening | Grid Design & System Hardening | 7.3.3.4. | Covered conductor maintenance | NA | [9 empty] | In compliance with regulations | GO 95 | General operations
Grid hardening | Grid Design & System Hardening | 7.3.3.5. | Crossarm maintenance, repair, and replacement | NA | [9 empty] | In compliance with regulations | GO 95 | General operations
Grid hardening | Grid Design & System Hardening | 7.3.3.6. | Distribution pole replacement and reinforcement, including with composite poles | NA |  |  | NA | [5 empty] | NA | In compliance with regulations | GO 95 | General operations | # of pole remediations | This activity is not considered by SCE to be a WMP activity and dollars/units represent SCE's full service area, not just its HFRA. Year initiated noted as "NA" as initiative started pre-GSRP/WMP. | 181874.339 |  |  | 9511 | 306564.8402 |  |  | 15265 | 219403.2361 |  |  | 11611
Grid hardening | Grid Design & System Hardening | 7.3.3.7. | Expulsion fuse replacement | SH-4 | Equipment failure | Other contact with object | 2018 |  |  | 1362.5192 | 3303.9847 | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | GSRPBA | Exceeding compliance with regulations | GO 95 | NA | Location count |  | 8955.1643 | 3261.7993 |  | 3025 |  | 1153.706 |  | 421 |  | 1333.607 |  | 481
Grid hardening | Grid Design & System Hardening | 7.3.3.8.1 | Grid topology improvements to mitigate or reduce PSPS events | SH-7 | [7 empty] | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. |  | Exceeding compliance with regulations | GO 95 | NA |  | SCE does not plan to incur incremental costs for this initiative.
Grid hardening | Grid Design & System Hardening | 7.3.3.8.2 | Grid topology improvements to mitigate or reduce PSPS events | SH-12 |  |  | 2020 |  |  |  |  | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | MGOIR | Exceeding compliance with regulations | GO 95 | NA | [6 empty] | 4000 |  | 9715 |  | 7000 |  | 9715
Grid hardening | Grid Design & System Hardening | 7.3.3.9. | Installation of system automation equipment | SH-5 |  |  | 2018 | [5 empty] | GSRPBA; FHPMA | Exceeding compliance with regulations | GO 95 | NA | # of devices |  | 5866.6214 |  |  | 49
Grid hardening | Grid Design & System Hardening | 7.3.3.10. | Maintenance, repair, and replacement of connectors, including hotline clamps | NA | [9 empty] | In compliance with regulations | GO 95 | General operations
Grid hardening | Grid Design & System Hardening | 7.3.3.11. | Mitigation of impact on customers and other residents affected during PSPS event | NA | [11 empty] | General operations
Grid hardening | Grid Design & System Hardening | 7.3.3.12. | Other corrective action | SH-14 | Wire-to-wire contact | Equipment failure | 2019 |  |  | 1867.0931 | 1956.5373 | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | WMPMA | Exceeding compliance with regulations | GO 95 | NA |  | Units to be determined by field assessments being conducted in Q1/Q2 2021. |  | 554.1823 | 9715 |  | 5943.3443 | 2221.4047 | 9715 |  | 33589.9313 | 14027.2623 | 9715
Grid hardening | Grid Design & System Hardening | 7.3.3.13. | Pole loading infrastructure hardening and replacement program based on pole loading assessment program | NA |  |  | NA | [5 empty] | NA | In compliance with regulations | GO 95 | General operations | # of pole remediations | This activity is not considered by SCE to be a WMP activity and dollars/units represent SCE's full service area, not just its HFRA. Year initiated noted as "NA" as initiative started pre-GSRP/WMP. | 97292.42 |  |  | 3805 | 209875.4302 |  |  | 1072 | 307949.2338 |  |  | 15135
Grid hardening | Grid Design & System Hardening | 7.3.3.14. | Transformers maintenance and replacement | NA |  |  | NA | [5 empty] | NA | In compliance with regulations | GO 95 | General operations | Includes overhead, padmount and BURD transformers, and associated inspections. | This activity is not considered by SCE to be a WMP activity and dollars/units represent SCE's full service area, not just its HFRA. Year initiated noted as "NA" as initiative started pre-GSRP/WMP. | 96400 | 3800.42 |  | 31947 | 96262.0708 | 5704 |  | 33408 | 98187.3065 | 6045.083 |  | 32335
Grid hardening | Grid Design & System Hardening | 7.3.3.15. | Transmission tower maintenance and replacement | SH-13 | Contamination | Equipment failure | 2020 | 0.005938 |  | 1.1505e-14 | 81.5993 |  | WMPMA | Exceeding compliance with regulations | GO 95 | NA | # of structures | [6 empty] | 1000 |  | 53
Grid hardening | Grid Design & System Hardening | 7.3.3.16. | Undergrounding of electric lines and/or equipment | SH-2 | Other contact with object | Wire-to-wire contact | 2019 |  |  | 447.0314 | 347.2735 | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | WMPMA | Exceeding compliance with regulations | GO 95 | NA |  | In 2020, only design work was completed. | 961.3883 |  |  |  | 26350.0583 |  | 6 |  | 54347.1445 |  | 11
Grid hardening | Grid Design & System Hardening | 7.3.3.17.1 | Updates to grid topology to minimize risk of ignition in HFTDs | SH-15 | Equipment failure |  | 2019 |  |  |  | 12.9104 | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | WMPMA | Exceeding compliance with regulations | GO 95 | NA | # of replacements | [5 empty] | 852.9594 |  |  | 30 | 1750.543 |  |  | 60
Grid hardening | Grid Design & System Hardening | 7.3.3.17.2 | Updates to grid topology to minimize risk of ignition in HFTDs | SH-11 |  |  | 2019 |  |  |  |  | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | WMPMA | Exceeding compliance with regulations | GO 95 | NA |  |  |  | 73.8882 | 9715 |  | 4450 | 820 | 9715 |  | 3953 | 225 | 9715
Grid hardening | Grid Design & System Hardening | 7.3.3.17.3 | Updates to grid topology to minimize risk of ignition in HFTDs | SH-8 |  |  | 2019 |  |  |  |  | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | WMPMA | Exceeding compliance with regulations | GO 95 | NA | Cicuit miles within HFRA |  |  | 124.6627 |  | 6 |  | 400 |  | 10 |  | 750 |  | 13
Asset inspection | Asset Management & Inspections | 7.3.4.1. | Detailed inspections of distribution electric lines and equipment | NA |  |  | NA | [6 empty] | In compliance with regulations | GO 165 | General operations | 2020: 56,895 inspections in HFRA; 205,875 inspections in non-HFRA 2021: 27,000 inspections in HFRA; 244,000 inspections in non-HFRA 2022: 27,000 inspections in HFRA; 244,000 inspections in non-HFRA | Year initiated noted as "NA" as initiative started pre-GSRP/WMP. |  | 8960 |  | 262770 |  | 4222.9057 |  | 271000 |  | 4331.9908 |  | 271000
Asset inspection | Asset Management & Inspections | 7.3.4.2. | Detailed inspections of transmission electric lines and equipment | NA |  |  | NA | [6 empty] | In compliance with regulations | GO 165 | General operations | # of inspections | Year initiated noted as "NA" as initiative started pre-GSRP/WMP. |  | 3567.333 |  | 1313 |  | 7604.269 |  | 1313 |  | 7802.2789 |  | 1313
Asset inspection | Asset Management & Inspections | 7.3.4.3. | Improvement of inspections | IN-8 |  |  | 2021 |  |  |  |  | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | WMPMA | Exceeding compliance with regulations |  | NA |  |  | 28718.5992 | 2629.307 | 9715 |  | 17422 | 6490.201 | 9715 |  | 6600 | 5240.7 | 9715
Asset inspection | Asset Management & Inspections | 7.3.4.4. | Infrared inspections of distribution electric lines and equipment | IN-3 | Equipment failure |  | 2017 |  |  | 156.1043 | 1878.7442 | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | GSRPBA | Exceeding compliance with regulations | GO 95, Rule 31.2; GO 95, Rule 31.1 | NA |  |  |  | 790.7734 | 4416 |  |  | 426.5578 | 4425 |  |  | 426.5578 | 4425
Asset inspection | Asset Management & Inspections | 7.3.4.5. | Infrared inspections of transmission electric lines and equipment | IN-4 | Equipment failure |  | 2019 |  |  |  | 173.7768 | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | WMPMA | Exceeding compliance with regulations | GO 95, Rule 31.2; GO 95, Rule 31.1 | NA |  |  |  | 383.5504 | 1005 |  |  | 208.6865 | 1000 |  |  | 215.9556 | 1000
Asset inspection | Asset Management & Inspections | 7.3.4.6. | Intrusive pole inspections | NA |  |  | NA | [6 empty] | In compliance with regulations | GO 95 | General operations |  | Year initiated noted as "NA" as initiative started pre-GSRP/WMP. | [5 empty] | 4222.9057 | 14000 |  |  | 4331.9908 | 14000
Asset inspection | Asset Management & Inspections | 7.3.4.7. | LiDAR inspections of distribution electric lines and equipment | NA | [11 empty] | General operations
Asset inspection | Asset Management & Inspections | 7.3.4.8. | LiDAR inspections of transmission electric lines and equipment | NA | [11 empty] | General operations
Asset inspection | Asset Management & Inspections | 7.3.4.9.1 | Other discretionary inspection of distribution electric lines and equipment, beyond inspections mandated by rules and regulations | IN-1.1 | Equipment failure |  | 2018 |  |  | 2636.0793 | 2776.9884 | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | FRMMA; GSRPBA; WMPMA | Exceeding compliance with regulations | GO 95, Rule 31.2; GO 95, Rule 31.1; GO 165 | NA | 2020: # of Ground Inspections: 199,050; # of Aerial Inspections: 168,017; # of Remediations: 26,915 2021: # of Ground Inspections: 198,000; # of Aerial Inspections: 198,000; # of Remediations: 24,584 2022: # of Ground Inspections: 171,000; # of Aerial Inspections: 198,468; # of Remediations: 14,354 |  | 85218.9688 | 105553.2628 |  | 393982 | 147937.768 | 104185.2191 |  | 420584 | 88697.9096 | 91606.0157 |  | 383822.4144
Asset inspection | Asset Management & Inspections | 7.3.4.9.2 | Other discretionary inspection of distribution electric lines and equipment, beyond inspections mandated by rules and regulations | IN-5 |  |  | 2019 |  |  |  |  | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | FRMMA; WMPMA | Exceeding compliance with regulations | GO 95 Rule 31.2; GO 165 | NA |  |  |  | 402.545 |  | 268 |  | 315 |  | 181 |  |  |  | 102
Asset inspection | Asset Management & Inspections | 7.3.4.10. | Other discretionary inspection of transmission electric lines and | IN-1.2 | Equipment failure |  | 2018 |  |  | 540.3791 | 763.5109 | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | FRMMA; GSRPBA; WMPMA | Exceeding compliance with regulations | GO 95, Rule 31.2; GO 95, Rule 31.1; GO 165 | NA | 2020: # of Ground Inspections: 35,562; # of Aerial Inspections: 31,381; # of Remediations: 6,486 2021: # of Ground Inspections: 22,800; # of Aerial Inspections: 22,800; # of Remediations: 5,902 2022: # of Ground Inspections: 14,902; # of Aerial Inspections: 22,834; # of Remediations: 3,605 |  | 35934.3099 | 51820.5097 |  | 73429 | 50758.4 | 25180.938 |  | 51502 | 18098.1159 | 23824.8134 |  | 41341
Asset inspection | Asset Management & Inspections | 7.3.4.11. | Patrol inspections of distribution electric lines and equipment | NA |  |  | NA | [8 empty] | General operations |  | Year initiated noted as "NA" as initiative started pre-GSRP/WMP. |  | 25218.052 | 9715 |  |  | 24098.7909 | 9715 |  |  | 24782.3712 | 9715
Asset inspection | Asset Management & Inspections | 7.3.4.12. | Patrol inspections of transmission electric lines and equipment | NA | [11 empty] | General operations
Asset inspection | Asset Management & Inspections | 7.3.4.13. | Pole loading assessment program to determine safety factor | NA |  |  | NA | [6 empty] | In compliance with regulations | GO 95 | General operations | # of assessments | Year initiated noted as "NA" as initiative started pre-GSRP/WMP. |  | 14477.0821 |  | 121268 |  | 3209.9608 |  | 14400
Asset inspection | Asset Management & Inspections | 7.3.4.14. | Quality assurance / quality control of inspections | NA | [11 empty] | General operations
Asset inspection | Asset Management & Inspections | 7.3.4.15. | Substation inspections | NA |  |  | NA | [5 empty] | NA | In compliance with regulations | GO 174 | General operations | # of inspections | This activity is not considered by SCE to be a WMP activity and dollars/units represent SCE's full service area, not just its HFRA. Year initiated noted as "NA" as initiative started pre-GSRP/WMP. |  | 2671.657 |  | 4209 |  | 2854.962 |  | 4426 |  | 2986.492 |  | 5644
Vegetation management project | Vegetation Management & Inspections | 7.3.5.1. | Additional efforts to manage community and environmental impacts | NA | [11 empty] | General operations
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.2. | Detailed inspections of vegetation around distribution electric lines and equipment | NA |  |  | NA | [5 empty] | NA | In compliance with regulations | GO 95; GO 174 | General operations | # of ground inspection and aerial inspections | This activity is not considered by SCE to be a WMP activity and dollars/units represent SCE's full service area, not just its HFRA. Year initiated noted as "NA" as initiative started pre-GSRP/WMP. |  | 25755.7217 |  | 1760000 |  | 15020.37 |  | 1149000 |  | 15470.984 |  | 1149000
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.3. | Detailed inspections of vegetation around transmission electric lines and equipment | NA |  |  | NA | [5 empty] | NA | In compliance with regulations | GO 95; GO 174 | General operations | # of inspections | This activity is not considered by SCE to be a WMP activity and dollars/units represent SCE's full service area, not just its HFRA. Year initiated noted as "NA" as initiative started pre-GSRP/WMP. |  | 1773.7554 |  | 321000 |  | 2752.7 |  | 234000 |  | 2835.281 |  | 234000
Vegetation management project | Vegetation Management & Inspections | 7.3.5.4. | Emergency response vegetation management due to red flag warning or other urgent conditions | NA | [11 empty] | General operations
Vegetation management project | Vegetation Management & Inspections | 7.3.5.5.1 | Fuel management and reduction of “slash” from vegetation management activities | VM-2 | Equipment failure |  | 2019 |  |  | 1426.4149 | 1881.0953 | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | WMPMA | Exceeding compliance with regulations | PRC 4292 | NA | # of poles brushed |  |  | 7459.0831 |  | 234000 |  | 8271.6173 |  | 229190 |  | 6787.1583 |  | 229190
Vegetation management project | Vegetation Management & Inspections | 7.3.5.5.2 | Fuel management and reduction of “slash” from vegetation management activities | VM-3 |  |  | 2019 |  |  |  |  | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | FHPMA | Exceeding compliance with regulations | PRC 4291; PRC 4293 | NA | [5 empty] | 61 |  | 900 |  | 46 |  | 1089 |  | 49
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.6. | Improvement of inspections | NA | [11 empty] | General operations
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.7. | LiDAR inspections of vegetation around distribution electric lines and equipment | NA | [11 empty] | General operations
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.8. | LiDAR inspections of vegetation around transmission electric lines and equipment | NA |  |  | 2019 |  |  |  |  | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | WMPMA | Exceeding compliance with regulations | FAC-003-4 | NA |  |  |  | 4092.2315 | 1227 |  |  | 1485.4906 | 1227 |  |  | 1502.4868 | 1227
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.9. | Other discretionary inspections of vegetation around distribution electric lines and equipment | NA | [11 empty] | General operations
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.10. | Other discretionary inspections of vegetation around transmission electric lines and equipment | NA | [11 empty] | General operations
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.11. | Patrol inspections of vegetation around distribution electric lines and equipment | NA | Contact with vegetation | [6 empty] | 2018 GRC | FHPMA | Exceeding compliance with regulations | GO 95; PRC 4293; FAC-003-4 | NA |  | Year initiated noted as "NA" as initiative started pre-GSRP/WMP. | [5 empty] | 10009.0536 |  |  |  | 10309.3252
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.12. | Patrol inspections of vegetation around transmission electric lines and equipment | NA | Contact with vegetation | [6 empty] | 2018 GRC | FHPMA | Exceeding compliance with regulations | GO 95; PRC 4293; FAC-003-4 | NA |  | Year initiated noted as "NA" as initiative started pre-GSRP/WMP. | [5 empty] | 4305.7714 |  |  |  | 4434.9446
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.13. | Quality assurance / quality control of vegetation inspections | NA |  |  | 2019 |  |  |  |  | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | WMPMA | Exceeding compliance with regulations | GO 95; PRC 4293; FAC-003-4 | NA |  |  |  | 3966.0336 | 14000 |  |  | 5546.7819 | 14000 |  |  | 6158.9773 | 14000
Vegetation management project | Vegetation Management & Inspections | 7.3.5.14. | Recruiting and training of vegetation management personnel | NA | [11 empty] | General operations
Vegetation management project | Vegetation Management & Inspections | 7.3.5.15. | Remediation of at-risk species | NA | [11 empty] | General operations
Vegetation management project | Vegetation Management & Inspections | 7.3.5.16.1 | Removal and remediation of trees with strike potential to electric lines and equipment | VM-1 | Contact with vegetation |  | 2018 |  |  | 1404.6941 | 1602.1656 | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | GSRPBA | Exceeding compliance with regulations | GO 95 Rule 35; PRC 4293 | NA | # of tree assessments |  |  | 46684.7626 |  | 99523 |  | 80722.0319 |  | 200000 |  | 89161.7805 |  | 200000
Vegetation management project | Vegetation Management & Inspections | 7.3.5.16.2 | Removal and remediation of trees with strike potential to electric lines and equipment | VM-4 | Contact with vegetation |  | NA |  |  | 2284.1583 | 2413.127 | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | CEMA | Exceeding compliance with regulations | GO 95; PRC 4293; FAC-003-4 | NA |  | Year initiated noted as "NA" as initiative started pre-GSRP/WMP. |  | 37604 |  |  |  | 43444.52 |  |  |  | 44747.8556
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.17. | Substation inspection | NA | [11 empty] | General operations
Vegetation management project | Vegetation Management & Inspections | 7.3.5.18. | Substation vegetation management | NA | [11 empty] | General operations
Vegetation management project | Vegetation Management & Inspections | 7.3.5.19. | Vegetation inventory system | VM-6 |  |  | 2021 |  |  |  |  | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | WMPMA; GSRPBA | Exceeding compliance with regulations |  | NA |  |  | 16127.8644 | 1055.6305 | 14000 |  | 9940 | 4152.1774 | 14000 |  | 4475 | 4690.5012 | 14000
Vegetation management project | Vegetation Management & Inspections | 7.3.5.20 | Vegetation management to achieve clearances around electric lines and equipment | NA | Contact with vegetation |  | NA |  |  | 4042.1647 | 4511.8337 | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | FHPMA | Exceeding compliance with regulations | GO 95; PRC 4293; FAC-003-4 | NA |  | Year initiated noted as "NA" as initiative started pre-GSRP/WMP. |  | 233584.7285 | 14000 |  |  | 182747.4404 | 14000 |  |  | 187967.2815 | 14000
Other | Grid Operations & Operating Protocols | 7.3.6.1. | Automatic recloser operations | NA | [11 empty] | General operations
Other | Grid Operations & Operating Protocols | 7.3.6.2. | Crew-accompanying ignition prevention and suppression resources and services | NA | [11 empty] | General operations
Other | Grid Operations & Operating Protocols | 7.3.6.3. | Personnel work procedures and training in conditions of elevated fire risk | NA | [11 empty] | General operations
Other | Grid Operations & Operating Protocols | 7.3.6.4. | Protocols for PSPS re-energization | NA | [11 empty] | General operations
Other | Grid Operations & Operating Protocols | 7.3.6.5. | PSPS events and mitigation of PSPS impacts | PSPS-2 |  |  | 2018 |  |  | 107.5247 | 188.1622 | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | FRMMA; GSRPBA; WMPMA | Exceeding compliance with regulations | SB 167 | NA |  | This is the RSE for Community Resource Centers/Community Crew Vehicles. An RSE was calculated for Critical Care Backup Battery which is 12 and 22 for Tier 2 and Tier 3 respectively | 6843.2439 | 23977.0414 | 14000 |  | 7247.3697 | 48525.9686 | 14000 |  | 1250 | 48378.2279 | 14000
Other | Grid Operations & Operating Protocols | 7.3.6.6. | Stationed and on-call ignition prevention and suppression resources and services | NA | [11 empty] | General operations
Other | Data Governance | 7.3.7.1. | Centralized repository for data | DG-1 |  |  | 2021 |  |  |  |  | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | GSRPBA | Exceeding compliance with regulations |  | NA |  |  | 1796.1108 |  | 14000 |  | 15709.183 | 1052 | 14000 |  | 13698.24 | 2252 | 14000
Other | Data Governance | 7.3.7.2. | Collaborative research on utility ignition and/or wildfire | NA | [11 empty] | General operations
Other | Data Governance | 7.3.7.3. | Documentation and disclosure of wildfire-related data and algorithms | NA | [11 empty] | General operations
Other | Data Governance | 7.3.7.4. | Tracking and analysis of near miss data | NA | [11 empty] | General operations
Other | Resource Allocation Methodology | 7.3.8.1. | Allocation methodology development and application | NA |  |  | 2018 |  |  |  |  | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | FRMMA; WMPMA | Exceeding compliance with regulations |  | NA |  |  |  | 45202.1777 | 14000 |  |  | 7610.0635 | 14000 |  |  | 6086.0525 | 14000
Other | Resource Allocation Methodology | 7.3.8.2. | Risk reduction scenario development and analysis | NA | [11 empty] | General operations
Other | Resource Allocation Methodology | 7.3.8.3. | Risk spend efficiency analysis | NA | [11 empty] | General operations
Other | Emergency Planning & Preparedness | 7.3.9.1. | Adequate and trained workforce for service restoration | DEP-2 |  |  | 2018 |  |  |  |  | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | WMPMA | Exceeding compliance with regulations | GO 166 | NA |  |  |  | 615.6675 | 14000 |  |  | 2544.9991 | 14000 |  |  | 1956.9148 | 14000
Other | Emergency Planning & Preparedness | 7.3.9.2. | Community outreach, public awareness, and communications efforts | NA | [11 empty] | General operations
Other | Emergency Planning & Preparedness | 7.3.9.3 | Customer support in emergencies | NA | [11 empty] | General operations
Other | Emergency Planning & Preparedness | 7.3.9.4. | Disaster and emergency preparedness plan | NA | [11 empty] | General operations
Other | Emergency Planning & Preparedness | 7.3.9.5. | Preparedness and planning for service restoration | NA |  |  | 2018 |  |  |  |  | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | GSRPBA | Exceeding compliance with regulations |  | NA |  |  |  | 5327.909 | 14000 |  | 200 | 11567.6811 | 14000 |  | 600 | 11970.6163 | 14000
Other | Emergency Planning & Preparedness | 7.3.9.6. | Protocols in place to learn from wildfire events | NA | [11 empty] | General operations
Other | Stakeholder Cooperation & Community Engagement | 7.3.10.1.1 | Community engagement | DEP-1.2 |  |  | 2018 |  |  |  |  | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | GSRPBA | Exceeding compliance with regulations | R-1812005 | NA | # of meetings |  |  | 141.9413 |  | 9 |  | 109.9585 |  | 18 |  | 109.9585 |  | 18
Other | Stakeholder Cooperation & Community Engagement | 7.3.10.1.3 | Community engagement | DEP-1.3 |  |  | 2018 |  |  |  |  | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | FRMMA; GSRPBA | Exceeding compliance with regulations | R-1812005 | NA |  |  |  | 1654.7838 | 14000 |  |  | 3820.5736 | 14000 |  |  | 3903.7416 | 14000
Other | Stakeholder Cooperation & Community Engagement | 7.3.10.1.4 | Community engagement | DEP-4 |  |  | 2018 |  |  |  |  | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | FRMMA | Exceeding compliance with regulations |  | NA | # of surveys |  |  |  |  | 5 |  | 1434 |  | 4 |  | 1465 |  | 3
Other | Stakeholder Cooperation & Community Engagement | 7.3.10.2 | Cooperation and best practice sharing with agencies outside CA | NA | [11 empty] | General operations
Other | Stakeholder Cooperation & Community Engagement | 7.3.10.3 | Cooperation with suppression agencies | DEP-5 |  |  | 2020 |  |  | 1961.6509 | 3306.4653 | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | WMPMA | Exceeding compliance with regulations | PRC 4292; PRC 4293 | NA | # of aerial suppression resources |  |  | 2158 |  | 1 |  | 18000 |  | 5 |  | 18000 |  | 5
Other | Stakeholder Cooperation & Community Engagement | 7.3.10.4 | Forest service and fuel reduction cooperation and joint roadmap | NA | [11 empty] | General operations
Other |  | 7.1.D | Alternative Technologies | NA |  |  | 2018 |  |  |  |  | This activity was not included in SCE's 2018 GRC, but is included in its pending 2021 GRC. | GSRPBA; WMPMA | Exceeding compliance with regulations |  | NA |  | SCE has included costs related to alternative technology projects described in Section 7.1.D. | 1854.5692 | 158.9205 | 14000 |  | 8357.1864 |  | 14000 |  | 1545.5157 |  | 14000