## WD_REPORT
CIRCUIT | Switching Center | DATE | TIME | MADEC_Detected | Energized | MADEC_Detectable | MADEC_Detectable_Comments | Covered_Conductor | Evaluated_By | Assigned_To | PIA or MADEC detected? | QC | QC Comment | Dist | (NSEW) | CC comment | Energized Correct | Detectable Correct
HUGHES LAKE | Vincent | 2021-01-04 | 22:00 | 0 | 1 | 0 | No ILS. Per OMS E/O to isolate CHP. No VBTs present at time of event | 1 | GT |  | 0 |  |  | 36
SODA SPRINGS | Rector | 2021-01-25 | 12:35 | 0 | 1 | 0 | Per ILS, TM requests CB open to isolate WD. No VBTs in area. Need to look at covered conductor | 1 | GT |  | 0 |  |  | 51
CONDOR | Vincent | 2021-03-15 | 20:18 | 0 | 1 | 0 | TM requests RAR1542 operated to de-energize WD. No VBTs detected. Covered conductor | 1 | GT |  | 0 |  |  | 52
ROSEBUD | Rector | 2021-03-20 | 10:44 | 0 | 1 | 0 | Per ILS and RO, crane contacted primary and brought down covered conductor. Only onw VBT that was restored instantaneously from 221 V or 92% of nominal | 1 | GT |  | 0 |  |  | 50
STARGLOW | Valley | 2021-05-02 | 16:18 | 0 | 1 | 0 | No ILS, Per RO, TM opened BLF to isolate WD. No VBTs present | 1 | GT |  | 0 |  |  | 77
MUTUAL | Vista | 2021-06-25 | 18:11 | 0 | 1 | 0 | Per RO, TM cut over them arm jumpers isolating WD. No sustained VBTs | 1 | GT |  | 0 |  |  | 31
SODA SPRINGS | Rector | 2021-07-28 | 21:33 | 0 | 1 | 0 | Per ILS, TM requested EO to isolate WD. Covered conductor, BLFs did not operate. Low Voltage displayed is 121 V similar loss of phase | 1 | GT |  | 0 |  |  | 51
MAHOGANY | Rector | 2021-08-13 | 12:22 | 0 | 0 | 0 | Aerial cable down. No VBTs present | 1 | GT |  | 0 |  |  | 51
MCCLENNY | Rector | 2021-08-15 | 23:33 | 0 | 0 | 0 | Per ILS, ckt LO and TM isolated WD deadline. Aerial cable | 1 | GT |  | 0 |  |  | 53
PASCOE | Rector | 2021-08-18 | 10:19 | 0 | 1 | 0 | No ILS, Per RO and OMS, tree crew dropped tree on primary aerial cable. No VBTs present | 1 | GT |  | 0 |  |  | 53
CHEVELLE | Orange County | 2021-08-26 | 5:45 | 0 | 1 | 0 | No ILS, RO does not call out if WD was energized. No VBTS | 1 | GT |  | 0 |  |  | 30
TRI CITY | Mesa | 2021-09-03 | 15:21 | 0 | 1 | 0 | Per ILS, TM isolated WD by operating BLF02099. No sustained VBTs | 1 | GT |  | 0 |  |  | 27
BIGFOOT | Rector | 2021-09-08 | 13:31 | 0 | 0 | 0 | No ILS, per RO tree with primary cable fell over and need to replace 5 spans of cable. No VBTs | 1 | GT |  | 0 |  |  | 51
NAPOLEON | Vista | 2021-10-26 | 1:26 | 0 | 1 | 0 | No ILS. Per RO, ATW. No VBTs | 1 | GT |  | 0 |  |  | 31
MULHOLLAND | Ventura | 2021-11-11 | 14:39 | 0 | 0 | 0 | Per ILS, ckt LO and TM isolated WD deadline | 1 | GT |  | 0 |  |  | 35
MAGUIRE | Ventura | 2021-11-14 | 19:49 | 0 | 1 | 0 | Per ILS, ckt R&R beyond RAR0117 and TM requests open to de-energize. No VBTs | 1 | GT |  | 0 |  |  | 35